## Workbook Instructions
Instructions For Using The Asset Registry Template
1) Download A Raw Data Report From FLOW
A. Go to the FLOW Dashbord
B. Choose The Reports Icon
C. Choose Export Reports
D. Using The Drop Down Menus Choose Your Asset Registry Raw Data
E. Under Export Raw Data Report Click Show Advanced Settings
F. Check the box below the sentence "Export this report for use with an external system. This export format cannot be re-imported into the FLOW system."
G. Click on Raw Data Report
H. Once the report is generated, rename and save it
2) Copy Raw Data Into The Asset Registry
A. Open the Raw Data Report you have saved
B. Select and copy all data from the report
C. Paste the data into the Raw Data tab of the Asset Registry -- starting at cell A1
3) Breaking Up The Community Field
A. In the raw data report there is a column called "Community" that has all of the administrative information for the community (i.e. Country, District/Municipality, Sub-District/Sub-Municipality, Community). This column divides categories using the "¦" or bar symbol which can be found by hitting shift and the key above Enter. You should break up this field before copying the raw data and pasting it into the Raw Data tab of the Asset Registry
B. To break up this field follow these steps.
C. Download a raw data report of the data collected for the asset registry from FLOW and Open this excel document
D. Insert 6 columns after the "Community" column. To do this highlight the column next to "Community", right click and then choose Insert. Repeat this step 6 times. Even if you have less than 6 administrative or geographical divisions add 6 columns so that the rest of the formulas are in the correct place.
Before Inserting Columns:
Inserting Columns:
After Columns Are Inserted:
E. Rename the header row in the Community column and the 6 new columns to be Geo Level 1, Geo Level 2, Geo Level 3, Geo Level 4 , Geo Level 5, Geo Level 6 and Geo Level 7
Renamed Columns:
F. Highlight all of the data in the Geo Level 1 column except for the header row (row 1)
G. While the data in Geo Level 1 is highlighted Click on the Data tab in Excel and click on Text to Columns
H. A Text to Columns wizard will pop up.
In Step 1 choose the Delimited option then click Next:
In Step 2 under Delimiters Take the check mark off of the Tab box and Check the Other Box and put a ¦ or Bar symbol in the box next to Other then click Finish:
This will break up the data into the new columns it will look like this:
Do not worry if there are columns with no data in them, just leave those columns in the spreadsheet and leave them blank.
I. After you have broken up the columns copy and past the data including the header row into the Asset Registry Raw Data tab and proceed with further instructions.
4) Changing The Asset Registry Template To Default Government Regulatons to Your Country
A. This is a step you should complete before working with the Asset Registry and Save the change to the template so that when you work with the template in the future the change is allready made and does not need to be made again.
B. Before working with the Asset Registry you should change the Government Standard formulas to refer to your country. To do so follow these steps.
C. Open the Asset Registry workbook and go the the Reference Sheet Tab. Click on "Formulas" then choose "Name Manager"
D. This will open a "Name Manager" wizard. In the list of Names scroll down to fnd the row for "Gov_Standard_Quantity"
E. Double click on "Gov_Standards_Quantity" and then click on the small icon at the bottom.
F. This will open allow you to select a cell from the workbook, choose the number in the cell next to your country in the "Government Standards Water Quantity" section of the "Reference Sheet" tab. For example, if your country is Honduras you would choose cell "B17" which has 75 in it. In this case do not take out the second $ sign in the formula -- leave the formula alone and click icon again then click "OK"
G. Close out of name manager and save the template, then proceed to work with the template following the other instructions.
5) Manage Names -- This Step Is Only Necessry If You Have Added, Deleted or Moved Survey Questions Around In The FLOW Survey
If you have added, moved any questions in the survey this will affect the formulas in the asset registry spread sheet and you will need to update the formulas using the name manager funtion. There are detailed directions below, however, if you are not familiar with the name manager function it may be useful to view one of these instructional videos first: Name Manager English -- https://www.youtube.com/watch?v=sBSULe4aRA0 Name Manager Spanish: https://www.youtube.com/watch?v=npNOMu300AM . Note: No questions should be deleted from the surveys.
A. Because columns in the raw data report have been added, moved from what the formulas in the workbook were expecting, we will be using name manager to tell the workbook where to find the data needed for the formulas. All of the formulas and names have allready been created we just need to define new ranges for the names.
B. Click on the Formulas tab
C. Clcik on Name Manager
D. Click on the Comments Column -- this will put the names in order
E. Double Click on the first Name in the list -- this should be Year_Data_Was_Collected
F. You will see a box that looks like this:
G. Click on the icon indicated with the red arrow
H. Navigate to the Raw Data Tab
I. Find the column called "Year" and click on the cell right under the header name
J. You will see a box that looks like this:
K. Take out the second $ sign from the formula in the box. Only take out the second $ sign not the first one. Do not change anything else in this formula.
L. The formual should now look like this:
M. Cick the icon indicated with the red arrow.
N. Click ok
O. Click on the next name in the name manager and repeat the process above matching the name to the column with the matching data and then choosing the cell below that column header and removing the second $ sign.
P. Repeat until all names have been matched to the correct columns in the raw data
Q. Note: While most of the columns should be easy to match to the correct name a few are not intutive. There are 7 names in the name manager Geo_Level_2 thru Geo_Level_6. These should correspond with the geographical levels in your data which vary by country. If you do not have 7 total levels of geographical distinctions you can just use as many names as necessary and skip the additonal ones. For example: if a country has 4 geograqphical levels (Country, District, Municipality, Community) the country name would match up with the lable "Country" in the name manager, the District would match to Geo_Level_2, the municipality would match to Geo_Level_3 and the community would match to the label "Community".
6) Updating The Pivot Charts
A. If you have less than 200 rows of data delete the rows with no data from the Asset Registry tab.
B. In Excel Click on the Formulas Tab
C. Click on the icon for Name Manger
D. Click on the name tag named "Summary"
E. This will open a box that looks like this:
F. Click on the button indicated above by the red arrow
G. Navigate to the Asset Regitry tab and select all the rows that have data in them then hit enter
H. Click Ok
I. Click Close
J. Navigate to the Summary tab
K. Click on cell A1
L. At the top of the screen you should now see a tab in pink called Pivot Table Tools
M. Click Options uder Pivot Table Tools
N. Click on the arrow beneath the Refresh All Option and Choose Refresh All
O. This will cause all charts to update with the most current information. Note: The charts will also automatically update each time the spreadseet is opened.

## Summary
Level Of Priority To Replace/Repair The System | Count
High Priority | 142
Medium Priority | 91
Low Priority | 683
Grand Total | 916
Risk Based On Age | Count
High Risk | 24
Medium Risk | 12
Low Risk | 880
Grand Total | 916
Risk Based On Current Condition | Count
High Risk | 142
Medium Risk | 95
Low Risk | 679
Grand Total | 916
Level Of Service: Water Point/System | Count
Basic Level of Service | 166
Intermediate Level of Service | 549
High Level of Service | 201
Grand Total | 916

## Asset Registry
General Information | [15 empty] | Results |  |  |  |  | Actions |  |  | Remaining Lifespan | [9 empty] | Physical Condition of Components | [10 empty] | Level Of Service | [7 empty] | Count Of Components | [9 empty] | Data For Calculations
Year Data Was Collected | Geo Level 1 | Geo Level 2 | Geo Level 3 | Geo Level 4 | Geo Level 5 | Geo Level 6 | Geo Level 7 | Water Point/System Unique ID | Total Number Of Families In The Community | Total Number Of Families With Access To An Improved Water Point/System | Total Number Of Families Without Access To An Improved Water Point/System | Type Of Water Point/System | Year Of Construction | Construction Funded By | Source Of Water Point/System | Risk Based On Age | Risk Based On Current Condition | Level Of Service: Water Point/System | Level Of Priority To Replace/Repair The System | Level Of Service: Water Point/System Score | Alert | Component(s) | Recommended Activity | Remaining Lifespan Of Intake Structure (Years) | Remaining Lifespan Of Conduction Line (Years) | Remaining Lifespan Of Storage Tank (Years) | Remaining Lifespan of Other Concrete Structures (Years) | Remaining Lifespan Of Distribution Network (Years) | Remaining Lifespan Of The Pump (Years) | Remaining Lifespan Of The Pump Station (Years) | Remaining Lifespan Of The Treatment Equipment (Years) | Remaining Lifespan Of The Treatment Housing Structure (Years) | Remaining Lifespan Of The Kiosk/Tap Stand(Years) | Physical State Of The Intake Structure. 1: Normal; 2: Poor; 3: Does Not Function; None: Blank | Physical State Of The Conduction Line. 1: Normal; 2: Poor; 3: Does Not Function; None: Blank | Physical State Of The Storage Tank. 1: Normal; 2: Poor; 3: Does Not Function; None: Blank | Physical State Of The Concrete Structures : 1: Normal; 2: Poor; 3: Does Not Function; None: Blank | Physical State Of The Distribution Network: Normal. 1: Normal; 2: Poor; 3: Does Not Function; None: Blank | Physical State Of The Pump Normal. 1: Normal; 2: Poor; 3: Does Not Function; None: Blank | Physical State Of The Pump House/Station. 1: Normal; 2: Poor; 3: Does Not Function; None: Blank | Physical State Of The Treatment Equipment. 1: Normal; 2: Poor; 3: Does Not Function; None: Blank | Physical State Of The Treatment Housing Structure. 1: Normal; 2: Poor; 3: Does Not Function; None: Blank | Physical State Of The Kiosk/Tap Stand. 1:Normal; 2: Poor; 3:Does Not Function; None: Blank | Overall State Of The Water Point/System 1: Normal; 2: Poor; 3: Does Not Function; None: Leave Blank | Water Point/System Improved Or Unimproved. 1: Improved; 0: Unimproved | Is The Source Protected? 1: Yes; 0: No | Number Of Users Meets Gov. Standards 1: # Of Users <=Gov.Standards; 0 # Of Users < Gov. Standards | Does The Water Point/System Provide Adequate Water Quantity? 1: Yes; 0: No | Does Water System Have Adequate Water Quality? (Bacteria, Turbidity, Other Contaminants Of Concern) 1: Yes; 0: No | Was The Water Point/ System Out Of Service For One Day Or Less Per Month In The Last Year? 1: Yes; 0: No | Is Water Available From The Water Point/System On The Day Of The Visit? 1: Yes; 0: No | Water Point/System In Good Overall Condition and Functioning | Number Of Sources | Number Of Intake Structures | Number of Conduction Lines | Approximate Length Of Conduction Lines (Meters) | Number Of Storage Tanks | Number Of Other Concrete Structures | Number Of Distribution Networks | Approximate Length Of Distribution Networks (Meters) | Number Of Pumps | Number Of Kiosks Or Tap Stands | Presence Of Intake Structure? 1: Yes; 0: No | Type Of Intake Structure | Year The Intake Structure Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction. | Presence Of Conduction Line? 1: Yes; 0: No | Year Conduction Line was Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Presence Of Storage Tank? 1: Yes; 0: No | Year The Storage Tank Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Presence Of Other Concrete Structures (Sedimentation Tank, Pressure Break Tank, etc.)? 1: Yes; 0: No | Year Other Concrete Structures Were Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Presence Of Distribution Network? 1: Yes; 0: No | Year The Distribution Network Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Presence Of Pump? 1: Yes; 0: No | Year Pump Was Installed. If Replaced Year Of Most Recent Replacement | Presence Of A Pump House/Station? 1: Yes; 0: No | Year The Pump House/Station Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Presence Of Treatment Equipment? 1: Yes; 0: No | Type Of Treatment: (Disinfection/Chlorination, Sedimentation, Filtration) | Year Treatment Equipment Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Presence Of Treatment Housing Structure? 1: Yes; 0: No | Year Treatment Housing Structure Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Presence Of Public Kiosk Or Tap Stand? 1: Yes; 0: No | Year The Kiosk Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction
2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Gakenke |  |  | Gahama Kisaro network | 865 | 865 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Intake Structure, Pump, | Create Plan To Repair or Replace Components | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | ah |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 30000 | 7 | 14 | 1 | 30000 | 2 | 1 | 1 |  | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Gihanga II | 151 | 151 |  | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | [6 empty] | 19 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7000 | 3 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Cyungo | Rwili | Karambi |  |  | Nyamagana | 60 | 10 | 50 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyagasozi |  |  | Kararama network | 197 | 197 |  | Piped Network With Pump | 2009 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 5000 | 5 | 14 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Ngarama |  |  | Rutare-Nyirangarama gravity/Nyirangarama water point | 89 | 89 |  | Piped Network -- Gravity Only | 1960 | Government Of Rwanda | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | [9 empty] | -37 | [9 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 1960
2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Gaseke |  |  | Gisoro- Nyundo network | 176 | 65 | 111 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 6 | 10 | 2 | 7000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Kararama and Rwamugaza pumping | 965 | 965 |  | Piped Network -- Gravity Only¦Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | [5 empty] | 15 | 1 | 1 | 1 | 1 | [5 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 8000 | 7 | 14 |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Kinihira | Butunzi | Gisekuru |  |  | Miyove- Kinihira | 143 | 80 | 63 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | -8 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1989
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gihonga |  |  |  | 20 | 20 |  | Piped Network -- Gravity Only | 2016 | Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 |  |  | 29 |  |  |  |  | 19 | 1 | 1 |  |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 180 | 1 | 900 |  |  | 1 | 700 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 0 |  | 0 |  | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Rwamahwa | Cyondo |  |  |  | 173 | 150 |  | Piped Network With Pump | 2012 | Waterforpeople | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 |  |  | 15 | 25 |  |  |  |  | 15 | 1 |  |  | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 |  |  |  | 14 | 2 | 30000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 0 |  | 0 |  | 1 | 2012 | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ngoma | Kabuga | Kirambo |  |  | Nganzo-Kabarore | 131 | 40 | 138 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 2 | 2 | 1 |  | 3 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 400 | 3 |  | 2 | 800 |  | 4 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Ruhondo |  |  | Kishwi network | 184 | 46 |  | Piped Network -- Gravity Only | 2003 | Goverment | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 16 |  | 16 |  |  |  |  | 19 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 700 | 2 |  | 2 | 680 |  | 4 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2003 | 0 |  | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Murambi 2 wpt/Nyirambuga pumping | 174 | 174 | 45 | Piped Network With Pump | 2012 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components |  |  | 25 | [6 empty] | 15 |  |  | 1 | [6 empty] | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Cyungo | Marembo | Murambo |  |  |  | 586 | 541 |  | Piped Network -- Gravity Only | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 |  | 25 |  | 25 |  |  |  |  | 15 | 1 |  | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 5 | 1 |  |  | 5 |  | 1 | 1234 |  | 10 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 0 |  | 1 | 2012 | 0 |  | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point at Refectory APEKI Tumba/Nyirambuga pumping | 115 | 115 | 106 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 25 |  | 25 |  |  |  |  | 15 |  |  | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 |  | 1 | 100 |  | 6 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Murambi | Gatwa | Akarambi |  |  | Mutagata Motorised Network | 206 | 100 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 4 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Masoro | Kabuga | Rubaya |  |  | Mutagata motorised network | 167 | 167 | 100 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 1900 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gitaba |  |  | Musenge network | 195 | 95 | 52 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Other Concrete Structures Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 19 | 1 | 1 | 1 | 2 | 2 | 1 | 1 |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Ngoma | Karambo | Jyambere |  |  | Gahama network | 117 | 65 | 67 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Intake Structure, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 |  |  |  |  | 17 | 2 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1800 | 2 | 1 | 1 | 1200 |  | 5 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 135 | 68 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Distribution Line, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 1 | 2 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Tumba | Taba | Kamuragi |  |  | Water point chez Safari/Nyirambuga pumping system | 154 | 154 | 86 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Karama |  |  | Bitete-Muvumu | 121 | 35 | 22 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Conduction Line, Other Concrete Structures | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 2 | 1 | 2 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1000 | 4 | 6 | 1 | 4000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Gicumbi | Mutete | Nyarubuye | Rugarama |  |  | rukondo | 162 | 140 | 102 | Piped Network -- Gravity Only | 2012 | G. Thierry | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 | 25 |  | 25 |  |  |  |  | 15 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4500 | 4 |  | 1 | 4500 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 0 |  | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Rweya |  |  | kirikumuryango network | 212 | 110 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Masoro | Shengampuri | Mutagata |  |  |  | 124 | 124 | 8 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 15 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Buyoga | Gahororo | Bunyana |  |  | Ndarage | 108 | 100 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring¦Groundwater (Well, Etc.) | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 |  |  |  |  | 20 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 6700 | 5 |  | 1 | 6700 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Rebero |  |  | Water point at Rebero/Matonyanga gravity | 175 | 175 |  | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 20 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Burega | Taba | Nyagisozi |  |  | Rwamugaza | 520 | 520 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kanyoni |  |  | charity water 203.032 | 640 | 640 |  | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 2000 | 2 | 2 | 1 | 500 | 3 | 1 | 1 |  | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Rwanzu |  |  | Rwanzu wpt behind TCT/Nyirambuga pumping | 154 | 154 |  | Piped Network With Pump | 2012 | Gor | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 15 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 11 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kinini |  |  | BF at GS Rukingu/Gashinge gravity | 250 | 250 | 85 | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 26 | [6 empty] | 16 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2013 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 165 | 80 | 185 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Intake Structure, Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 2 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Bikamba |  |  | Rwamugaza | 205 | 20 |  | Piped Network -- Gravity Only | 2003 | Goverment | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Karambi |  |  | Karambi water point/Tare-Rusiga pumping | 164 | 164 | 72 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 |  | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 10 | 8 | 1 | 4000 | 1 |  | 3 | 8000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kinihira | Butunzi | Akamiyove |  |  | Nyamagana-Kinihira | 132 | 60 | 100 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Murambi | Gatwa | Akarambi |  |  | Mutagata Motorised Network | 206 | 106 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 4 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Kararama network | 965 | 965 |  | Piped Network With Pump | 2009 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 12 | 22 | 12 | 22 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 5000 | 14 | 23 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza network | 229 | 229 | 29 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Buyoga | Mwumba | Nyamwiza |  |  | kiruruma | 149 | 120 |  | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 |  |  |  |  | 20 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3 | 9000 | 11 |  | 3 | 9000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Cyinzuzi | Migendezo | Marembo |  |  | 0 | 735 | 735 | 29 | Piped Network With Pump | 2009 | Umushinga Witwa Ema | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 12 | 22 | 12 | 22 | -1 | 12 |  |  | 12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 5000 | 16 | 23 | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 229 | 200 |  | Piped Network -- Gravity Only | 2005 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 18 | 19 | 18 | 19 | [5 empty] | 19 | 1 | 1 | 1 | 1 | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2000 | 1 | 2 |  |  |  | 2 | 1 | Start Chamber | 2005 | 1 | 2016 | 1 | 2005 | 1 | 2016 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Burega | Karengeli | Bugoboka |  |  | Rwamugaza network | 80 | 80 | 23 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 35000 | 7 | 14 | 1 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Base | Rwamahwa | Cyondo |  |  | Ruramba | 173 | 150 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 29 | 19 | 29 | 19 | [5 empty] | 19 | 1 | 3 | 1 | 1 | [5 empty] | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 4500 | 2 | 2 |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Kabuga |  |  |  | 119 | 119 | 96 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Nyarurembo |  |  | Mutagata motorised network | 144 | 48 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Burega | Butangampundu | Gacyamo |  |  | Rwamugaza | 550 | 550 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 12 | 25 | 15 | 25 | -1 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 5000 | 16 | 23 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Karambi |  |  | Gahama Kisaro network | 184 | 184 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Pump, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 30000 | 7 | 14 | 1 | 30000 | 2 | 1 | 1 |  | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Buyoga | Karama | Cyasenga |  |  | Water point near GS Kadendegere/Nyirambuga pumping | 165 | 165 | 145 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Gishyita |  |  | Bitete-Rwahi network | 205 | 60 | 219 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 600 | 6 | 6 | 1 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza | 229 | 10 |  | Piped Network -- Gravity Only | 2003 | Goverment | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 12 | 12 | 2 | 35000 |  | 3 | 1 | "Springbox" --Intake Structure At A Spring | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Buyoga | Busoro | Rugarama |  |  | Water point at EP Busoro/Nyirambuga pumping system | 189 | 189 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 25 | [6 empty] | 15 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 |  |  |  |  | 4 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Muduha |  |  | Muduha water point/Matonyanga gravity | 160 | 160 | 133 | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 30 | [6 empty] | 20 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2017 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 165 | 32 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Gitwa |  |  | Gitwa water point/Nkombe gravity system | 134 | 134 | 60 | Piped Network -- Gravity Only | 2013 | Coforwa | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 5 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2002
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kibaya |  |  | Mutungo | 133 | 73 |  | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Conduction Line, Storage Tank, Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components |  | 7 | 17 |  | 17 |  |  |  |  | 7 |  | 2 | 2 |  | 2 |  |  |  |  | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 |  | 1 | 500 | 2 |  | 1 | 2000 |  | 1 | 0 |  |  | 1 | 2004 | 1 | 2004 | 0 |  | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Kisaro | Murama | Kibingwe |  |  |  | 122 | 122 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 2 | 30000 | 7 | 14 | 1 | 30000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 27 | 27 | 262 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 500 | 2 |  | 1 | 500 | 1 |  | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 325 | 63 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Byimana |  |  | Byimana water point/Tare-Rusiga pumping | 92 | 92 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 |  |  |  | 5 | 18 |  |  | 18 | 1 | 1 |  |  |  | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 10 | 8 | 1 | 4000 |  |  |  |  | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 0 |  | 0 |  | 0 |  | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Masoro | Shengampuri | Agasharu |  |  |  | 130 | 130 |  | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Ngarama |  |  | Water point at Nyirangarama cell/Rutare-Nyirangarama gravity | 109 | 109 | 50 | Piped Network -- Gravity Only | 2013 | Local Government In Ubudehe Program | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 16 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Ruhanya |  |  | Musenge Network | 102 | 52 |  | Piped Network With Pump | 2014 | Wfp | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Marembo center water point/Nyirambuga pumping | 134 | 134 |  | Piped Network With Pump | 2012 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 25 | [6 empty] | 15 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Cyinzuzi | Migendezo | Nyamugali |  |  |  | 111 | 111 | 107 | Piped Network With Pump | 2009 | Umushinga Witwa Ema | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Intake Structure, | Create Plan To Repair or Replace Components | 22 | 12 | 22 | 12 | 22 | -1 | 12 |  |  | 12 | 2 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 5000 | 16 | 23 | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gisiza |  |  | kinywamagana pumping network | 212 | 105 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Terambere |  |  | Terambere water point/Nyabishengeshi water gravity system | 79 | 79 | 5 | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  | 16 | [7 empty] | 16 |  | 1 | [7 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  | 1 | 100 | [5 empty] | 1 | 0 |  |  | 1 | 2013 | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 50 | 45 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 214 | 214 | 23 | Piped Network With Pump | 1986 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 5000 | 15 |  | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Rwamahwa | Cyondo |  |  | Ruramba | 173 | 150 | 94 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 30 | 19 | 29 | 19 | [5 empty] | 19 | 1 | 3 | 1 | 1 | [5 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 4500 | 2 | 2 |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Ngona |  |  | Bitete-Rwahi network | 122 | 28 | 30 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 600 | 6 | 6 | 1 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Cyungo | Burehe | Nyagatovu |  |  | Nyamagana | 100 | 70 | 16 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 24 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2011 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Buyoga | Butare | Ryanyirakayobe |  |  | Nyagahera | 96 | 80 | 162 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Conduction Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 29 | 17 | 27 | 17 | 27 |  |  |  |  | 17 | 2 | 2 | 1 | 1 | 1 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 2 | 6800 | 3 | 3 | 1 | 1200 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | Mutagata Gravity Network | 214 | 52 | 260 | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures Distribution Line, | Create Plan To Repair or Replace Components | 17 | 7 | 17 | 7 | 17 |  |  |  |  | 19 | 2 | 2 | 2 | 2 | 2 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3500 | 6 | 4 | 2 | 4500 |  | 12 | 1 | "Springbox" --Intake Structure At A Spring | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 325 | 65 | 29 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Rwamahwa | Mutima |  |  | Rutare I | 229 | 200 | 204 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 |  | 29 | [6 empty] | 19 | 1 |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 0 |  | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 354 | 150 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 495 | 495 | 29 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 22 | 15 | 25 | 15 | 25 | -4 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2006 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Base | Rwamahwa | Mutima |  |  | Rutare I | 169 | 140 | 23 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components |  | 19 | 29 |  | 29 |  |  |  |  | 19 |  | 1 | 1 |  | 1 |  |  |  |  | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 |  | 1 | 3800 | 2 |  | 1 | 3800 |  | 2 | 0 |  |  | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Rwamahwa | Kiruli |  |  | Migogo | 223 | 200 |  | Piped Network -- Gravity Only | 2009 | Padiri(Lake Angels). | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Distribution Line, | Create Plan To Repair or Replace Components | 22 | 12 | 22 |  | 22 |  |  |  |  | 12 | 2 | 2 | 2 |  | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 6800 | 3 |  | 1 | 6800 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 0 |  | 1 | 2009 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Masoro | Shengampuri | Mutagata |  |  |  | 124 | 124 | 91 | Piped Network With Pump | 1998 |  | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5000 | 15 |  | 2 | 5000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Musenge Network | 118 | 27 | 136 | Piped Network With Pump | 2014 | Wfp | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Rwahi |  |  | Bitete-Rwahi network | 161 | 25 | 54 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 600 | 6 | 6 | 1 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Mutoyi |  |  | Miyove-Kinihira | 119 | 65 | 5 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, Kiosk/Tap Stand | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | 18 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Buyoga | Gitumba | Remera |  |  | Kiruruma | 130 | 125 | 92 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 15 | 5 | 3 | 9000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyarunyinya |  |  | Bitete-Rwahi network | 132 | 40 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 600 | 6 | 6 | 1 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Tumba | Taba | Nyirambuga |  |  | Nyirambuga pumping station2/Nyirambuga source | 128 | 128 |  | Piped Network With Pump | 2012 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 | 25 |  | 25 | 2 | 15 | 10 |  | 15 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 8 | 5 | 1 | 50 | 1 |  | 1 | 4000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 0 |  | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2012
2017 | Rwanda | Rulindo | Burega | Karengeli | Kanunga |  |  | Rwamugaza | 275 | 275 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 16 | 6 | 16 | 6 | [5 empty] | 6 | 1 | 1 | 1 | 1 | [5 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 2 | 1 | 8000 | 20 | 16 |  |  |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Murambi | Bubangu | Karwa |  |  | rwiseke | 215 | 215 | 75 | Piped Network -- Gravity Only | 2001 | Governement (District, Wasac) And Water For People | Spring | Medium Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Consider Replacing Aging Components | Conduction Line, Distribution Network, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 14 | 4 | 14 |  | 14 |  |  |  |  | 4 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 12000 | 7 |  | 1 | 12000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2001 | 1 | 2001 | 1 | 2001 | 0 |  | 1 | 2001 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2001
2017 | Rwanda | Rulindo | Buyoga | Gahororo | Gatare |  |  | Kiruruma | 175 | 100 | 121 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 |  |  | 27 | 4 | 17 |  |  | 19 | 1 | 3 |  |  | 1 | 1 | 1 |  |  | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 9000 |  |  | 3 | 9000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 0 |  | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Rwahi |  |  | Bitete-Rwahi network | 161 | 40 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 600 | 6 | 6 | 1 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | Giko | Karambo |  |  | Karambo water point/Buramira gravity | 104 | 104 |  | Piped Network -- Gravity Only | 2015 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Burega | Taba | Lyinzovu |  |  | Rwamugaza | 505 | 505 | 53 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Buyoga | Mwumba | Nyarubuye |  |  | kiruruma | 173 | 120 | 72 | Piped Network -- Gravity Only | 2014 |  | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 |  | 29 | 4 | 17 |  |  | 20 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 6700 | 11 |  | 3 | 6700 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2016 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Mukumba |  |  | Muvumu- Taba | 92 | 20 | 32 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components |  | 16 | 26 | 16 | 26 |  |  |  |  | 16 |  | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 1 |  | 1 | 800 | 3 | 9 | 1 | 7500 |  | 1 | 0 |  |  | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Kisaro | Gitatsa | Ruberano |  |  | gahama | 132 | 100 | 85 | Piped Network With Pump | 2017 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 30000 | 7 | 14 | 2 | 30000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Gishyita |  |  | Bitete-Rwahi network | 205 | 120 | 98 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 600 | 6 | 6 | 1 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Murambi | Mvuzo | Kabuga |  |  | Gakoma network | 199 | 101 |  | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 4 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  |  | 17 |  | 17 |  |  |  |  | 7 |  |  | 1 |  | 2 |  |  |  |  | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 |  |  |  | 2 |  | 1 | 4000 |  | 2 | 0 |  |  | 0 |  | 1 | 2004 | 0 |  | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Tumba | Gahabwa | Rushaki |  |  | Rushaki water point at Habimana/Nyirambuga pumping system | 152 | 152 | 18 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  | 20 | 30 |  | 30 |  |  |  |  | 20 |  | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  | 1 | 2017 | 1 |  | 1 | 1000 |  | 2 | 0 |  |  | 1 | 2017 | 1 | 2017 | 0 |  | 1 | 2017 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Cyungo | Marembo | Nganzo |  |  | Mugomero Murambo | 150 | 132 | 104 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 |  |  |  |  | 18 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 10000 | 10 | 3 | 2 | 10000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Kigarama |  |  | Mutagata motorised network | 169 | 65 | 68 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Masoro | Kabuga | Kanunga |  |  | Mutagata motorised network | 143 | 75 | 75 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kirurumo |  |  | Bitete-Muvumu | 80 | 5 | 10 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Conduction Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 2 | 1 | 1 | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1000 | 4 | 6 | 1 | 4000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Rukozo | Buraro | Kamiyove |  |  | Kabonanyoni | 40 | 30 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 3 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point at Gisha center/Nyirambuga pumping | 133 | 133 | 104 | Piped Network With Pump | 2015 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | [9 empty] | 18 | [9 empty] | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 135 | 31 |  | Piped Network -- Gravity Only | 2014 | Water For People, Wasac And Rulindo District | Spring | Low Risk | Medium Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Other Concrete Structures Distribution Line, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point chez Hategekimana/Nyirambuga pumping | 169 | 169 | 29 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 20 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutembe | 229 | 200 | 52 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 29 | 19 | 29 |  | 29 |  |  |  |  | 19 | 1 | 1 | 1 |  | 1 |  |  |  |  | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 2700 | 2 |  | 1 | 2700 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Mbogo | Bukro | Buhira |  |  | Musenge Network | 100 | 48 | 5 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Other Concrete Structures Distribution Line, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Rukozo | Mberuka | Mataba |  |  | Kabonanyoni | 70 | 65 | 42 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyarusange |  |  | Gisoro- Nyundo network | 97 | 55 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 6 | 10 | 2 | 7000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Ngoma | Kabuga | Kiruli |  |  | Musenge network | 139 | 139 | 30 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 20 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Cyungo | Burehe | Sove |  |  | Nyamagana | 80 | 50 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | Well | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Cyamutara |  |  | Rwamugaza network | 243 | 243 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 15 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Kivubwe |  |  | Rwamugaza network | 173 | 173 | 82 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Ngoma | Karambo | Kagwa |  |  | Kabarore- Ngoma- Nyabuko network | 123 | 41 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Intake Structure, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 2 | 1 | 1 |  | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 2 | 13 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Buyoga | Karama | Kajeneni |  |  | Karambo center water point/Nyirambuga pumping | 175 | 175 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Murambi | Mvuzo | Ntyaba |  |  | 0 | 680 | 680 |  | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 35000 | 6 | 30 | 1 | 35000 | 3 | 1 | 1 |  | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyarurama |  |  | Rwamugaza network | 168 | 168 | 8 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Rukozo | Mberuka | Kabera |  |  | Kabonanyoni | 138 | 130 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Pump Station, | Create Plan To Repair or Replace Components | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Rusenyi |  |  | marenge | 156 | 156 | 96 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Mbogo | Mushali | Bukongi |  |  | Gitabage network | 168 | 72 |  | Piped Network -- Gravity Only | 2008 | Catholic Church | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 21 | 11 | 21 |  | 21 |  |  |  |  | 11 | 1 | 1 | 1 |  | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 700 | 2 |  | 1 | 500 |  | 3 | 1 | "Springbox" --Intake Structure At A Spring | 2008 | 1 | 2008 | 1 | 2008 | 0 |  | 1 | 2008 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2008
2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point/AEP Kigarama gravity | 243 | 243 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 19 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Ruri |  |  | 0 | 945 | 945 |  | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 35000 | 45 | 38 | 1 | 35000 | 3 | 1 | 1 | Collection Chamber | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Kisaro | Mubuga | Rutabo |  |  | Gahama Kisaro network | 148 | 148 | 56 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Pump, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 30000 | 7 | 14 | 1 | 30000 | 2 | 1 | 1 |  | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ngoma | Munyarwanda | Ngaru |  |  | Kabarore-Ngoma-Nyabuko network | 106 | 50 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Pump, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 2 | 1 |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 4 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Gitwa |  |  | Water point at Gasiza Health Post/Tare-Rusiga pumping | 134 | 134 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 |  | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 10 | 8 | 1 | 4000 | 1 |  | 3 | 8000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Buhande |  |  | Water point from Rutare gravity on Tare-Rusiga pumping system | 129 | 129 |  | Piped Network With Pump | 2015 | Government In Partnership With Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 |  | 28 |  |  |  |  | 18 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 8 | 8 | 2 | 2000 | 4 |  | 1 | 2000 |  | 4 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 495 | 495 | 82 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Medium Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Consider Replacing Aging Components | Storage Tank, Distribution Network, Pump Station, Treatment Equipment, Kiosk/Tap Stand | Further Technical Diagnostic Needed | 22 | 15 | -1971 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 16 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ngoma | Karambo | Butare |  |  | Shishi network | 122 | 40 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 2 | 1 | 1 |  | 1 |  |  |  |  | 3 | 2 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 700 | 2 |  | 1 | 4000 |  | 4 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Byimana |  |  | Water Point at College Foundation Sina Gerard/Tare-Rusiga pumping | 92 | 92 | 253 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 |  | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 8 | 8 | 1 | 4000 | 1 |  | 3 | 8000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Masoro | Kivugiza | Rebero |  |  | Mutagata motorised network | 376 | 123 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Murambi | Gatwa | Kigarama |  |  |  | 209 | 209 | 51 | Piped Network -- Gravity Only | 2001 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 14 | 4 | 14 |  | 14 |  |  |  |  | 20 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 12000 | 7 |  | 1 | 12000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2001 | 1 | 2001 | 1 | 2001 | 0 |  | 1 | 2001 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  |  | 151 | 100 | 125 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 20 | 1 | 1 | 2 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 11 |  | 3 | 9000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 165 | 40 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Murambi | Bubangu | Taba |  |  | rwiseke | 193 | 193 |  | Piped Network With Pump | 2001 | Governement (District, Wasac) And Water For People | Spring | Medium Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Consider Replacing Aging Components | Conduction Line, Distribution Network, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 14 | 4 | 14 |  | 14 |  |  |  |  | 4 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1200 | 7 |  | 1 | 1200 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2001 | 1 | 2001 | 1 | 2001 | 0 |  | 1 | 2001 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2001
2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Gihanga II | 151 | 151 | 23 | Piped Network -- Gravity Only | 2016 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 |  |  |  |  | 20 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7000 | 3 |  | 1 | 7000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Base | Rwamahwa | Cyondo |  |  | Ruramba | 173 | 150 | 108 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 29 |  | 29 | 19 | [5 empty] | 19 | 1 |  | 1 | 1 | [5 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 |  |  | 2 | 2 |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Gisoro- Nyundo network | 188 | 80 | 105 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 6 | 10 | 2 | 7000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Murambi | Bubangu | Gashubi |  |  | Mutagata Motorised Network | 140 | 35 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Kigamba water point/Rutomvu gravity | 172 | 172 |  | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 16 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Karera |  |  | Rwamugaza network | 182 | 182 | 29 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 17 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 14 | 1 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Base | Rwamahwa | Mutima |  |  | Rutare I | 169 | 140 | 5 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Intake Structure, | Create Plan To Repair or Replace Components | 29 | 20 | 29 | [6 empty] | 20 | 2 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 3800 | 2 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2017 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Rukozo | Mbuye | Ruhanga |  |  | Kabonanyoni | 150 | 145 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 2015 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Kingazi4 wpt/Nyakabizi1&2 | 157 | 157 | 48 | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 16 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Buyoga | Gitumba | Rutabo |  |  | kiruruma | 128 | 80 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 11 |  | 3 | 9000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Bushoki | Mukoto | Marembo |  |  | Marembo water point/Tare-Rusiga pumping | 90 | 90 | 38 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 |  | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 8 | 8 | 1 | 4000 | 1 |  | 1 | 8000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Murambi | Bubangu | Mayange |  |  | Mutagata Motorised Network | 198 | 160 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Gatsinde |  |  | Kiringo wpt/Nyirambuga pumping | 178 | 178 | 95 | Piped Network With Pump | 2012 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 25 | [6 empty] | 15 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Murambi | Mvuzo | Rurama |  |  | Mutagata Motorised Network | 155 | 60 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Gatare |  |  | Gatare water point near cafe plantation/Nyirambuga pumping | 143 | 143 | 3 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  |  | 25 | 20 | [5 empty] | 15 |  |  | 1 | 1 | [5 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 |  |  |  | 1 | 2 |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2012 | 1 | 2017 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Kisaro | Sayo | Rusongati |  |  | Kiruruma | 163 | 160 | 60 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring¦Groundwater (Well, Etc.) | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 9000 | 15 | 5 | 3 | 4000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Rimwe |  |  | kirikumuryango network | 120 | 60 | 5 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Rukozo | Mbuye | Nyarusebeya |  |  | Kabonanyoni | 60 | 55 | 87 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Ngona |  |  | Bitete-Rwahi network | 122 | 35 | 100 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 600 | 6 | 6 | 1 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Kigali |  |  | kirikumuryango network | 220 | 120 | 162 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Nyabyondo |  |  | kirikumuryango network | 312 | 150 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 10000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Burega | Butangampundu | Karugaju |  |  | Rwamugaza | 345 | 345 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 16 | 6 | 27 | 17 | [5 empty] | 17 | 1 | 1 | 1 | 1 | [5 empty] | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 2 | 1 | 8000 | 20 | 16 |  |  |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2014 | 1 | 2014 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point at Nyirabirori cell/Nyirambuga pumping | 169 | 169 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Rusiga | Kirenge | Rebero |  |  | Kirenge water point/Tare-Rusiga pumping | 181 | 181 | 117 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 10 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Masoro | Shengampuri | Umubuga |  |  | Mutagata Gravity Network | 175 | 58 | 29 | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 17 | 7 | 17 | 7 | 17 |  |  |  |  | 7 | 2 | 2 | 2 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 3500 | 6 | 4 | 2 | 4500 |  | 12 | 1 | "Springbox" --Intake Structure At A Spring | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare I | 229 | 200 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Intake Structure, Conduction Line, | Create Plan To Repair or Replace Components | 29 | 17 | 29 | [6 empty] | 19 | 2 | 2 | 1 | [6 empty] | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 1 | 4500 | 2 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2014 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Giko cell water point/Nyirambuga pumping | 134 | 134 |  | Piped Network With Pump | 2012 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Tumba | Gahabwa | Rushaki |  |  | Rushaki water point Bizimana/Nyirambuga pumping system | 152 | 152 |  | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  |  | 20 | 30 |  |  |  |  | 20 |  |  |  | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 1 | 1000 |  | 2 | 0 |  |  | 0 |  | 0 |  | 1 | 2017 | 1 | 2017 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Bubiro |  |  | Gakenke-Muyongwe-Karyango-Mugera Water point/Tare-Rusiga pumping | 300 | 300 | 119 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  | 18 | 28 |  | 28 | 5 | 18 |  |  | 18 |  | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 8 |  | 1 | 4000 | 1 |  | 3 | 4000 | 2 | 2 | 0 |  |  | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kinihira | Marembo | Cyogo |  |  | Nyamagana-Kinihira | 184 | 65 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 18 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Murambi | Gatwa | Kigarama |  |  | rwisike | 209 | 209 | 21 | Piped Network -- Gravity Only | 2001 | Governement (District, Wasac) And Water For People | Spring | Medium Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Consider Replacing Aging Components | Conduction Line, Distribution Network, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 14 | 4 | 14 |  | 14 |  |  |  |  | 4 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1200 | 7 |  | 1 | 1200 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2001 | 1 | 2001 | 1 | 2001 | 0 |  | 1 | 2001 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2001
2017 | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | Kiduha | 151 | 130 | 62 | Piped Network -- Gravity Only | 2007 | Italians(Lake Angels) | Groundwater (Well, Etc.) | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 20 | 10 | 20 | [6 empty] | 10 | 2 | 2 | 2 | [6 empty] | 2 | 2 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 2200 | 3 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2007 | 1 | 2007 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2007
2017 | Rwanda | Rulindo | Kinihira | Rebero | Taba |  |  | Miyove-Kinihira | 122 | 60 | 5 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, Kiosk/Tap Stand | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | 18 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rukozo | Mbuye | Musare |  |  | Kabonanyoni | 40 | 35 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 2 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Gitaba |  |  | Murambo catchment | 118 | 118 |  | Piped Network -- Gravity Only | 2015 | Rulindo District | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 |  | 28 |  |  |  |  | 18 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 100 | 1 |  | 1 | 1000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Bushoki | Mukoto | Muko |  |  | Rusave water supply system/Water point at Anselme Gerant | 116 | 116 | 234 | Piped Network -- Gravity Only | 2013 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 16 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 3 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 354 | 120 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Rusekabuye |  |  | Rwamugaza network | 195 | 195 | 88 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 3500 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Cyinzuzi | Rudogo | Musenyi |  |  | Kararama | 98 | 10 |  | Piped Network With Pump | 2009 | Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 12 | 22 | 12 | 22 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 5000 | 7 | 14 | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Gifuba |  |  | Rutare source catchment area | 108 | 108 |  | Piped Network -- Gravity Only | 1960 | Government | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | -27 | -37 |  | -37 | -27 |  |  |  |  | -37 | 2 | 2 |  | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 100 |  | 1 | 1 | 1000 |  |  | 1 | "Springbox" --Intake Structure At A Spring | 1960 | 1 | 1960 | 0 |  | 1 | 1960 | 1 | 1960 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1960
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Gasiza market water point1/Nyagahondo gravity system | 228 | 228 | 2000 | Piped Network -- Gravity Only | 2010 | Caritas | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  |  | 23 |  | 23 |  |  |  |  | 13 |  |  | 1 |  | 1 |  |  |  |  | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 |  |  |  | 1 |  | 2 | 1000 |  | 1 | 0 |  |  | 0 |  | 1 | 2010 | 0 |  | 1 | 2010 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2010
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Bugarura |  |  |  | 5000 | 3000 | 81 | Piped Network -- Gravity Only | 2000 | Governement (District, Wasac) And Water For People | Spring | Medium Risk | High Risk | Basic Level of Service | High Priority | 3 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 23 | 13 | 23 | 13 | 23 | 0 | 13 | 3 |  | 13 | 1 | 1 | 2 | 3 | 2 | 3 | 3 | 1 |  | 3 | 3 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 5 | 4 | 1 | 6500 | 2 | 20 | 6 | 10000 | 1 | 14 | 1 | "Springbox" --Intake Structure At A Spring | 2010 | 1 | 2010 | 1 | 2010 | 1 | 2010 | 1 | 2010 | 1 | 2010 | 1 | 2010 | 1 | Disinfection/Chlorination | 2010 | 0 |  | 1 | 2010
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Karama |  |  | Bitete-Muvumu | 121 | 40 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Conduction Line, Other Concrete Structures | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 2 | 1 | 2 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 1000 | 1000 | 4 | 6 | 1 | 4000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 495 | 495 | 78 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Conduction Line, | Create Plan To Repair or Replace Components | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ngoma | Karambo | Butare |  |  | Shishi network | 122 | 44 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Intake Structure, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 2 | 1 | 1 |  | 1 |  |  |  |  | 2 | 2 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 700 | 2 |  | 1 | 4000 |  | 4 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 35 | 35 | 81 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Magezi |  |  | Miyove-Kinihira | 141 | 60 | 89 | Piped Network -- Gravity Only | 1989 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | -8 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1989
2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Gatembe |  |  | Miyove-Kinihira | 149 | 60 | 71 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | -8 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1989
2017 | Rwanda | Rulindo | Kinihira | Butunzi | Barayi |  |  | Nyamagana-Kinihira | 151 | 80 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 3 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Bushoki | Mukoto | Marembo |  |  | Marembo police station/Tare-Rusiga pumping | 90 | 90 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 |  |  | 28 | 5 | 18 |  |  | 18 | 1 | 1 |  |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 10 | 8 | 1 | 4000 |  |  | 1 | 8000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 0 |  | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kisaro | Mubuga | Nyakarekare |  |  | Gahama Kisaro network | 150 | 150 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Other Concrete Structures Pump, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 2 | 1 | 2 | 1 |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 30000 | 7 | 14 | 1 | 30000 | 2 | 1 | 1 |  | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ngoma | Munyarwanda | Kirungu |  |  | Kabarore-Ngoma-Nyabuko network | 77 | 77 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Pump, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 2 | 1 |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 4 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Kisaro | Murama | Kibingwe |  |  | Gahama Kisaro network | 122 | 122 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 | 25 | 15 | 25 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 30000 | 6 | 12 | 1 | 30000 |  | 1 | 1 |  | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Buyoga | Karama | Karambo |  |  | Karambo water point/Nyirambuga pumping | 165 | 165 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Tare |  |  | Tare-Rusiga pumping system/Water point at Tare | 109 | 109 | 112 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Kigarama |  |  | Mutagata motorised network | 169 | 57 | 1125 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kamatongo |  |  | 0 | 1125 |  |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 3 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 22 | 12 | 27 | 17 | 27 | -1 | 12 |  |  | 17 | 3 | 1 | 3 | 3 | 3 | 1 | 1 |  |  | 3 | 3 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 3 | 2 | 3000 | 3 | 8 | 2 | 3000 | 1 | 1 | 1 |  | 2009 | 1 | 2009 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Water point at Nyagahondo source1/Nyagahondo gravity system | 228 | 228 |  | Piped Network -- Gravity Only | 2010 | Caritas | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  | 13 | 23 |  | 23 |  |  |  |  | 13 |  | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  | 1 | 100 | 1 |  | 2 | 1000 |  | 1 | 0 |  |  | 1 | 2010 | 1 | 2010 | 0 |  | 1 | 2010 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2010
2017 | Rwanda | Rulindo | Tumba | Taba | Nyirataba |  |  | Nyirataba1 water point/Nyirambuga pumping | 169 | 169 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Bukiga water point/Nyirambuga pumping | 169 | 169 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Base | Gitare | Gisiza |  |  | Rwicanyoni | 116 | 115 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | [6 empty] | 19 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 8600 | 3 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Water point near Gitera/Nyagahondo water gravity system | 228 | 228 | 88 | Piped Network -- Gravity Only | 2010 | Caritas | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  | 13 | 23 | [6 empty] | 13 |  | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1000 | 1 |  |  |  |  | 1 | 0 |  |  | 1 | 2010 | 1 | 2010 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2010
2017 | Rwanda | Rulindo | Ngoma | Karambo | Karambi |  |  | Gahama network | 117 | 29 | 8 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Intake Structure, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 |  |  |  |  | 17 | 2 | 1 | 1 | 1 | 1 |  |  |  |  | 2 | 2 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1800 | 2 | 1 | 1 | 1200 |  | 5 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Rukozo | Buraro | Kivomo |  |  | Nyamagana | 78 | 70 | 5 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Base | Cyohoha | Kabingo |  |  | Nyamagana | 65 | 60 | 23 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Base | Rwamahwa | Kiruli |  |  | Migogo | 223 | 200 | 92 | Piped Network -- Gravity Only | 2009 | Italians(Lake Angels) | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 22 | 12 | 22 |  | 25 |  |  |  |  | 12 | 2 | 2 | 2 |  | 2 |  |  |  |  | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 2 | 3000 | 3 |  | 2 | 3000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 0 |  | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Ngoma | Karambo | Karambi |  |  | Gahama network | 117 | 25 | 25 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 |  |  |  |  | 17 | 2 | 1 | 1 | 1 | 1 |  |  |  |  | 3 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1800 | 2 | 1 | 1 | 1200 |  | 5 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Buyoga | Ndarage | Kagozi |  |  | ndarage | 155 | 130 | 88 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 5000 | 5 |  | 1 | 6700 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Nyarushinya |  |  | kinywamagana pumping network | 238 | 150 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Rwahi |  |  | Bitete-Rwahi network | 450 | 450 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 600 | 6 | 6 | 1 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Gifuba |  |  | Rutare-Nyirangarama gravity system/Water point at ADEPR NYIRANGARAMA | 108 | 108 |  | Piped Network -- Gravity Only | 2015 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Murambi | Mvuzo | Munyinya |  |  | Mutagata Motorised Network | 130 | 130 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Rukozo | Buraro | Kivomo |  |  | Nyamagana | 700 | 700 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Rusiga | Gako | Gifumba |  |  | Source Murungurira/Murungurira-Nyakariba gravity system | 188 | 188 |  | Piped Network -- Gravity Only | 2010 | Local Government | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  | 13 | 23 | 13 | [5 empty] | 13 |  | 2 | 2 | 3 | [5 empty] | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 2 |  | 1 | 100 | 1 | 1 |  |  |  | 1 | 0 |  |  | 1 | 2010 | 1 | 2010 | 1 | 2010 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2010
2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Kabeza |  |  | marenge | 120 | 120 |  | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 5000 | 7 |  | 2 | 5000 | 1 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point at Gisha church/Nyirambuga Pumping | 133 | 133 | 59 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kagunda |  |  | Muvumu- Taba | 94 | 35 | 136 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components |  | 16 | 26 | 16 | 26 |  |  |  |  | 16 |  | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 |  | 1 | 800 | 3 | 9 | 1 | 7500 |  | 1 | 0 |  |  | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Nyamirembe |  |  | kirikumuryango network | 256 | 120 | 89 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 10000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Kinihira | Butunzi | Ndorandi |  |  | Nyamagana-Kinihira | 139 | 50 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | Water point chez Nsabayezu/Kivomo-Ntakara gravity | 198 | 198 |  | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  |  |  | 18 | [5 empty] | 18 |  |  |  | 3 | [5 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 2 |  |  |  |  | 1 |  |  |  | 1 | 0 |  |  | 0 |  | 0 |  | 1 | 2015 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Bushoki | Giko | Kivomo |  |  | Kivomo water point/Buramira gravity | 127 | 127 | 122 | Piped Network -- Gravity Only¦Private Tap With Piped Supply | 2015 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Rweya |  |  | kirikumuryango network | 212 | 90 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 10000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point 2 at Gisha/Nyirambuga pumping | 133 | 133 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Gitambi |  |  | Rwamugaza network | 230 | 230 | 21 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 35000 | 7 | 12 | 2 | 3500 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Buyoga | Butare | Giko |  |  | Kiduha | 151 | 130 | 60 | Piped Network -- Gravity Only | 2007 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, | Create Plan To Repair or Replace Components | 20 | 10 | 20 | [6 empty] | 10 | 2 | 2 | 2 | [6 empty] | 1 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 2200 | 3 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2007 | 1 | 2007 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2007
2017 | Rwanda | Rulindo | Cyungo | Rwili | Karambi |  |  | Nyamagana | 80 | 20 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Rusiga | Taba | Bitare |  |  | Bitare-Gahondo sources catchment area | 113 | 113 | 97 | Piped Network -- Gravity Only | 2017 | Government Of Rwanda | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 30 | 20 | 30 | [6 empty] | 20 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 400 | 2 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 1 | 2017 | 1 | 2017 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Ngoma | Kabuga | Nyabuko |  |  | Kabarore-Ngoma-Nyabuko network | 122 | 25 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring¦Groundwater (Well, Etc.) | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Intake Structure, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 2 | 1 | 1 |  | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 2 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Kigamba2 water point/Rutomvu gravity | 172 | 172 | 97 | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 16 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyarunyinya |  |  | Bitete-Rwahi network | 132 | 35 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 600 | 6 | 6 | 1 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Gitaba |  |  | Ngarama water point/Rutomvu gravity | 110 | 110 |  | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 26 | [6 empty] | 16 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2013 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Karambi |  |  | Gahama Kisaro network | 184 | 184 | 106 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 30000 | 7 | 14 | 1 | 30000 | 2 | 1 | 1 |  | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Rwambogo |  |  | Rwambogo | 156 | 50 | 12 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 29 | 19 | 29 |  | 29 |  |  |  |  | 19 | 1 | 1 | 2 |  | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 2 | 1 | 700 | 1 |  | 1 | 350 |  | 3 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Buyoga | Ndarage | Karambi |  |  | Ndarage | 112 | 100 | 123 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 6700 | 5 |  | 1 | 6700 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Mushali | Bukongi |  |  | Gitabage network | 168 | 45 |  | Piped Network -- Gravity Only | 2008 | Catholic Church | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 21 | 11 | 21 |  | 21 |  |  |  |  | 11 | 1 | 1 | 1 |  | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 700 | 2 |  | 1 | 500 |  | 3 | 1 | "Springbox" --Intake Structure At A Spring | 2008 | 1 | 2008 | 1 | 2008 | 0 |  | 1 | 2008 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2008
2017 | Rwanda | Rulindo | Burega | Butangampundu | Kisigiro |  |  | Rwamugaza | 605 | 605 | 101 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Other Concrete Structures Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 16 | 6 | 16 | 6 | [5 empty] | 6 | 1 | 1 | 1 | 2 | [5 empty] | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 8000 | 20 | 16 |  |  |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Murambi | Bubangu | Gashubi |  |  | Mutagata Motorised Network | 140 | 39 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Gitare | Mugenda I |  |  | Water point at Innocent's/Nyirambuga pumping system | 117 | 117 | 19 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Buyoga | Busoro | Rugarama |  |  | Ndarage | 189 | 170 | 78 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 6700 | 5 |  | 1 | 6700 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Murambi | Bubangu | Rebero |  |  | Mutagata Motorised Network | 148 | 70 |  | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Tumba | Barari | Gaseke |  |  | Water point chez Rujugiro/Nyirambuga pumping system | 149 | 149 |  | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 19 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Mukoto | Buvumo |  |  | Rukungeri-Bushoki cafe washing factory gravity system | 124 | 124 | 29 | Piped Network -- Gravity Only | 2007 | Local Government In Partnership With Bushoki Cafe Washing Factory | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  | 10 | 20 | [6 empty] | 10 |  | 1 | 2 | [6 empty] | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 |  | 100 | 800 | 1 |  |  |  |  | 1 | 0 |  |  | 1 | 2007 | 1 | 2007 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2007
2017 | Rwanda | Rulindo | Base | Gitare | Nyamugali |  |  | Rutembe | 229 | 200 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 29 | 19 | 29 | [6 empty] | 19 | 1 | 2 | 3 | [6 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 2 | 1 | 1 | 3500 | 2 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Burega | Butangampundu | Kisigiro |  |  | Rwamugaza | 605 | 605 | 104 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 2 | 5000 | 16 | 23 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Rwambogo |  |  | Rwambogo | 156 | 52 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 29 | 19 | 29 |  | 29 |  |  |  |  | 19 | 1 | 1 | 2 |  | 1 |  |  |  |  | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 2 | 1 | 700 | 1 |  | 1 | 350 |  | 3 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Buyoga | Busoro | Rugarama |  |  | Water at Kaziba chez Verene/Nyirambuga pumping system | 189 | 189 | 1125 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kamatongo |  |  | 0 | 1125 |  |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 3 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 22 | 17 | 27 | 17 | 27 | -1 | 12 |  |  | 17 | 1 | 3 | 3 | 3 | 3 | 1 | 1 |  |  | 3 | 3 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 2 | 2 | 3000 | 6 | 13 | 2 | 3000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Kinihira | Butunzi | Barayi |  |  | Miyove- Kinihira | 1600 | 1600 | 10 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | -8 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 3 | 1 | 8000 | 4 | 18 | 2 | 1989 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1989
2017 | Rwanda | Rulindo | Cyinzuzi | Migendezo | Gitabage |  |  | Kararama | 120 | 110 | 57 | Piped Network With Pump | 2009 | Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 5000 | 7 | 14 | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Muvumu |  |  | Muvumu- Taba | 132 | 75 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components |  | 16 | 26 | 16 | 26 |  |  |  |  | 16 |  | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 |  | 1 | 800 | 3 | 9 | 1 | 7500 |  | 1 | 0 |  |  | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | Mukoto | Buyogoma |  |  | Buyogoma water point | 130 | 130 |  | Piped Network -- Gravity Only | 2013 | Government Of Rwanda | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 16 | [9 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Burega | Butangampundu | Karambi |  |  | Rwamugaza network | 73 | 73 | 60 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 1 | 2 | 35000 | 7 | 14 | 1 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Rimwe |  |  | kirikumuryango network | 120 | 60 | 50 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Base | Cyohoha | Rubanda |  |  | Migogo | 170 | 120 | 98 | Piped Network -- Gravity Only | 2013 | Lake Angels | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 22 | 12 | 22 |  | 22 |  |  |  |  | 16 | 2 | 2 | 2 |  | 2 |  |  |  |  | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 2 | 3000 | 3 |  | 2 | 3000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 0 |  | 1 | 2009 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Ntunguru |  |  | Miyove-Kinihira | 168 | 70 | 45 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | -8 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1989
2017 | Rwanda | Rulindo | Masoro | Kivugiza | Musenga |  |  | Mutagata Gravity network | 185 | 140 | 100 | Piped Network -- Gravity Only | 1987 |  | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 17 | 7 | 17 | 7 | 17 |  |  |  |  | 18 | 2 | 2 | 2 | 2 | 2 |  |  |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3500 | 6 | 4 | 2 | 4500 |  | 12 | 1 | "Springbox" --Intake Structure At A Spring | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | Nganzo-Kabarore | 198 | 98 | 7 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 2 | 2 | 1 |  | 3 |  |  |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 400 | 3 |  | 2 | 800 |  | 5 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 77 | 70 |  | Piped Network -- Gravity Only | 2005 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 18 | 8 | 18 | 20 | [5 empty] | 19 | 1 | 1 | 1 | 1 | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7000 | 2 | 2 |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2005 | 1 | 2005 | 1 | 2005 | 1 | 2017 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Nkore source catchment | 172 | 172 | 61 | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components |  | 16 | 26 |  | 26 |  |  |  |  | 16 |  | 1 | 1 |  | 1 |  |  |  |  | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 |  | 1 | 50 | 1 |  | 1 | 2000 |  | 1 | 0 |  |  | 1 | 2013 | 1 | 2013 | 0 |  | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Magezi |  |  | Miyove-Kinihira | 141 | 80 | 3 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | -8 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1989
2017 | Rwanda | Rulindo | Rukozo | Buraro | Kabingo |  |  | Kabonanyoni | 38 | 35 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Remera |  |  | Kinyankera gravity system | 105 | 105 | 65 | Piped Network -- Gravity Only | 2010 | Local Government And Community | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  | 18 | 28 |  | 28 |  |  |  |  | 13 |  | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 100 | 1 |  | 1 | 1000 |  | 3 | 0 |  |  | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2010
2017 | Rwanda | Rulindo | Ngoma | Karambo | Jyambere |  |  | Gahama network | 117 | 52 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 |  |  |  |  | 17 | 2 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1800 | 2 | 1 | 1 | 1200 |  | 5 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Tumba | Gahabwa | Kabuga |  |  | Water point chez Ntuyenabo/Nyirambuga pumping system | 155 | 155 | 13 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 20 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Base | Cyohoha | Kabuga |  |  | Gihanga | 73 | 60 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 29 | 19 | 29 | [6 empty] | 19 | 2 | 2 | 2 | [6 empty] | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 7200 | 6 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Gihanga |  |  | Water point at Gihanga under road/Nyirambuga pumping | 152 | 152 | 95 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 30 | 20 | [5 empty] | 20 |  |  | 1 | 1 | [5 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 | 1 |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2017 | 1 | 2017 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gitaba |  |  | Musenge network | 195 | 100 | 146 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Other Concrete Structures Distribution Line, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 19 | 1 | 1 | 1 | 2 | 2 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Masoro | Kivugiza | Gasenga |  |  | Mutagata motorised network | 284 | 138 | 12 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 180 |  | Piped Network -- Gravity Only | 2012 | Padiri | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 19 | 25 | 15 | 25 |  |  |  |  | 15 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 2 | 1 | 6450 | 2 | 2 | 1 | 6450 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2016 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Rusiga | Taba | Karenge |  |  | Water point at Kukabuga/Bitare-Gahondo gravity | 112 | 112 |  | Piped Network -- Gravity Only | 1989 | Catholic Church | Spring | Medium Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 30 | 20 | 2 | [6 empty] | -8 | 1 | 1 | 3 | [6 empty] | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 2 | 2 | 400 | 1 |  |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 1 | 2017 | 1 | 1989 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 1989
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Water point at Kayenzi cell near TCT/Nyirambuga pumping system | 174 | 174 | 12 | Piped Network With Pump | 2012 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 180 |  | Piped Network -- Gravity Only¦Private Tap With Piped Supply | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 29 | 15 | 25 | 15 | 29 |  |  |  |  | 15 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 2 | 6450 | 2 | 2 | 2 | 1000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point/AEP Kigarama | 243 | 243 |  | Piped Network -- Gravity Only | 2015 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rukozo | Buraro | Kivomo |  |  | Nyamagana | 1100 | 1100 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza network | 229 | 229 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Buyoga | Karama | Karambo |  |  | Water point at Karama cell/Nyirambuga pumping | 165 | 165 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Gahama |  |  |  | 115 | 115 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Storage Tank, Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components |  |  | 16 |  | 16 |  |  |  |  | 6 |  |  | 2 |  | 2 |  |  |  |  | 2 | 2 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 |  |  |  | 1 |  | 1 | 100 |  | 1 | 0 |  |  | 0 |  | 1 | 2003 | 0 |  | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Tumba | Gahabwa | Mafene |  |  | Water point at Gahabwa cell(near EP Gahabwa)/Nyirambuga pumping | 172 | 172 | 84 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Ngoma | Karambo | Karambi |  |  | Gahama network | 117 | 33 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 |  |  |  |  | 17 | 2 | 1 | 1 | 1 | 1 |  |  |  |  | 3 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1800 | 2 | 1 | 1 | 1200 |  | 5 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza network | 229 | 229 | 74 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 35000 | 7 | 14 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kagunda |  |  | Muvumu- Taba | 94 | 20 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components |  | 16 | 26 | 16 | 26 |  |  |  |  | 16 |  | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 |  | 1 | 800 | 3 | 9 | 1 | 7500 |  | 1 | 0 |  |  | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Burega | Karengeli | Rwamiko |  |  | Rwamugaza | 440 | 440 | 93 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Rusiga | Taba | Bitare |  |  | Muvumu-Taba | 113 | 20 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Storage Tank, Kiosk/Tap Stand | Create Plan To Repair or Replace Components |  | 16 | 26 | 16 | 26 |  |  |  |  | 16 |  | 1 | 2 | 1 | 1 |  |  |  |  | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 |  | 1 | 800 | 3 | 9 | 1 | 7500 |  | 1 | 0 |  |  | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | Mukoto | Gatare |  |  | Gatare water point/Tare-Rusiga pumping | 129 | 129 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 |  | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 10 | 8 | 1 | 4000 | 1 |  | 1 | 8000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Kazi |  |  | Rwamugaza network | 184 | 184 |  | Piped Network -- Gravity Only | 2003 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 14 | 1 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Gitwa |  |  | Rwamugaza network | 120 | 120 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Tumba | Taba | Ruvumba |  |  | Water point chez Darage/Nyirambuga pumping system | 109 | 109 | 92 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 15 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 100 | 158 | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 25 | 19 | 25 | 15 | 29 |  |  |  |  | 20 | 2 | 3 | 2 | 1 | 1 |  |  |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 3 | 2 | 2 | 1000 | 3 | 1 | 2 | 1200 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2016 | 1 | 2012 | 1 | 2012 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Gisoro-Nyundo network | 188 | 30 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Storage Tank, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2013 | 30 | 6 | 10 | 2 | 7000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Gihinga |  |  | 0 | 850 | 850 |  | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 35000 | 2 | 6 | 1 | 1000 | 3 | 1 | 1 |  | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatiba |  |  | Gihanga II | 151 | 151 | 58 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 19 | 29 | [6 empty] | 19 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7000 | 3 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Kinihira | Butunzi | Kiniihira |  |  | Miyove- Kinihira | 118 | 60 | 195 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | -8 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1989
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Kigali |  |  | Gisoro- Nyundo network | 220 | 25 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 6 | 10 | 2 | 7000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Buyoga | Mwumba | Gakoma |  |  | Water point at Gakoma/Nyirambuga pumping | 176 | 176 | 28 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kisaro | Mubuga | Rutabo |  |  | gahama | 148 | 120 | 39 | Piped Network With Pump | 2017 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 30 | 20 | 25 |  | 25 |  |  |  |  | 20 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 12000 | 2012 |  | 2 | 12000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 1 | 2017 | 1 | 2012 | 0 |  | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Ngoma | Mugote | Kiboha |  |  | Kabarore-Ngoma- Nyabuko network | 74 | 35 | 86 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 4 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 118 | 32 | 149 | Piped Network -- Gravity Only | 1997 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 |  |  |  |  | 19 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 700 | 1 | 2 | 2 | 800 |  | 5 | 1 | Start And Collection Chamber | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  | Kibuye | 186 | 37 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 |  | 19 | 29 |  |  |  |  | 19 | 1 | 1 |  | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1500 |  | 1 | 1 | 1000 |  | 2 | 1 | Start And Collection Chamber | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rusiga | Gako | Gifumba |  |  | Gifumba gravity system | 188 | 188 |  | Piped Network -- Gravity Only | 2010 | Local Government | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  | 13 | 23 | [6 empty] | 13 |  | 3 | 2 | [6 empty] | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 |  | 1 | 700 | 1 | [5 empty] | 0 |  |  | 1 | 2010 | 1 | 2010 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2010
2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point/AEP Kigarama gravity | 243 | 243 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 19 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Ruhanga |  |  | Ruhanga2 water point/Tare-Rusiga pumping | 147 | 147 | 106 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 |  | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 10 | 8 | 1 | 4000 | 1 |  | 3 | 8000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gicumbi |  |  | Musenge Network | 141 | 35 | 50 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Other Concrete Structures Distribution Line, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Ngoma | Munyarwanda | Ngaru |  |  | Kabarore-Ngoma-Nyabuko network | 106 | 56 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Pump, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 2 | 1 |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 4 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Kabagabaga |  |  | kirikumuryango network | 850 | 850 | 75 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Karindi |  |  |  | 120 | 45 | 97 | Piped Network -- Gravity Only | 2007 |  | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 10 | 11 | [6 empty] | 19 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1000 | 1 |  |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2007 | 1 | 1998 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 118 | 21 |  | Piped Network -- Gravity Only | 1997 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 |  |  |  |  | 19 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 700 | 1 | 2 | 2 | 800 |  | 5 | 1 | Start And Collection Chamber | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Murambi | Gatwa | Gatare |  |  | rwiseke | 179 | 179 | 83 | Piped Network -- Gravity Only | 2001 | Governement (District, Wasac) And Water For People | Spring | Medium Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Consider Replacing Aging Components | Conduction Line, Distribution Network, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed |  | 4 | 14 |  | 14 |  |  |  |  | 4 |  | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 |  | 1 | 1200 | 7 |  | 1 | 1200 |  | 1 | 0 |  |  | 1 | 2001 | 1 | 2001 | 0 |  | 1 | 2001 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2001
2017 | Rwanda | Rulindo | Ngoma | Kabuga | Kirambo |  |  | Kabarore-Ngoma-Nyabuko network | 131 | 48 | 5 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 2 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 50 | 45 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 14 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 5 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 450 | 450 | 79 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 14 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 5 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Ngoma | Munyarwanda | Busizi |  |  | Kabarore-Ngoma-Nyabuko network | 100 | 21 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 2 | 1 |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 4 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Bikamba |  |  | Rwamugaza network | 205 | 205 | 12 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 180 | 112 | Piped Network -- Gravity Only | 2012 | Padiri | Spring¦Groundwater (Well, Etc.) | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 29 | 19 | 25 | 15 | [5 empty] | 15 | 1 | 1 | 1 | 1 | [5 empty] | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 3 | 2 | 1 | 6450 | 2 | 2 |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2012 | 1 | 2012 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Masoro | Shengampuri | Umubuga |  |  | Mutagata Gravity network | 175 | 63 |  | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures Distribution Line, | Create Plan To Repair or Replace Components | 17 | 7 | 17 | 7 | 17 |  |  |  |  | 19 | 2 | 2 | 2 | 2 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3500 | 6 | 4 | 2 | 4500 |  | 12 | 1 | "Springbox" --Intake Structure At A Spring | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Gitare | Gihora |  |  | Gihora2 water point/Rutomvu gravity | 101 | 101 |  | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components |  |  | 26 | [6 empty] | 16 |  |  | 1 | [6 empty] | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2013 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Tumba | Gahabwa | Kagusa |  |  | Kagusa water point/Nyirambuga pumping | 146 | 146 | 71 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Buhita |  |  | Miyove-Kinihira | 131 | 60 |  | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, Kiosk/Tap Stand | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | 18 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Muvumu |  |  | Muvumu- Taba | 400 | 400 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components |  | 16 | 26 | 16 | 26 |  |  |  |  | 16 |  | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 |  | 1 | 800 | 3 | 9 | 1 | 7500 |  | 1 | 0 |  |  | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | Mukoto | Marembo |  |  | Water point at Marembo school/Tare-Rusiga pumping | 90 | 90 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 |  |  | 28 | 5 | 18 |  |  | 18 | 1 | 1 |  |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 10 | 8 | 1 | 4000 |  |  | 1 | 8000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 0 |  | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Ruhanga |  |  | Ruhanga center Water point/Tare-Rusiga pumping | 147 | 147 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 |  |  | 28 | 5 | 18 |  |  | 18 | 1 | 1 |  |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 10 | 8 | 1 | 4000 |  |  | 3 | 8000 | 2 | 2015 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 0 |  | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Bushoki | Giko | Rugote |  |  | Rugote water point/Rutomvu gravity system | 147 | 147 | 80 | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 26 | [6 empty] | 16 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2013 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Gashinge |  |  | Mutagata motorised network | 229 | 149 | 48 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Buyoga | Gitumba | Rutabo |  |  |  | 128 | 80 |  | Piped Network With Pump | 2014 |  | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 11 |  | 3 | 9000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Gihinga |  |  | 0 | 850 | 850 |  | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Other Concrete Structures | Create Plan To Repair or Replace Components | 29 | 19 | 29 | 19 | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 | 2 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 35000 | 2 | 6 | 1 | 1000 | 3 | 1 | 1 |  | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Mbogo | Mushali | Nyakabuye |  |  | Matyazo network | 147 | 147 | 5 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 29 | 19 | 29 | 19 | 29 |  |  |  |  | 19 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 3 | 4 | 1 | 4300 | 1 | 2 | 1 | 1800 |  | 4 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Nyamagana | 100 | 95 | 12 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 14 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 1 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 180 | 106 | Piped Network -- Gravity Only | 2012 | Padiri | Spring¦Groundwater (Well, Etc.) | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 25 | 19 | [5 empty] | 15 | 1 | 1 | 1 | 1 | [5 empty] | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 6450 | 3 | 2 |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Well | 2016 | 1 | 2016 | 1 | 2012 | 1 | 2016 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Kabagabaga |  |  | kirikumuryango network | 181 | 75 | 143 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Rutonde |  |  | kirikumuryango network | 241 | 98 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Base | Gitare | Mugenda I |  |  | Gitare center water point/Nyirambuga pumping system | 117 | 117 |  | Piped Network With Pump | 2012 | Local Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 25 | [6 empty] | 15 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 2 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Gasiza center water point served by gravity before Tare pumping | 228 | 228 | 68 | Piped Network With Pump | 2015 | Gvt And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 |  | 28 |  |  |  |  | 18 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 8 | 8 | 1 | 4000 | 1 |  | 1 | 2000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 135 | 67 | 40 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Other Concrete Structures Distribution Line, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyarunyinya |  |  | kinywamagana pumping network | 132 | 92 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Rutonde |  |  | kirikumuryango network | 1350 | 1350 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Base | Gitare | Mugenda I |  |  | Gitare cell water point/Nyirambuga pumping system | 117 | 117 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 15 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | [8 empty] | 6 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza network | 229 | 229 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Nyamagana | 850 | 850 | 16 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Buyoga | Butare | Ryanyirakayobe |  |  | Nyagahera | 96 | 80 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6800 | 3 |  | 3 | 1200 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Amahoro |  |  | Gicumbi Mutete network | 109 | 109 |  | Piped Network With Pump | 2009 | Government | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 22 | 12 | 22 | 12 | 22 | -1 | 12 |  |  | 12 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 30000 | 5 | 10 | 2 | 30000 | 1 | 1 | 1 |  | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Bushoki | Giko | Cyili |  |  | Rutomvu source catchment area and intake structures | 169 | 169 |  | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 |  | 26 |  |  |  |  | 16 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 100 | 1 |  | 2 | 2000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 0 |  | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Gihanga |  |  | Water point at Rusura Primary school/Nyirambuga pumping | 152 | 152 | 55 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 30 | [6 empty] | 20 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2017 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kalindi |  |  | Musenge Network | 120 | 65 | 86 | Piped Network With Pump | 2014 | Wfp | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Kinihira | Rebero | Ndusu |  |  | Miyove-Kinihira | 146 | 60 | 89 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, Kiosk/Tap Stand | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | 18 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Mwagiro |  |  | Kirikumuryango network | 139 | 50 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Masoro | Kabuga | Karambi |  |  | Mutagata motorised network | 127 | 127 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Buramira water point/Buramira gravity | 104 | 104 | 201 | Piped Network -- Gravity Only | 2015 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | kinywamagana pumping network | 281 | 80 | 164 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kigarama |  |  | kinywamagana pumping network | 233 | 69 | 87 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 118 | 31 |  | Piped Network -- Gravity Only | 1997 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 |  |  |  |  | 19 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 2 | 2 | 1 | 700 | 1 | 2 | 2 | 800 |  | 5 | 1 | Start And Collection Chamber | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Burega | Karengeli | Kiziba |  |  | Rwamugaza | 400 | 400 | 46 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 16 | 6 | 16 | 6 | [5 empty] | 6 | 1 | 1 | 1 | 1 | [5 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 2 | 1 | 8000 | 20 | 16 |  |  |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | nyiragahera | 151 | 105 | 29 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 11 |  | 3 | 9000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Base | Rwamahwa | Mutima |  |  | Rutare I | 169 | 140 | 43 | Piped Network -- Gravity Only | 2016 |  | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | [8 empty] | 19 | 1 | [8 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [7 empty] | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Cyohoha | Buramba |  |  | Gihanga | 163 | 120 | 122 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | [8 empty] | 19 | 1 | [8 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [7 empty] | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Kigarama |  |  | Mutagata motorised network | 169 | 47 | 92 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 100 | 33 | Piped Network -- Gravity Only | 2012 | Padiri | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 | -1985 | 20 | 25 |  |  |  |  | 15 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 2 | 1 | 6450 | 1 | 3 | 2 | 6800 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2 | 1 | 2017 | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Buyoga | Gahororo | Gitabura |  |  | kiruruma | 129 | 96 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 18160 |  | 27 | 4 | 17 |  |  | 7636 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 9000 | 4 |  | 3 | 9000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 20147 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 9633
2017 | Rwanda | Rulindo | Bushoki | Mukoto | Gatare |  |  | Nkombe gravity system catchment area | 129 | 129 |  | Piped Network -- Gravity Only | 2002 | Coforwa | Spring¦Lake/Reservoir | Medium Risk | Low Risk | High Level of Service | Low Priority | 8 | Consider Replacing Aging Components | Conduction Line, Distribution Network, Pump, Pump Station, Treatment Equipment, Kiosk/Tap Stand | Further Technical Diagnostic Needed | 15 | 5 | 15 |  | 15 |  |  |  |  | 5 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 |  | 3 | 100 | 1 |  | 1 | 1000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2002 | 1 | 2002 | 1 | 2002 | 0 |  | 1 | 2002 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2002
2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatiba |  |  | Gihanga II | 151 | 151 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | [6 empty] | 19 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7000 | 3 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Water point at GS Ngarama/Rutumvo gravity | 172 | 172 |  | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 16 | [9 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | Giko | Cyili |  |  | Cyili2 water point/Rutomvu gravity | 169 | 169 |  | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  |  | 26 | [6 empty] | 16 |  |  | 1 | [6 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2013 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Burega | Taba | Nyagisozi |  |  | Rwamugaza | 505 | 505 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 3 | 2 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Gatobotobo |  |  | Rwamugaza network | 103 | 103 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Rugogwe |  |  | Rwamugaza network | 192 | 192 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Rusiga | Gako | Kabunigu |  |  | Gako-Kabunigo water point/Tare-Rusiga pumping | 219 | 219 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 10 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Tumba | Gahabwa | Rushaki |  |  | Water point at Marembo center/Nyirambuga pumping | 152 | 152 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Buyoga | Karama | Cyasenga |  |  | Water point at Cyasenga/Nyirambuga pumping | 165 | 165 | 107 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kinihira | Rebero | Kirwa |  |  | Miyove-Kinihira | 187 | 80 | 103 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, Kiosk/Tap Stand | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | 18 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Murambi | Mvuzo | Rurama |  |  | Mutagata Motorised Network | 155 | 52 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Tumba | Taba | Nyirataba |  |  | Water point at Nyirataba/Nyirambuga pumping | 169 | 169 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Rwamugaza network | 193 | 193 | 15 | Piped Network With Pump | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 45 | 30 | 92 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 100 |  | Piped Network -- Gravity Only | 2012 | Padiri | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 25 | 15 | 25 | 15 | 30 |  |  |  |  | 20 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 3 | 2 | 2 | 6450 | 3 | 2 | 2 | 1500 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2017 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Amahoro |  |  | Mutagata motorised network | 120 | 120 | 14 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Buyoga | Butare | Gasave |  |  | KIDUHA | 114 | 100 | 129 | Piped Network -- Gravity Only | 2007 | Italians(Lake Angels) | Groundwater (Well, Etc.) | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Conduction Line, Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 20 | 10 | 20 |  | 20 |  |  |  |  | 17 | 2 | 2 | 1 |  | 2 |  |  |  |  | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 2200 | 3 |  | 1 | 2200 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2007 | 1 | 2007 | 0 |  | 1 | 2007 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Kinihira | Marembo | Kigali |  |  | Nyamagana-Kinihira | 189 | 60 | 119 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kinihira | Marembo | Kigali |  |  | Nyamagana- Kinihira | 189 | 70 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo |  |  | marenge | 203 | 203 | 121 | Piped Network With Pump | 1998 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 5000 | 15 |  | 1 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Bwishya |  |  | Miyove-Kinihira | 181 | 60 | 52 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | -8 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1989
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Ruhanya |  |  | Mutungo | 102 | 50 | 5 | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Storage Tank, Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components |  | 7 | 17 |  | 17 |  |  |  |  | 7 |  | 1 | 2 |  | 2 |  |  |  |  | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 |  | 1 | 500 | 2 |  | 1 | 2000 |  | 3 | 0 |  |  | 1 | 2004 | 1 | 2004 | 0 |  | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Cyungo | Burehe | Gitandi |  |  | Nyamagana | 40 | 35 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 14 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 2100 | 11 | 15 | 1 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kanyoni |  |  | 0 | 640 | 640 |  | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 35000 | 10 | 8 | 1 | 35000 | 3 | 1 | 1 |  | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rusiga | Taba | Gahondo |  |  | Gahondo water point chez Safari/Bitare-Gahondo gravity | 83 | 83 | 100 | Piped Network -- Gravity Only | 1989 | Catholic Church | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 30 | 20 | [7 empty] | -8 | 1 | 1 | [7 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 2 | 2 | 400 | [5 empty] | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 1 | 2017 | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 1989
2017 | Rwanda | Rulindo | Mbogo | Mushali | Buraro |  |  | Matyazo network | 155 | 55 | 15 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 |  |  |  |  | 19 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 4 | 1 | 4300 | 1 | 2 | 1 | 1800 |  | 4 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Cyungo | Burehe | Sove |  |  | Nyamagana | 30 | 15 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Conduction Line, Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 2 | 1 | 1 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 29 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Kigomwa |  |  | marenge | 118 | 118 | 110 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 | 6 | 19 | 9 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 500 | 15 |  | 2 | 500 | 1 | 3 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | Filtration | 2016 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Kigali |  |  | Gisoro- Nyundo network | 220 | 110 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 6 | 10 | 2 | 7000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Gatagara |  |  | 0 | 725 | 725 |  | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 35000 | 10 | 6 | 1 | 35000 | 3 | 1 | 1 |  | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Mukoto | Rusave |  |  | Rusave water point/Tare-Rusiga pumping | 101 | 101 | 92 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 |  |  | 28 | 5 | 18 |  |  | 18 | 1 | 1 |  |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 8 | 8 | 1 | 4000 |  |  | 1 | 8000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 0 |  | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Mukumba |  |  | Bitete-Muvumu | 92 |  | 93 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 2 | 1 | 2 | 1 |  |  |  |  | 3 | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 3 | 1 | 1 | 1000 | 4 | 6 | 1 | 4000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 118 | 25 |  | Piped Network -- Gravity Only | 1997 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 |  |  |  |  | 19 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 700 | 1 | 2 | 2 | 800 |  | 5 | 1 | Start Chamber And Collection Chamber | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Murambi | Mvuzo | Kabuga |  |  |  | 199 | 199 |  | Piped Network -- Gravity Only | 2001 | Governement (District, Wasac) And Water For People | Spring | Medium Risk | Low Risk | High Level of Service | Low Priority | 8 | Consider Replacing Aging Components | Conduction Line, Distribution Network, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 29 | 4 | 14 |  | 14 |  |  |  |  | 4 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 12000 | 7 |  | 1 | 12000 |  | 7 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2001 | 1 | 2001 | 0 |  | 1 | 2001 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2001
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Gatobotobo |  |  | Rwamugaza network | 103 | 103 | 75 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Masoro | Kabuga | Kanunga |  |  | Mutagata motorised network | 143 | 68 | 76 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Karama |  |  | Bitete-Muvumu | 121 | 45 | 87 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Conduction Line, Other Concrete Structures | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 2 | 1 | 2 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1000 | 4 | 6 | 1 | 4000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Ngoma | Kabuga | Nyabuko |  |  | Kabarore-Ngoma-Nyabuko network | 122 | 35 | 18 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Intake Structure, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 2 | 1 | 1 |  | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 4 | 5 | 2 | 8000 | 14 |  | 2 | 7000 | 2 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Mushali | Gitaba |  |  | Matyazo network | 118 | 100 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 29 | 19 | 29 | 19 | 29 |  |  |  |  | 19 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 4 | 1 | 4300 | 1 | 2 | 1 | 1800 |  | 4 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Gitaba |  |  | Rutembe catchment area | 118 | 118 | 91 | Piped Network -- Gravity Only | 2015 | Rulindo District | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 18 | 28 | 18 | 28 |  |  |  |  | 18 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 100 | 1 | 1 | 1 | 1000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Rutonde |  |  | kirikumuryango network | 241 | 150 | 5 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Buyoga | Gitumba | Munini |  |  | Kiruruma | 158 | 153 | 73 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 15 | 5 | 3 | 9000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kibaya |  |  | Mutungo | 133 | 60 |  | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 4 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  | 7 | 17 |  | 17 |  |  |  |  | 7 |  | 2 | 2 |  | 2 |  |  |  |  | 3 | 3 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 |  | 1 | 2000 | 2 |  | 1 | 2000 |  | 1 | 0 |  |  | 1 | 2004 | 1 | 2004 | 0 |  | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Cyinzuzi | Migendezo | Gitabage |  |  | 0 | 735 | 735 |  | Piped Network With Pump | 2009 | Umushinga Witwa Ema | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 12 | 22 | 12 | 22 | -1 | 12 |  |  | 12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 2 | 5000 | 16 | 23 | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Budaha |  |  | Water point at Budaha nearby pumping station/Tare pumping | 205 | 205 | 10 | Piped Network With Pump | 2015 | Gvt And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  | 18 | 28 |  | 28 |  |  |  |  | 18 |  | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 8 |  | 1 | 4000 | 1 |  | 1 | 2000 |  | 1 | 0 |  |  | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Base | Cyohoha | Kabingo |  |  | Nyamagana | 70 | 60 | 9 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Base | Rwamahwa | Kiruli |  |  | Migogo | 129 | 120 |  | Piped Network -- Gravity Only | 2009 | Italians(Lake Angels) | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Storage Tank, Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 22 |  | 22 |  | 22 |  |  |  |  | 12 | 1 |  | 2 |  | 2 |  |  |  |  | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 |  |  | 3 |  | 2 | 3000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 0 |  | 1 | 2009 | 0 |  | 1 | 2009 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Ngoma | Mugote | Sakara |  |  | Kararama pumping network | 99 | 99 |  | Piped Network With Pump | 2007 | Government | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 4 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 20 | 10 | 20 | 10 | 20 | -3 | 10 |  |  | 10 | 2 | 1 | 1 | 1 | 1 | 2 | 2 |  |  | 3 | 3 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 4 | 3 | 1 | 1500 | 25 | 20 | 4 | 30000 | 2 | 47 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2007 | 1 | 2007 | 1 | 2007 | 1 | 2007 | 1 | 2007 | 1 | 2007 | 1 | 2007 | 0 |  |  |  |  | 1 | 2007
2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Karera |  |  | Rwamugaza network | 182 | 182 | 6 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Buyoga | Gitumba | Nyarubuye |  |  | Kiruruma | 146 | 140 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 15 | 5 | 3 | 9000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Kisaro | Mubuga | Rutabo |  |  | Gahama Kisaro network | 740 | 740 | 8 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 30000 | 7 | 14 | 1 | 30000 | 2 | 1 | 1 |  | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Buyoga | Gitumba | Munini |  |  | Kiruruma | 158 | 150 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 | 17 | 27 |  |  |  |  | 17 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 15 | 5 | 3 | 9000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Kisaro | Mubuga | Gako |  |  | Gahama Kisaro network | 955 | 955 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Pump, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 30000 | 7 | 14 | 1 | 30000 | 2 | 1 | 1 |  | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Kivure source/Buramira gravity system | 134 | 134 |  | Piped Network -- Gravity Only | 2015 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 |  |  |  |  | 18 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 100 | 2 | 2 | 1 | 1000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Rugaragara |  |  | charity water 203.033 | 815 | 815 | 149 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 35000 | 10 | 6 | 1 | 1000 | 3 | 1 | 1 |  | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Ruri |  |  | Mutagata Gravity network | 189 | 40 |  | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 17 | 7 | 17 | 7 | 17 |  |  |  |  | 7 | 2 | 2 | 2 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3500 | 6 | 4 | 2 | 4500 |  | 12 | 1 | "Springbox" --Intake Structure At A Spring | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Burega | Butangampundu | Kigabiro |  |  | Rwamugaza | 565 | 565 |  | Piped Network With Pump | 2012 | 2 | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Karambi |  |  | Nyabishengeshi source/Nyabishengeshi gravity system | 79 | 79 |  | Piped Network -- Gravity Only | 2013 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 |  | 26 |  |  |  |  | 16 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1000 | 1 |  | 4 | 4000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 0 |  | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Rusenyi |  |  | marenge | 156 | 156 | 207 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 |  | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 2 | 0 |  |  | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatimba |  |  | kinywamagana pumping network | 217 | 10 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kanyoni |  |  | charity water 203.037 | 640 | 640 | 5 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 2000 | 3 | 6 | 1 | 2000 | 3 | 1 | 1 |  | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rukozo | Mberuka | Mataba |  |  | Kabonanyoni | 75 | 70 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Kabirizi |  |  | Rwamugaza network | 148 | 148 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 14 | 1 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Murambi | Bubangu | Ruhunga |  |  | Mutagata Motorised Network | 112 | 112 | 145 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 6 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  | Musenge Network | 186 | 41 |  | Piped Network With Pump | 2014 |  | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyagasozi |  |  | Rwamugaza network | 197 | 197 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 |  |  |  |  | 17 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 35000 | 7 | 14 | 1 | 35000 |  | 1 | 1 | Null | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Nyamagana | 850 | 850 | 6 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Base | Gitare | Gisiza |  |  | Rwicanyoni | 116 | 110 | 58 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | [6 empty] | 19 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 8600 | 3 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Bugarura |  |  | kirikumuryango network | 119 | 61 | 111 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gicumbi |  |  | Musenge Network | 141 | 30 | 255 | Piped Network With Pump | 2014 |  | Spring | Low Risk | Medium Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Other Concrete Structures Distribution Line, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 325 | 70 | 11 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Cyungo | Marembo | Murambo |  |  | Mugomero Marembo | 161 | 150 |  | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 |  |  |  |  | 18 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 10000 | 10 | 3 | 2 | 10000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rukozo | Buraro | Murwa |  |  | Kabonanyoni | 800 | 800 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Tumba | Barari | Gaseke |  |  | Water point at Rukore Primary School/Nyirambuga pumping | 149 | 149 |  | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 20 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Buyoga | Karama | Cyasenga |  |  | Water point at GS Kadendegere/Nyirambuga pumping | 165 | 165 | 29 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 4 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutembe | 229 | 200 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 29 | 19 | 29 | [6 empty] | 19 | 2 | 2 | 1 | [6 empty] | 3 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 2 | 2 | 1 | 4000 | 2 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Murambi | Mvuzo | Iraro |  |  | Mutagata Motorised Network | 147 | 147 |  | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Tumba | Misezero | Taba |  |  | Water point chez Nsekanabo/Nyirambuga pumping | 100 | 100 | 56 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 30 | [6 empty] | 15 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2017 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Base | Gitare | Nyamugali |  |  | Rutembe | 121 | 65 | 117 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 29 | 20 | 29 | [6 empty] | 19 | 2 | 2 | 3 | [6 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 2500 | 2 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2017 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Mwagiro |  |  | Kirikumuryango network | 139 | 22 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Water point at EP Murambi Publique/Nyirambuga pumping | 174 | 174 | 14 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 25 | [6 empty] | 15 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 214 | 200 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 |  |  |  |  | 19 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7200 | 6 |  | 2 | 4500 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Gitare | Mugenda I |  |  | Water point near Gitare school/Nyirambuga pumping system | 117 | 117 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | [9 empty] | 15 | [9 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Water point2 at Gasiza market/Nyagahondo gravity system | 228 | 228 |  | Piped Network -- Gravity Only | 2010 | Caritas | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 13 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2010
2017 | Rwanda | Rulindo | Kisaro | Murama | Ryarubuguza |  |  | Gahama Kisaro network | 495 | 495 | 5 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 30000 | 7 | 14 | 1 | 30000 | 2 | 1 | 1 |  | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Rukozo | Mbuye | Kibare |  |  | Kabonanyoni | 90 | 85 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rusiga | Taba | Nyakarama |  |  | Nyakarama water point/Nyakabizi gravity | 101 | 101 | 71 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 26 | [6 empty] | 16 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2013 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Magezi |  |  | Miyove-Kinihira | 141 | 70 |  | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | -8 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1989
2017 | Rwanda | Rulindo | Murambi | Gatwa | Amataba |  |  | Mutagata Motorised Network | 134 | 134 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 30 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Budaha |  |  | Nkombe water point/Nkombe gravity | 205 | 205 |  | Piped Network -- Gravity Only | 2002 | Coforwa | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 5 | [9 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2002
2017 | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point at EP Tumba Public/Nyirambuga pumping | 115 | 115 | 50 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 2 |  |  |  |  | 3 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Cyungo | Marembo | Gahinga |  |  | Mugomero Marembo | 652 | 602 | 143 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 |  |  |  |  | 18 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 10000 | 10 | 3 | 2 | 10000 |  | 8 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Ruhondo |  |  | Kishwi network | 184 | 41 | 23 | Piped Network -- Gravity Only | 2003 | Goverment | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 16 | 19 | 16 |  | 16 |  |  |  |  | 6 | 1 | 1 | 1 |  | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 700 | 2 |  | 2 | 680 |  | 4 | 1 | "Springbox" --Intake Structure At A Spring | 2003 | 1 | 2016 | 1 | 2003 | 0 |  | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Base | Cyohoha | Gihemba |  |  | kazabazana | 163 | 140 | 72 | Piped Network With Pump | 1998 |  | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 2 | 2 | 30000 | 7 | 14 | 2 | 30000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Mukumba |  |  | Bitete-Muvumu | 92 | 20 | 40 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 2 | 1 | 2 | 1 |  |  |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 3 | 1 | 1 | 1000 | 4 | 6 | 4 | 4000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo |  |  | Cyaruzinge | 120 | 80 | 23 | Piped Network -- Gravity Only | 1998 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 |  | 30 | 20 |  | 7 |  |  |  | 20 | 3 |  | 1 | 2 |  | 1 |  |  |  | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 |  |  | 5 | 8 |  |  | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 0 |  | 1 | 2017 | 1 | 2017 | 0 |  | 1 | 2017 | 0 |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Gatete |  |  | gahama | 163 | 140 |  | Piped Network With Pump | 2012 |  | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 25 | 15 | 25 | 15 | 25 |  |  |  |  | 15 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 2 | 2 | 12000 | 7 | 14 | 2 | 12000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | Rwintare2 water point/Tare-Rusiga pumping | 281 | 281 | 49 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Munini |  |  | Musenge network | 111 | 62 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Other Concrete Structures Distribution Line, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Kararama network | 193 | 193 |  | Piped Network With Pump | 2009 | Umushinga Witwa Ema | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 12 | 16 | 6 | 16 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 3 | 1 | 2 | 5000 | 7 | 14 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2009 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Kabakene |  |  | kirikumuryango network | 99 | 99 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 4 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point/AEP Kigarama gravity | 243 | 243 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 19 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Rusura |  |  | Water point chez Senzoga/Nyirambuga pumping | 157 | 157 | 7 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 30 | [6 empty] | 20 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2017 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 77 | 70 | 29 | Piped Network -- Gravity Only | 2005 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 18 | 8 | 18 | 19 | [5 empty] | 20 | 1 | 1 | 1 | 1 | [5 empty] | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 4500 | 1 | 2 |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2005 | 1 | 2005 | 1 | 2005 | 1 | 2016 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Kisaro | Murama | Mugomero |  |  | gahama | 129 | 100 | 50 | Piped Network With Pump | 2012 | Waterforpeople | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 | 25 | 15 | 25 |  |  |  |  | 15 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 2 | 12000 | 7 | 14 | 2 | 12000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Cyungo | Rwili | Kivumu |  |  | Sakara | 570 | 520 | 45 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 29 | 19 | 29 | 5 | 18 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 2 | 1 | 1 | 1200 | 2 | 5 | 1 | 2300 | 2 | 4 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Ngoma | Mugote | Rukoma |  |  | Kararama pumping network | 92 | 47 |  | Piped Network With Pump | 2007 | Government | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 4 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 20 | 10 | 20 | 10 | 20 | -3 | 10 |  |  | 10 | 1 | 1 | 1 | 1 | 2 | 2 | 2 |  |  | 3 | 3 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 4 | 3 | 1 | 1500 | 25 | 20 | 4 | 30000 | 2 | 47 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2007 | 1 | 2007 | 1 | 2007 | 1 | 2007 | 1 | 2007 | 1 | 2007 | 1 | 2007 | 0 |  |  |  |  | 1 | 2007
2017 | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point behind Gisha center/Nyirambuga pumping | 133 | 133 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at Buyoga secondary school/Nyirambuga pumping | 177 | 177 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 6 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at Buyoga Health Center/Nyirambuga pumping | 177 | 177 | 9 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 6 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Base | Cyohoha | Bukangano |  |  | Migogo | 129 | 120 | 11 | Piped Network -- Gravity Only | 2009 | Padiri | Groundwater (Well, Etc.) | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Conduction Line, Storage Tank, Distribution Line, | Create Plan To Repair or Replace Components | 22 | 12 | 22 |  | 22 |  |  |  |  | 19 | 1 | 2 | 2 |  | 2 |  |  |  |  | 1 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 6800 | 3 |  | 1 | 6800 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 0 |  | 1 | 2009 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Cyungo | Marembo | Murambo |  |  | Mugomero Marembo | 161 | 150 | 77 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 |  |  |  |  | 18 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 10000 | 10 | 3 | 2 | 10000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Amahoro |  |  | Nyakagezi | 120 | 43 | 8 | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 30 | [8 empty] | 20 | 2 | [8 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | [7 empty] | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Kisaro | Sayo | Rugarama |  |  | Kiruruma | 109 | 101 | 15 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 3 | 9000 | 15 | 5 | 3 | 4000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Buyoga | Butare | Giko |  |  | Kiduha-muyanza | 115 | 100 | 12 | Piped Network -- Gravity Only | 2007 | Italians(Lake Angels) | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Storage Tank, Distribution Line, | Create Plan To Repair or Replace Components | 27 | 17 | 20 |  | 20 |  |  |  |  | 17 | 1 | 1 | 2 |  | 2 |  |  |  |  | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2200 | 3 |  | 1 | 1000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2007 | 0 |  | 1 | 2007 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Kabeza |  |  | gahama | 92 | 80 | 33 | Piped Network With Pump | 2012 | Gouverment | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 30000 | 7 | 14 | 2 | 30000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Base | Rwamahwa | Cyondo |  |  | Ruramba | 173 | 140 | 108 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 29 | 19 | 29 | 19 | [5 empty] | 19 | 1 | 1 | 1 | 1 | [5 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 4500 | 2 | 2 |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Kisaro | Gitatsa | Ndago |  |  | gahama | 148 | 40 | 238 | Piped Network -- Gravity Only | 2012 | Waterfor People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 |  | 25 | 1 | [5 empty] | 20 | 1 |  | 1 | 1 | [5 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 |  |  | 7 | 14 |  |  |  | 1998 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 0 |  | 1 | 2012 | 1 | 1998 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Masoro | Kivugiza | Rebero |  |  | Mutagata motorised network | 376 | 138 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Ngarama |  |  | Nyirangarama water point/Rutare-Nyirangarama gravity system | 89 | 89 |  | Piped Network -- Gravity Only | 1960 | Government Of Rwanda | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | [9 empty] | -37 | [9 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 1960
2017 | Rwanda | Rulindo | Rusiga | Kirenge | Rebero |  |  | Gashinge source/Gashinge gravity | 181 | 181 |  | Piped Network -- Gravity Only | 2013 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 18 | 26 | [6 empty] | 16 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 800 | 1 |  |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2015 | 1 | 2013 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Wpt at Murambi Central Catholic Church/Nyirambuga pumping | 174 | 174 |  | Piped Network With Pump | 2012 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 11 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Base | Gitare | Rugerero |  |  | Water point at Gasana/Nyirambuga pumping system | 143 | 143 | 104 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  |  | 25 | [6 empty] | 15 |  |  | 2 | [6 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Nyarurembo |  |  | Mutagata motorised network | 144 | 40 |  | Piped Network -- Gravity Only | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Rugaragara |  |  | charity water 203.207 | 815 | 815 | 10 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 35000 | 2 | 2 | 1 | 1000 | 3 | 1 | 1 |  | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Cyohoha | Gihemba |  |  | Nyamagana | 85 | 75 | 15 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Base | Cyohoha | Gihemba |  |  | Nyamagana | 75 | 60 | 140 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Conduction Line, Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 2 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Masoro | Kigarama | Rukurazo |  |  | Mutagata Gravity Network | 247 | 107 | 7 | Piped Network -- Gravity Only | 2004 |  | Groundwater (Well, Etc.) | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 17 | 7 | 17 | 7 | 17 |  |  |  |  | 10 | 2 | 2 | 2 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3500 | 6 | 4 | 2 | 4500 |  | 12 | 1 | "Springbox" --Intake Structure At A Spring | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2007
2017 | Rwanda | Rulindo | Buyoga | Butare | Karambi |  |  | Nyagahera | 107 | 100 | 119 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Intake Structure, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 30 | 17 | 27 | 17 | 27 |  |  |  |  | 17 | 2 | 1 | 1 | 1 | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6800 | 3 | 3 | 1 | 1200 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Ruri |  |  | Mutagata Motorised Network | 189 | 70 | 50 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Cyungo | Marembo | Gahinga |  |  | Mugomero Murambo | 652 | 602 | 152 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 |  |  |  |  | 18 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 10000 | 10 | 3 | 2 | 10000 |  | 8 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gisiza |  |  | kinywamagana pumping network | 212 | 60 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo |  |  |  | 203 | 203 | 12 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 180 |  | Piped Network -- Gravity Only | 2016 | Padiri Gitovu | Spring¦Groundwater (Well, Etc.) | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 25 | 19 | 25 | 19 | 25 |  |  |  |  | 20 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 4 | 3 | 1 | 6450 | 2 | 2 | 1 | 6450 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2016 | 1 | 2012 | 1 | 2016 | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Kisaro | Murama | Ryarubuguza |  |  | Gahama Kisaro network | 99 | 99 | 36 | Piped Network With Pump | 2012 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30000 | 7 | 14 | 1 | 30000 | 2 | 1 | 1 |  | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Base | Gitare | Kirwa |  |  | Rwicanyoni | 136 | 100 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 |  | 29 | [6 empty] | 19 | 1 |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 |  |  | 3 |  |  |  |  | 2 | 1 | Start Chamber | 2016 | 0 |  | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rukozo | Buraro | Kabingo |  |  | Kabonanyoni | 40 | 40 | 118 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 19000 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Masoro | Shengampuri | Amataba |  |  | Mutagata Gravity Network | 178 | 60 |  | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 17 | 7 | 17 | 7 | 17 |  |  |  |  | 7 | 2 | 2 | 2 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3500 | 6 | 4 | 2 | 4500 |  | 12 | 1 | "Springbox" --Intake Structure At A Spring | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 214 | 214 | 4 | Piped Network With Pump | 1986 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rukozo | Mbuye | Mujebe |  |  | Kabonanyoni | 50 | 46 | 14 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 214 | 200 | 4 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  | 19 | 29 |  | 29 |  |  |  |  | 19 |  | 2 | 1 |  | 2 |  |  |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 |  | 1 | 7200 | 6 |  | 1 | 7200 |  | 2 | 0 |  |  | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Murambi | Mvuzo | Kabuga |  |  | rwiseke | 199 | 195 | 6 | Piped Network -- Gravity Only | 2001 | Governement (District, Wasac) And Water For People | Spring | Medium Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Consider Replacing Aging Components | Conduction Line, Distribution Network, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 14 | 4 | 14 |  | 14 |  |  |  |  | 4 | 1 | 1 | 1 |  | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1200 | 7 |  | 1 | 1200 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2001 | 1 | 2001 | 1 | 2001 | 0 |  | 1 | 2001 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2001
2017 | Rwanda | Rulindo | Buyoga | Gahororo | Bunyana |  |  | Kiruruma | 108 | 102 | 25 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.)¦Null | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 15 | 5 | 3 | 9000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Buyoga | Ndarage | Kimagali |  |  | kiruruma | 125 | 100 | 30 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 20 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 3 | 9000 | 11 |  | 3 | 9000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kirurumo |  |  | Bitete-Rwahi network | 80 | 50 | 5 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 600 | 6 | 6 | 1 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Cyungo | Rwili | Karambi |  |  | Nyamagana | 50 | 45 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 4 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Bushoki | Mukoto | Buyogoma |  |  | Buyogoma water point/Tare-Rusiga pumping system | 130 | 130 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 |  | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 8 | 8 | 1 | 4000 | 1 |  | 1 | 8000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Tumba | Gahabwa | Mafene |  |  | Nyirambuga 2Pumping station/Source Nyakagezi | 172 | 172 | 24 | Piped Network With Pump | 2012 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Storage Tank, Pump, | Create Plan To Repair or Replace Components | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 2 | 1 | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 2 | 1 | 200 | 1 | 2 | 1 | 800 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Base | Rwamahwa | Gitovu |  |  | Rwankende | 154 | 130 | 29 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 29 | 15 | 29 | 19 | 29 |  |  |  |  | 20 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 3 | 2 | 1 | 6450 | 3 | 2 | 1 | 6450 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2012 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Cyungo | Burehe | Sove |  |  | Nyamagana | 74 | 45 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Rusiga | Kirenge | Ntaruka |  |  | Ntaruka water point/Ntaruka-Nyange gravity system | 176 | 176 |  | Piped Network -- Gravity Only | 2010 | Local Government And Nyange Girls School | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  | 13 | 23 |  | 23 |  |  |  |  | 13 |  | 1 | 2 |  | 1 |  |  |  |  | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 |  | 1 | 100 | 1 |  | 1 | 1000 |  | 1 | 0 |  |  | 1 | 2010 | 1 | 2010 | 0 |  | 1 | 2010 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2010
2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 214 | 214 |  | Piped Network With Pump | 1986 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5000 | 15 |  | 1 | 5000 | 1 | 21 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Bubiro |  |  | Bubiro water point/Rutomvu gravity system | 158 | 158 |  | Piped Network -- Gravity Only | 2013 | Government Of Rwanda | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 16 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Burega | Butangampundu | Gashinge |  |  | Rwamugaza | 435 | 435 | 10 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Conduction Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 16 | 6 | 16 | 6 | [5 empty] | 17 | 1 | 2 | 1 | 1 | [5 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 2 | 1 | 8000 | 10 | 8 |  |  |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Cyungo | Rwili | Kabanda |  |  | Nyamagana | 69 | 59 | 111 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Kinihira | Rebero | Kabuga |  |  | Miyove-Kinihira | 191 | 80 | 52 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, Kiosk/Tap Stand | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | 18 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kinihira | Rebero | Taba |  |  | Miyove-Kinihira | 122 | 70 | 7 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | -8 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1989
2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 77 | 70 | 309 | Piped Network -- Gravity Only | 2005 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 18 | [8 empty] | 8 | 1 | [8 empty] | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | [7 empty] | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2005 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2005
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 354 | 45 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Tumba | Misezero | Kavumu |  |  | Water point at Kavumu/Nyirambuga pumping | 139 | 139 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2015 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Rusura |  |  | Water point chez Gidasi/Nyirambuga pumping | 157 | 157 |  | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 30 | [6 empty] | 20 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2017 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatiba |  |  | Gihanga II | 151 | 151 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | [6 empty] | 19 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7000 | 3 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | Rwintare1water point[RW.WFP.Q3.14.166.028]/Tare-Rusiga pumping | 281 | 281 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyagasozi |  |  | Kararama network | 197 | 197 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 22 | 12 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 3 | 1 | 2 | 5000 | 7 | 14 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Burega | Butangampundu | Kigabiro |  |  | Rwamugaza | 565 | 565 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Storage Tank, Other Concrete Structures | Create Plan To Repair or Replace Components | 16 | 6 | 16 | 6 | [5 empty] | 6 | 1 | 1 | 2 | 2 | [5 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 8000 | 20 | 16 |  |  |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Kigomwa |  |  | marenge | 118 | 118 | 81 | Piped Network With Pump | 1997 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 15 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Masoro | Kabuga | Kigarama |  |  | Mutagata motorised network | 176 | 95 |  | Piped Network With Pump | 1987 | Water For People And Government Will | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 30 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Water point near TCT/Nyirambuga pumping | 174 | 174 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | 18 | 28 |  |  |  |  | 18 |  |  | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 | 1 | 2 | 1000 |  | 2 | 0 |  |  | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kinihira | Marembo | Cyogo |  |  | Nyamagana-Kinihira | 420 | 420 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 3 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Tumba | Barari | Gaseke |  |  | Gaseke center water point/Nyirambuga pumping | 149 | 149 | 29 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 20 | [9 empty] | 1 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 214 | 185 | 148 | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 29 | 19 | 29 | [6 empty] | 20 | 1 | 2 | 1 | [6 empty] | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 2 | 7200 | 6 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  |  | 186 | 38 |  | Piped Network With Pump | 2014 |  | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Murambi | Gatwa | Kabeza |  |  | Mutagata Motorised Network | 134 | 134 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Karambi |  |  | Nyabishengeshi gravity system/Karambi water point | 79 | 79 | 76 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 16 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | [9 empty] | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kibamba |  |  | Musenge Network | 176 | 100 | 305 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Burega | Butangampundu | Muhomdo |  |  | Rwamugaza | 305 |  |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 3 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 22 | 12 | 27 | 17 | 27 | -1 | 12 |  |  | 17 | 1 | 1 | 3 | 3 | 3 | 1 | 3 |  |  | 3 | 3 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 3 | 2 | 3000 | 3 | 8 | 2 | 3000 | 1 | 1 | 1 |  | 2009 | 1 | 2009 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Tumba | Taba | Nkinda |  |  | Nkinda water point/Nyirambuga pumping | 127 | 127 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | NKANGA SCHOOL WATER POINT/KIVOMO-NTAKARA GRAVITY | 129 | 129 |  | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  |  |  | 18 | [5 empty] | 18 |  |  |  | 3 | [5 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 2 |  |  |  |  | 1 |  |  |  | 1 | 0 |  |  | 0 |  | 0 |  | 1 | 2015 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Kigomwa |  |  |  | 118 | 118 | 153 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Gisoro- Nyundo network | 188 | 35 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 6 | 10 | 2 | 7000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Rwamugaza network | 193 | 193 | 39 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Buyoga | Gahororo | Gatenderi |  |  | Kiruruma | 141 | 102 |  | Piped Network With Pump | 2014 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3 | 9000 | 11 |  | 3 | 9000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point at GS Gisha/Nyirambuga pumping | 133 | 133 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 3 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | rwamugaza | 200 | 200 | 5 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Rukozo | Buraro | Shyondwe |  |  | Kabonanyoni | 75 | 70 | 85 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 10 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Ngoma | Karambo | Kagwa |  |  | Kabarore- Ngoma- Nyabuko network | 123 | 38 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Intake Structure, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 2 | 1 | 1 |  | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 2 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Burega | Butangampundu | Mayaga |  |  | Rwamugaza | 525 | 525 | 110 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 16 | 6 | 27 | 17 | [5 empty] | 17 | 1 | 1 | 1 | 1 | [5 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 2 | 1 | 8000 | 10 | 8 |  |  |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2014 | 1 | 2014 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Ruri |  |  | Mutagata Motorised Network | 189 | 79 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Gatsinde |  |  | Gatsinde water point/Nyirambuga pumping | 178 | 178 | 50 | Piped Network With Pump | 2012 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 25 | [6 empty] | 15 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Rukozo | Buraro | Kivomo |  |  | Nyamagana | 80 | 30 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Intake Structure, Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 2 | 1 | 1 | 1 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 214 | 214 |  | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rusiga | Gako | Ntakara |  |  | Kivomo water point/Kivomo-Ntakara | 200 | 200 | 39 | Piped Network -- Gravity Only | 2015 | Local Government With Partnering With The Community | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  | 18 | 28 | [6 empty] | 18 |  | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 100 | 1 |  |  |  |  | 1 | 0 |  |  | 1 | 2015 | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 229 | 190 | 144 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 30 | 19 | 29 | 19 | [5 empty] | 19 | 1 | 1 | 1 | 1 | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 1 | 1 |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kigarama |  |  | kinywamagana pumping network | 233 | 89 | 42 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Buyoga | Gahororo | Gipfundo |  |  | rukondo | 162 | 120 |  | Piped Network -- Gravity Only | 2012 | G.Thierry | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 |  |  | 25 |  |  |  |  | 15 | 1 | 1 |  |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4500 |  |  | 1 | 4500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 0 |  | 0 |  | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Rugando |  |  | Water point at Rugando chez Ndayambaje/Nyirambuga pumping | 161 | 161 |  | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 20 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Nyenyeri |  |  | Nyenyeri water point/Tare-Rusiga pumping | 68 | 68 | 62 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 |  | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 10 | 8 | 1 | 4000 | 1 |  | 3 | 8000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Munini |  |  | Musenge network | 111 | 49 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Burega | Taba | Nyagisozi |  |  | Rwamugaza | 520 | 520 | 95 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Gishyita |  |  | Gisoro- Nyundo network | 205 | 110 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 6 | 10 | 2 | 7000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Burega | Butangampundu | Gacyamo |  |  | Rwamugaza | 550 | 550 | 50 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 2 | 5000 | 16 | 23 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Cyungo | Marembo | Rusayo |  |  | Nyabirarama | 150 | 100 |  | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 |  |  |  |  | 18 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1200 | 1 | 1 | 1 | 1200 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Buyoga | Karama | Kigarama |  |  | Kigarama water point/Nyirambuga pumping system | 121 | 121 | 45 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 20 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Cyungo | Rwili | Karambi |  |  | Nyamagana | 50 | 5 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Masoro | Shengampuri | Agasharu |  |  |  | 130 | 130 |  | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rukozo | Buraro | Kabingo |  |  | Kabonanyoni | 35 | 35 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Other Concrete Structures | Create Plan To Repair or Replace Components | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 2 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 1 | 720 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rukozo | Mbuye | Mujebe |  |  | Kabonanyoni | 800 | 800 | 126 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Ruhondo |  |  | Kishwi network | 184 | 58 |  | Piped Network -- Gravity Only | 2003 | Goverment | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 29 | 19 | 16 |  | 16 |  |  |  |  | 6 | 1 | 1 | 1 |  | 1 |  |  |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 2 | 700 | 2 |  | 2 | 680 |  | 4 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2003 | 0 |  | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point Kumanga /Nyirambuga pumping | 115 | 115 | 95 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Storage Tank, Kiosk/Tap Stand | Create Plan To Repair or Replace Components |  |  | 25 | [6 empty] | 15 |  |  | 2 | [6 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Rimwe |  |  | Gisoro- Nyundo network | 120 | 25 | 64 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 6 | 10 | 2 | 7000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Kinihira | Rebero | Karambi |  |  | Nyamagana-Kinihira | 144 | 80 | 92 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Ngoma | Kabuga | Nyabuko |  |  | Kabarore-Ngoma-Nyabuko network | 122 | 30 | 6 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 2 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Base | Gitare | Gatete |  |  | Rwicanyoni | 141 | 135 | 10 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | [6 empty] | 19 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 8600 | 3 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rukozo | Mbuye | Nyarusebeya |  |  | Kabonanyoni | 80 | 70 | 50 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gihonga |  |  | Kibuye | 110 | 60 | 85 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 29 | 19 |  | 19 | 29 |  |  |  |  | 1 | 1 | 1 |  | 1 | 1 |  |  |  |  | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 2 | 1 | 1500 |  | 1 | 1 | 1000 |  | 1 | 1 | Start And Collection Chamber | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1998
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Gishyita |  |  | kirikumuryango network | 205 | 120 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Kisaro | Kigarama | Runyinya |  |  | wasac network towards Mutete in Gicumbi district | 148 | 148 | 135 | Piped Network -- Gravity Only | 2000 | Government | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 30000 | 7 | 14 | 1 | 30000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatimba |  |  | kinywamagana pumping network | 217 | 82 | 98 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Kinihira | Marembo | Gatare |  |  | Nyamagana- Kinihira | 168 | 70 | 1335 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 18 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Cyungo | Rwili | Nturo |  |  | Nyamabara | 2785 | 1450 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Murambi | Bubangu | Taba |  |  | rwiseke | 193 | 193 |  | Piped Network -- Gravity Only | 2001 | Governement (District, Wasac) And Water For People | Spring | Medium Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Consider Replacing Aging Components | Conduction Line, Distribution Network, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 14 | 4 | 14 |  | 14 |  |  |  |  | 4 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 12000 | 7 |  | 1 | 12000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2001 | 1 | 2001 | 1 | 2001 | 0 |  | 1 | 2001 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2001
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Ngendo |  |  | kirikumuryango network | 180 | 180 | 69 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 10000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kagunda |  |  | Muvumu- Taba | 94 | 25 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components |  | 16 | 26 | 16 | 26 |  |  |  |  | 16 |  | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 |  | 1 | 800 | 3 | 9 | 1 | 7500 |  | 1 | 0 |  |  | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point chez Haguma/Nyirambuga pumping | 169 | 169 |  | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 30 | 20 | 30 |  |  |  |  | 20 |  |  | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 | 1 | 1 | 100 |  | 2 | 0 |  |  | 0 |  | 1 | 2017 | 1 | 2017 | 1 | 2017 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Rwahi |  |  | Bitete-Rwahi network | 360 | 360 | 124 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 600 | 6 | 6 | 1 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Kinihira | Marembo | Cyogo |  |  | Nyamagana-Kinihira | 184 | 60 | 102 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Rwambogo |  |  | Rwambogo | 156 | 54 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Storage Tank, Distribution Line, | Create Plan To Repair or Replace Components | 29 | 19 | 29 |  | 29 |  |  |  |  | 19 | 1 | 1 | 2 |  | 2 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 700 | 1 |  | 1 | 350 |  | 3 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Kigali |  |  | Gisoro- Nyundo network | 300 | 300 | 108 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 6 | 10 | 2 | 7000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kinini/Mbogo |  |  |  | 188 | 80 | 45 | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 16 | [6 empty] | 7 | 1 | 1 | 1 | [6 empty] | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 1 | 1000 | 1 |  |  |  |  | 2004 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2003 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Kinihira | Butunzi | Bunahi |  |  | Nyamagana-Kinihira | 105 | 60 | 32 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kisaro | Gitatsa | Ruberano |  |  | gahama | 132 | 100 | 5 | Piped Network With Pump | 2012 | Waterforpeople | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 30000 | 7 | 14 | 2 | 30000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Base | Cyohoha | Kabingo |  |  | Nyamagana | 50 | 45 | 5 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 2 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Buyoga | Ndarage | Gahondo |  |  | Ndarage | 105 | 100 | 90 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 | [6 empty] | 17 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 6300 | 5 |  |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Masoro | Kabuga | Nyakizu |  |  | Mutagata motorised network | 196 | 106 | 8 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Buyoga | Gitumba | Munini |  |  | Kiruruma | 158 | 150 | 100 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 1 | 3 | 9000 | 15 | 5 | 3 | 9000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gicumbi |  |  | Musenge Network | 141 | 41 | 265 | Piped Network With Pump | 2014 |  | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 354 | 89 | 80 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyabitare |  |  | Gisaro-Nyundo network | 130 | 50 | 50 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 6 | 10 | 2 | 7000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Cyungo | Marembo | Gahinga |  |  | Mugomero Marembo | 652 | 602 | 108 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 |  |  |  |  | 18 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 10000 | 10 | 3 | 2 | 10000 |  | 8 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Ntunguru |  |  | Miyove- Kinihira | 168 | 60 | 14 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | 4 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2001
2017 | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 214 | 200 |  | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 29 | 19 | 29 |  | 29 |  |  |  |  | 20 | 1 | 2 | 1 |  | 2 |  |  |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 2 | 7200 | 6 |  | 2 | 7200 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Bushoki | Giko | Karambo |  |  | Water point at Buramira Primary school/Buramira-Kivure gravity system | 250 | 250 | 324 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 354 | 30 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 2 | 1 | 1 | 2 | 1 |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Kisaro | Murama | Kibingwe |  |  | Gahama Kisaro network | 610 | 610 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30000 | 7 | 14 | 1 | 30000 | 2 | 1 | 1 |  | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo |  |  | marenge | 203 | 203 |  | Piped Network With Pump | 1986 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 5000 | 15 |  | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at ADEPR Buyoga/Nyirambuga pumping | 177 | 177 | 98 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | Nganzo-Kabarore | 198 | 100 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 2 | 2 | 1 |  | 3 |  |  |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 400 | 3 |  | 2 | 800 |  | 5 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Rukore |  |  | Rwamugaza network | 184 | 184 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Rusura |  |  | Water point chez Ntihabose/Nyirambuga pumping | 157 | 157 | 95 | Piped Network With Pump | 2012 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | [9 empty] | 15 | [9 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Masoro | Kabuga | Kigarama |  |  | Mutagata motorised network | 176 | 81 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Rusiga | Gako | Kabuye |  |  | Ruganzu-Kabuye gravity system | 169 | 169 |  | Piped Network -- Gravity Only | 2010 | Private Operator And Local Government | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  | 13 | 23 | [6 empty] | 13 |  | 3 | 3 | [6 empty] | 3 | 3 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 |  | 1 | 100 | 1 | [5 empty] | 0 |  |  | 1 | 2010 | 1 | 2010 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2010
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Gatsinde |  |  | Gatsinde wpt/Nyirambuga | 178 | 178 | 50 | Piped Network With Pump | 2012 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 25 | [6 empty] | 15 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Cyungo | Marembo | Buyaga |  |  | Mugomero Marembo | 652 | 602 |  | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 18 | 28 | 18 | 28 |  |  |  |  | 18 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10000 | 10 | 3 | 2 | 10000 |  | 8 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point at APEKI Accommodation/Nyirambuga pumping | 115 | 115 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 25 |  | 25 |  |  |  |  | 15 |  |  | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 |  | 1 | 100 |  | 6 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Tumba | Misezero | Karambi |  |  | Water point chez Nkurunziza/Nyirambuga pumping | 160 | 160 |  | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 20 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Masoro | Kabuga | Gisiza |  |  | Mutagata motorised network | 135 | 135 | 21 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Kisaro | Murama | Akamanama |  |  | kano | 141 | 120 |  | Piped Network With Pump | 2012 | Waterforpeople | Spring | Medium Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Consider Replacing Aging Components | Other Concrete Structures, Distribution Network, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 25 |  | 25 | 1 | 25 |  |  |  |  | 1 | 1 |  | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 2 | 2 |  |  | 7 | 14 | 2 | 30000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 0 |  | 1 | 2012 | 1 | 1998 | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1998
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Budaha |  |  | Budaha water point/Nkome gravity system | 205 | 205 |  | Piped Network -- Gravity Only | 2002 | Coforwa | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 5 | [9 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2002
2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Marembo |  |  | marenge | 173 | 173 | 5 | Piped Network With Pump | 1998 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 5000 | 15 |  | 2 | 5000 | 1 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rukozo | Buraro | Murwa |  |  | Kabonanyoni | 75 | 70 | 231 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | kinywamagana pumping network | 281 | 50 | 4 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 28 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Buyoga | Gitumba | Remera |  |  | Kiruruma | 130 | 126 | 5 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 15 |  | 3 | 9000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 45 | 40 | 180 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Kayenzi |  |  | Rwamugaza | 200 | 20 |  | Piped Network -- Gravity Only | 2003 | Goverment | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Kabuga |  |  |  | 119 | 119 | 45 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kirurumo |  |  | Bitete-Rwahi network | 80 | 35 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 600 | 6 | 6 | 2 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Mbogo | Mushali | Rwambogo |  |  | Rwambogo Extension network | 69 | 69 | 23 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 22 | 19 | 29 | 19 | 29 |  |  |  |  | 19 | 2 | 1 | 1 | 1 | 3 |  |  |  |  | 1 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 1 | 1 | 600 | 1 | 1 | 1 | 100 |  | 1 | 1 | Suction Tank | 2009 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Rwamahwa | Kiruli |  |  | Migogo | 223 | 200 | 87 | Piped Network -- Gravity Only | 2009 | Padiri(Lake Angels). | Groundwater (Well, Etc.) | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Distribution Line, | Create Plan To Repair or Replace Components | 22 | 12 | 22 |  | 22 |  |  |  |  | 12 | 2 | 2 | 2 |  | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 6800 | 3 |  | 1 | 6800 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 0 |  | 1 | 2009 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Nyabisindu |  |  | kirikumuryango network | 149 | 62 | 37 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Conduction Line, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 2 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatimba |  |  | kinywamagana pumping network | 217 | 180 | 5 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Rukozo | Buraro | Rukingu |  |  | Kabonanyoni | 100 | 95 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Kingazi 2water point/Nyakabizi1&2 | 157 | 157 | 50 | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 16 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Cyungo | Rwili | Nyabisasa |  |  | Sakara | 570 | 520 |  | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 29 | 5 | 18 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 2 | 1 | 1 | 1200 | 2 | 5 | 1 | 2300 | 2 | 4 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 495 | 495 | 88 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ngoma | Kabuga | Kirambo |  |  | Nganzo-Kabarore | 131 | 43 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 3 | 2 | 1 |  | 3 |  |  |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 2 | 400 | 3 |  | 2 | 800 |  | 5 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Masoro | Kigarama | Nyakibungo |  |  |  | 229 | 229 | 101 | Piped Network With Pump | 1998 |  | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Murambi | Mvuzo | Kabuga |  |  | Mutagata Motorised Network | 199 | 98 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Murambi | Bubangu | Nyagisozi |  |  | Gakoma network | 154 | 154 |  | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components |  |  | 17 |  | 17 |  |  |  |  | 7 |  |  | 1 |  | 2 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 2 |  | 1 | 4000 |  | 2 | 0 |  |  | 0 |  | 1 | 2004 | 0 |  | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Base | Gitare | Gihora |  |  | Gihora Water point/Rutomvu gravity system | 101 | 101 | 119 | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 26 | [6 empty] | 16 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2013 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Mwagiro |  |  | Kirikumuryango network | 139 | 20 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Burega | Butangampundu | Kisigiro |  |  | Rwamugaza | 605 | 605 | 79 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ngoma | Karambo | Kagwa |  |  | Nganzo-Kabarore | 123 | 44 | 35 | Piped Network -- Gravity Only | 2014 |  | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 30 |  | 27 |  |  |  |  | 17 | 2 | 2 | 1 |  | 3 |  |  |  |  | 2 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 400 | 3 |  | 2 | 800 |  | 5 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2017 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Ngoma | Mugote | Kiboha |  |  | Kabarore-Ngoma-Nyabuko network | 74 | 39 | 3 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 4 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Base | Gitare | Kirwa |  |  | Rwicanyoni | 116 | 113 | 10 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | [6 empty] | 19 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 8600 | 3 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Cyinzuzi | Rudogo | Gasiza |  |  | Rwagitare | 76 | 66 | 9 | Piped Network -- Gravity Only | 2009 | Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 12 | 22 | 12 | 22 |  |  |  |  | 12 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1200 | 1 | 2 | 1 | 900 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Buyoga | Gahororo | Shagasha |  |  | Kiruruma | 209 | 200 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 15 | 5 | 3 | 9000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Tumba | Misezero | Karambi |  |  | Water point chez Nkurunziza/Nyirambuga pumping | 160 | 160 |  | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components |  |  | 30 | [6 empty] | 20 |  |  | 1 | [6 empty] | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2017 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Nyakaruri |  |  | kinywamagana pumping network | 127 | 127 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Remera |  |  | Kinyankeri water point at Buyogoma-Remera border | 105 | 105 | 3 | Piped Network -- Gravity Only | 2007 | Local Government In Collaboration With The Community | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 13 | [9 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 3 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2010
2017 | Rwanda | Rulindo | Buyoga | Gitumba | Rutabo |  |  | Kiruruma | 128 | 125 | 100 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 | 17 | 27 | 4 |  |  |  | 17 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 3 | 4000 | 15 | 5 | 3 | 4000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Buliza |  |  | Mutagata Motorised Network | 221 | 121 | 12 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 180 |  | Piped Network -- Gravity Only | 2012 | Padiri | Spring¦Groundwater (Well, Etc.) | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 19 | 25 | 15 | 29 |  |  |  |  | 15 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 2 | 1 | 6450 | 2 | 2 | 1 | 6450 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2016 | 1 | 2012 | 1 | 2012 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point at APEKI Tumba Boys Dormitory/Nyirambuga pumping | 115 | 115 | 267 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 25 |  | 25 |  |  |  |  | 15 |  |  | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 |  | 1 | 100 |  | 6 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 325 | 58 | 28 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 6 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Rwamahwa | Kabahama |  |  | Migogo | 178 | 150 | 14 | Piped Network -- Gravity Only | 2009 | Padiri(Lake Angels). | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 22 | 12 | 22 |  | 22 |  |  |  |  | 12 | 2 | 2 | 2 |  | 2 |  |  |  |  | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 6800 | 2 |  | 1 | 6800 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 0 |  | 1 | 2009 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Buyoga | Butare | Gasave |  |  | Kiduha | 114 | 100 | 80 | Piped Network -- Gravity Only | 2007 | Governement (District, Wasac) And Water For People | Spring¦Null | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Conduction Line, Storage Tank, | Create Plan To Repair or Replace Components | 27 | 10 | 20 | [6 empty] | 17 | 1 | 2 | 2 | [6 empty] | 1 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 2200 | 3 |  |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2007 | 1 | 2007 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Karindi |  |  |  | 120 | 40 |  | Piped Network -- Gravity Only | 2007 |  | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 20 | 10 | 10 | [6 empty] | 10 | 1 | 1 | 2 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 1 |  |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2007 | 1 | 1997 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2007
2017 | Rwanda | Rulindo | Burega | Taba | Gasango |  |  | Rwamugaza network | 79 | 79 | 9 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Buyoga | Gitumba | Gitaba |  |  | Kiruruma | 169 | 160 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 1 | 3 | 9000 | 15 | 5 | 3 | 9000 | 2 | 2014 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Rusiga | Gako | Ntakara |  |  | Ntakara water point/Ntakara gravity system | 129 | 129 | 14 | Piped Network -- Gravity Only | 2015 | Local Government In Partnership With Community | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 214 | 200 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 29 | 19 | 29 |  | 29 |  |  |  |  | 19 | 1 | 1 | 1 |  | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 7200 | 6 |  | 1 | 7200 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Ngoma | Mugote | Kigina |  |  | Shishi network | 84 | 84 | 61 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 2 | 1 | 1 |  | 1 |  |  |  |  | 1 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 700 | 2 |  | 1 | 4000 |  | 4 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Ngoma | Munyarwanda | Busizi |  |  | Kabarore-Ngoma-Nyabuko network | 100 | 39 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 4 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Tumba | Barari | Gashoro |  |  | Gashoro water point/Nyirambuga pumping | 161 | 161 | 84 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  |  | 30 | [6 empty] | 20 |  |  | 3 | [6 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2017 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Ngoma | Karambo | Butare |  |  | Shishi network | 122 | 38 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 2 | 1 | 1 |  | 1 |  |  |  |  | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 700 | 2 |  | 1 | 4000 |  | 4 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Water point at centre kigamba/Rutumvo gravity | 172 | 172 |  | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | [9 empty] | 18 | [9 empty] | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kinini |  |  | Kinini water point/Ntaruka-Gahama gravity | 250 | 250 |  | Piped Network -- Gravity Only | 2008 | Gor | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 19 | 9 | [7 empty] | 11 | 1 | 1 | [7 empty] | 1 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 100 | [5 empty] | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2006 | 1 | 2006 | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2008
2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kinini |  |  | Kinini 2 water point/Ntaruka-gahama gravity | 250 | 250 | 107 | Piped Network -- Gravity Only | 2006 | Gor | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  |  | 19 | [6 empty] | 9 |  |  | 2 | [6 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2006 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2006
2017 | Rwanda | Rulindo | Masoro | Kigarama | Rukurazo |  |  | Mutagata Gravity network | 247 | 140 |  | Piped Network -- Gravity Only | 1987 |  | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures Distribution Line, | Create Plan To Repair or Replace Components | 17 | 7 | 17 | 7 | 17 |  |  |  |  | 7 | 2 | 2 | 2 | 2 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3500 | 6 | 4 | 2 | 4500 |  | 12 | 1 | "Springbox" --Intake Structure At A Spring | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Bushoki | Mukoto | Muko |  |  | Water point at Godoro/Rusave gravity system | 116 | 116 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 16 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Tumba | Barari | Kigarama |  |  | Water point nearby APEKI Tumba Technical School/Nyirambuga pumping | 154 | 154 | 780 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Nyakabanga |  |  | 0 | 780 |  | 63 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 3 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 22 | 17 | 27 | 17 | 27 | -1 | 12 |  |  | 17 | 1 | 3 | 3 | 3 | 3 | 1 | 1 |  |  | 3 | 3 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 3 | 2 | 3000 | 2 | 8 | 2 | 3000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Kinihira | Butunzi | Gisekuru |  |  | Nyamagana-Kinihira | 143 | 80 | 256 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 325 | 69 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2015
2017 | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at Buyoga sector/Nyirambuga pumping | 177 | 177 | 33 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Gatete |  |  | gahama | 163 | 130 |  | Piped Network -- Gravity Only | 2012 | Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 30000 | 7 | 14 | 2 | 30000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Rusana |  |  | Rwamugaza network | 276 | 276 | 58 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Kinihira | Butunzi | Kiniihira |  |  | Nyamagana-Kinihira | 118 | 60 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 6000 | 7 | 8 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Rwanzu |  |  | Matonyanga source catchment | 154 | 154 |  | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 30 | 20 | 30 |  | 30 |  |  |  |  | 20 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 100 | 1 |  | 2 | 4000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 1 | 2017 | 1 | 2017 | 0 |  | 1 | 2017 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Ruhanya |  |  | musenge | 25 | 25 | 10 | Piped Network With Pump | 2014 | Water For People | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Other Concrete Structures Distribution Line, Pump, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Cyinzuzi | Migendezo | Gitabage |  |  | Kararama | 70 | 60 |  | Piped Network With Pump | 2009 | Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 12 | 22 | 12 | 22 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 5000 | 7 | 14 | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Kingazi water point chez Rwigema/Nyakabizi gravity | 157 | 157 |  | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 26 | [6 empty] | 16 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2013 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Tare |  |  | Nyakariba-Tare gravity system | 109 | 109 |  | Piped Network -- Gravity Only | 2015 | Loal Government In Ubudehe Program | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Rwanzu |  |  | Rwanzu2 wpt/Nyirambuga pumping | 154 | 154 | 100 | Piped Network With Pump | 2012 | Gor | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 15 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 11 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gisiza |  |  | kinywamagana pumping network | 212 | 112 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Murambi2 water point/Nyirambuga pumping | 174 | 174 | 52 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 15 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 11 | [9 empty] | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Masoro | Shengampuri | Amataba |  |  | Mutagata Gravity Network | 178 | 126 | 88 | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 17 | 7 | 17 | 7 | 17 |  |  |  |  | 7 | 2 | 2 | 2 | 2 | 2 |  |  |  |  | 2 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 3500 | 6 | 4 | 2 | 4500 |  | 12 | 1 | "Springbox" --Intake Structure At A Spring | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Nyarurembo |  |  | Mutagata motorised network | 144 | 56 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyakambu |  |  | Rwamugaza network | 186 | 186 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Burega | Butangampundu | Gashinge |  |  | Rwamugaza | 435 | 435 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 16 | 6 | 27 | 17 | [5 empty] | 17 | 1 | 1 | 1 | 1 | [5 empty] | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 2 | 2 | 1 | 8000 | 10 | 8 |  |  |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2014 | 1 | 2014 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Burega | Butangampundu | Kibiraro |  |  | Rwamugaza | 500 | 500 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 4 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 16 | 17 | 16 | 17 | [5 empty] | 17 | 1 | 1 | 1 | 1 | [5 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 2 | 1 | 8000 | 20 | 16 |  |  |  | 1 | 1 |  | 2003 | 1 | 2014 | 1 | 2003 | 1 | 2014 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Amahoro |  |  |  | 120 | 120 | 121 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring¦Null | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 5300 | 24 | 2 | 2 | 17200 | 2 | 32 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Masoro | Shengampuri | Umubuga |  |  | Mutagata Gravity Network | 175 | 54 |  | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 17 | 7 | 17 | 7 | 17 |  |  |  |  | 7 | 2 | 2 | 2 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3500 | 6 | 4 | 2 | 4500 |  | 12 | 1 | "Springbox" --Intake Structure At A Spring | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Burega | Taba | Mwenene |  |  | Rwamugaza | 445 | 445 | 78 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyabitare |  |  | Gisoro-Nyundo network | 130 | 52 | 60 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Storage Tank, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 6 | 10 | 2 | 7000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Ngoma | Karambo | Nyakagezi |  |  | Sehuta | 99 | 39 | 111 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 1 | 1 | 1 |  | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1500 | 1 |  | 1 | 200 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Murambi | Bubangu | Gashubi |  |  | Mutagata Motorised Network | 140 | 29 | 10 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Rukozo | Mbuye | Musare |  |  | Kabonanyoni | 80 | 70 | 11 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 2015 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | Nyagahera | 151 | 140 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 27 | 17 | 18127 | 17 | 27 |  |  |  |  | 17 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 6800 | 3 | 3 | 1 | 1200 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 20114 | 1 | 2014 | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Base | Gitare | Rugerero |  |  | Water point at Mbarusha/Nyirambuga pumping system | 143 | 143 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Buyoga | Busoro | Karambo |  |  | Water point2 at Gakoma/Nyirambuga pumping | 138 | 138 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Burega | Butangampundu | Karambi |  |  | Rwamugaza | 365 | 365 | 136 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Storage Tank, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 16 | 17 | 16 | 6 | [5 empty] | 17 | 1 | 1 | 2 | 1 | [5 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 2 | 1 | 8000 | 10 | 8 |  |  |  | 1 | 1 |  | 2003 | 1 | 2014 | 1 | 2003 | 1 | 2003 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Nyamirembe |  |  | kirikumuryango network | 256 | 120 | 28 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 500 | 17 | 6 | 2 | 10000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Base | Rwamahwa | Kabahama |  |  | Migogo | 178 | 150 |  | Piped Network -- Gravity Only | 2009 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Conduction Line, Storage Tank, Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 22 | 12 | 22 |  | 22 |  |  |  |  | 12 | 1 | 2 | 2 |  | 2 |  |  |  |  | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 6800 | 3 |  | 1 | 6800 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 0 |  | 1 | 2009 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo |  |  |  | 203 | 203 | 64 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5000 | 15 |  | 1 | 5000 | 1 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kagunda |  |  | Muvumu-Taba | 94 | 30 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components |  | 16 | 26 | 16 | 26 |  |  |  |  | 16 |  | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 |  | 1 | 800 | 3 | 9 | 1 | 7500 |  | 1 | 0 |  |  | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kamatongo |  |  | 0 | 1125 | 1125 |  | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 2 | 1 | 1 | 35000 | 3 | 6 | 1 | 35000 | 3 | 1 | 1 |  | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Tumba | Barari | Rukore |  |  | Water point at Rukore center/Nyirambuga pumping | 157 | 157 | 5 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 25 |  | 28 |  |  |  |  | 18 |  |  | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  | 2 | 2000 |  | 2 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rukozo | Buraro | Nyenyeri |  |  | Kabonanyoni | 45 | 40 | 7 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Conduction Line, | Create Plan To Repair or Replace Components | 28 | 18 | 28 | 18 | 28 | 6 | 18 |  |  | 18 | 1 | 2 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kisaro | Sayo | Cyasuli |  |  | Kiruruma | 129 | 122 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 9000 | 15 | 4 | 3 | 4000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Gakenke |  |  | Gahama Kisaro network | 173 | 173 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Other Concrete Structures Pump, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 2 | 1 | 2 | 1 |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 30000 | 7 | 14 | 1 | 30000 | 2 | 1 | 1 |  | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Bushoki | Giko | Kivomo |  |  | Kivomo2 water point/Buramira gravity | 127 | 127 | 50 | Piped Network -- Gravity Only | 2015 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Cyungo | Rwili | Nturo |  |  | Sakara | 570 | 520 | 5 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 29 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1200 | 2 | 5 | 1 | 2300 | 2 | 4 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rukozo | Buraro | Rukingu |  |  | Kabonanyoni | 30 | 25 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Tumba | Barari | Karambi |  |  | Karambi water point/Nyirambuga pumping | 170 | 170 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Burega | Karengeli | Rwamiko |  |  | Rwamugaza | 440 | 440 | 46 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | kiduha | 151 | 105 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 11 |  | 32 | 9000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Rusiga | Kirenge | Rebero |  |  | Kigarama source/AEP Kigarama | 243 | 243 |  | Piped Network -- Gravity Only | 2015 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | [5 empty] | 18 | 1 | 1 | 1 | 1 | [5 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 100 | 1 | 1 |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Gitaba |  |  | Gitaba water point/Nyirambuga pumping | 118 | 118 | 92 | Piped Network With Pump | 2012 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 25 | [6 empty] | 15 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Kinihira | Rebero | Kirwa |  |  | Miyove-Kinihira | 187 | 95 | 60 | Piped Network -- Gravity Only | 1989 | Kgww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 7 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, Kiosk/Tap Stand | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | 18 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gihonga |  |  | Kibuye | 110 | 50 | 20 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 |  | 19 | 29 |  |  |  |  | 19 | 1 | 1 |  | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1500 |  | 1 | 1 | 1000 |  | 2 | 1 | Start And Collection Chamber | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 200 | 180 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Nyakabizi1 source/Nyakabizi1 gravity-Gakenke | 200 | 200 | 145 | Piped Network -- Gravity Only | 2015 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | [6 empty] | 18 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 100 | 1 |  |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 165 | 20 | 87 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Muvumu |  |  | Muvumu- Taba | 132 | 45 | 75 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components |  | 16 | 26 | 16 | 26 |  |  |  |  | 16 |  | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 |  | 1 | 800 | 3 | 9 | 1 | 7500 |  | 1 | 0 |  |  | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kiviri |  |  | Muvumu- Taba | 135 | 60 | 20 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components |  | 16 | 26 | 16 | 26 |  |  |  |  | 16 |  | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 |  | 1 | 800 | 3 | 9 | 1 | 7500 |  | 1 | 0 |  |  | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Base | Gitare | Bushyiga |  |  | Gihanga | 170 | 150 | 10 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | [9 empty] | -19 | [9 empty] | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 1978
2017 | Rwanda | Gicumbi | Miyove | Mubuga | Gatare |  |  | Kabonanyoni | 30 | 20 | 51 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | kiduha | 151 | 100 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 11 |  | 3 | 9000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Terambere |  |  | Rutare-Nyirangarama gravity system/Water point at Terambere | 118 | 118 | 5 | Piped Network -- Gravity Only | 1960 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | [9 empty] | -37 | [9 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 1960
2017 | Rwanda | Rulindo | Rukozo | Buraro | Kabingo |  |  | Kabonanyoni | 40 | 35 | 112 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Murambi | Mvuzo | Rurama |  |  | Mutagata Motorised Network | 155 | 43 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 6 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Rusiga | Taba | Karambi |  |  | Water point at GS Gitanda/Nyakabizi gravity | 109 | 109 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 16 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Mbogo | Bukro | Buhira |  |  | Musenge Network | 52 | 52 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Tumba | Gahabwa | Mafene |  |  | Water point chez Mukamponga/Nyirambuga pumping system | 172 | 172 |  | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 20 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Bushoki | Giko | Cyili |  |  | Cyili water point/Rutomvu gravity | 169 | 169 | 111 | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 26 | [6 empty] | 16 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2013 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Nyabisindu |  |  | kirikumuryango network | 149 | 38 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Masoro | Shengampuri | Rusine |  |  | Mutagata Gravity network | 220 | 220 |  | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures Distribution Line, | Create Plan To Repair or Replace Components | 17 | 7 | 17 | 7 | 17 |  |  |  |  | 7 | 2 | 2 | 2 | 2 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3500 | 6 | 4 | 2 | 4500 |  | 12 | 1 | "Springbox" --Intake Structure At A Spring | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kinini/Mbogo |  |  | Kinini-Mbogo water point/Ntaruka-Gahama gravity | 188 | 188 | 53 | Piped Network -- Gravity Only | 2006 | Gor | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 19 | 9 | [7 empty] | 9 | 1 | 1 | [7 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 100 | [5 empty] | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2006 | 1 | 2006 | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2006
2017 | Rwanda | Rulindo | Buyoga | Mwumba | Nyarubuye |  |  | kiruruma | 173 | 120 | 29 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | [6 empty] | 20 | 1 | 1 | 1 | [6 empty] | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 1 | 6700 | 5 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Kisaro | Murama | Mugomero |  |  | gahama | 129 | 100 | 5 | Piped Network With Pump | 2012 | Waterforpeople | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 30000 | 7 | 14 | 2 | 30000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Rukozo | Buraro | Kabgayi |  |  | Kabonanyoni | 60 | 55 | 100 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gakoma |  |  | Musenge network | 146 | 46 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Distribution Line, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 1 | 2 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | Nkanga center water point/Kivomo-Ntakara gravity | 129 | 129 | 57 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 18 | [9 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Nyabubare |  |  | Muvumu- Taba | 97 | 40 | 59 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components |  | 16 | 26 | 16 | 26 |  |  |  |  | 16 |  | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 |  | 1 | 800 | 3 | 9 | 1 | 7500 |  | 1 | 0 |  |  | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Mutoyi |  |  | Miyove-Kinihira | 119 | 60 | 5 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, Kiosk/Tap Stand | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | 18 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Buyoga | Ndarage | Gahondo |  |  | Ndarage | 105 | 100 | 50 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | [5 empty] | 17 | 1 | 1 | 1 | 1 | [5 empty] | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 6300 | 5 | 8 |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Mushali | Gitaba |  |  | Gitabage Network | 118 | 68 |  | Piped Network -- Gravity Only | 2008 | Catholic Church | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 21 | 11 | 21 |  | 21 |  |  |  |  | 11 | 1 | 1 | 1 |  | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 700 | 2 |  | 1 | 500 |  | 3 | 1 | "Springbox" --Intake Structure At A Spring | 2008 | 1 | 2008 | 1 | 2008 | 0 |  | 1 | 2008 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2008
2017 | Rwanda | Rulindo | Tumba | Barari | Karambi |  |  | Karambi2 water point/Nyirambuga pumping | 170 | 170 | 231 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | kinywamagana pumping network | 281 | 50 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | Mukoto | Mukoto |  |  | Mukoto water point/Nyagahondo gravity system | 119 | 119 | 89 | Piped Network -- Gravity Only | 2010 | Caritas | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 13 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2010
2017 | Rwanda | Rulindo | Kinihira | Butunzi | Ndorandi |  |  | Nyamagana-Kinihira | 139 | 50 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kigarama |  |  | charity water 203.031 | 1165 | 1165 |  | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 35000 | 10 | 8 | 1 | 1000 | 3 | 1 | 1 |  | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point for People near Buyoga secondary school/Nyirambuga pumping | 177 | 177 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | [9 empty] | 18 | [9 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Buyoga | Karama | Cyasenga |  |  | Water point at grouped area of Cyasenga/Nyirambuga | 165 | 165 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | [9 empty] | 18 | [9 empty] | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point[Charity:Water203.148]/AEP Kigarama gravity | 243 | 243 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 29 | [6 empty] | 19 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rusiga | Kirenge | Ntaruka |  |  | Ntaruka source/Ntaruka-Gahama gravity | 176 | 176 |  | Piped Network -- Gravity Only | 2006 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 19 | 9 | 19 |  | 19 |  |  |  |  | 9 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 100 | 1 |  | 1 | 1000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2006 | 1 | 2006 | 1 | 2006 | 0 |  | 1 | 2006 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2006
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Budaha |  |  | Budaha water point/Nkombe gravity system | 205 | 205 |  | Piped Network -- Gravity Only | 2002 | Coforwa | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | [9 empty] | 5 | [9 empty] | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2002
2017 | Rwanda | Rulindo | Bushoki | Giko | Gashiru |  |  | Water point at Marembo center/Nyirambuga pumping system | 120 | 120 | 56 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 25 | [6 empty] | 15 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2012 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Base | Gitare | Nyamugali |  |  | Rutembe | 121 | 65 | 87 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 29 | 19 | 29 | [6 empty] | 20 | 1 | 1 | 1 | [6 empty] | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 2500 | 1 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Ngoma | Karambo | Karambi |  |  | Kabarore-Ngoma-Nyabuko network | 117 | 30 | 58 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Intake Structure, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 2 | 1 | 1 |  | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 2 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Kinihira | Butunzi | Kiniihira |  |  | Nyamagana-Kinihira | 118 | 60 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 3 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Karera |  |  | Rwamugaza network | 182 | 182 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyarurama |  |  | Rwamugaza network | 168 | 168 | 24 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 14 | 1 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Base | Cyohoha | Gitwa |  |  | Gihanga | 104 | 80 | 36 | Piped Network -- Gravity Only | 1980 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | -2 | 17 | 27 | [6 empty] | 17 | 1 | 1 | 2 | [6 empty] | 1 | 2 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 5000 | 2 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 1985 | 1 | 2014 | 1 | 2014 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Buyoga | Mwumba | Murambo |  |  | Kiruruma | 136 | 100 | 50 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 3 | 9000 | 11 |  | 3 | 9000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Cyungo | Marembo | Rusayo |  |  | Nyabirarama | 150 | 100 |  | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 |  |  |  |  | 18 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1200 | 1 | 1 | 1 | 1200 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Cyinzuzi | Rudogo | Gaseke |  |  | Nyamateke network | 127 | 127 | 100 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 16 | 14 | 16 | 6 | 24 |  |  |  |  | 6 | 1 | 1 | 2 | 3 | 1 |  |  |  |  | 1 | 3 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 2 | 1 | 2 | 30000 | 5 | 6 | 1 | 30000 |  | 1 | 1 |  | 2003 | 1 | 2011 | 1 | 2003 | 1 | 2003 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kiziranyenzi |  |  | kinywamagana pumping network | 140 | 40 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Terambere |  |  | Rutare-Nyirangarama gravity system/Terambere water point | 118 | 118 |  | Piped Network -- Gravity Only | 1960 | Government | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | -37 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | [9 empty] | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 1960
2017 | Rwanda | Rulindo | Tumba | Taba | Nyirataba |  |  | Water point at EP Ruvumba/Nyirambuga pumping | 169 | 169 | 5 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 6 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rukozo | Buraro | Kabgayi |  |  | Kabonanyoni | 40 | 35 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Rusiga | Gako | Kabunigu |  |  | Water point at Kabunigu/Tare-Rusiga pumping system | 219 | 219 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutembe | 229 | 229 | 26 | Piped Network -- Gravity Only | 2009 | Padiri | Groundwater (Well, Etc.) | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Storage Tank, Distribution Line, | Create Plan To Repair or Replace Components | 29 | 19 | 22 |  | 22 |  |  |  |  | 19 | 1 | 1 | 2 |  | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 1 | 2500 | 2 |  | 2 | 3000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2009 | 0 |  | 1 | 2009 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Kinihira | Rebero | Ndusu |  |  | Miyove-Kinihira | 146 | 120 | 49 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, Kiosk/Tap Stand | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | 18 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Ngoma | Karambo | Nyakagezi |  |  | Sehuta | 99 | 50 | 168 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1500 | 1 |  | 1 | 200 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Bitete-Rwahi network | 188 | 20 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 600 | 6 | 6 | 1 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Rusura |  |  | Water point near Rusura center/Nyirambuga pumping | 157 | 157 |  | Piped Network With Pump | 2017 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 30 |  | 30 |  |  |  |  | 20 |  |  | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 |  | 1 | 100 |  | 2 | 0 |  |  | 0 |  | 1 | 2017 | 0 |  | 1 | 2017 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Masoro | Kigarama | Nyakibungo |  |  |  | 229 | 229 | 92 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 100 |  | Piped Network -- Gravity Only | 2017 | Padiri | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 30 | [8 empty] | 20 | 1 | 1 | [7 empty] | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 3 | 2 |  | 6450 | [5 empty] | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 0 | 2016 | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Tumba | Taba | Ruvumba |  |  | Water point chez Fari/Nyirambuga pumping | 109 | 109 | 5 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Rukozo | Buraro | Rukingu |  |  | Kabonanyoni | 70 | 65 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point1 at ADEPR PEPO Tumba/Nyirambuga pumping | 169 | 169 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 5 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kibamba |  |  | Musenge Network | 76 | 76 | 40 | Piped Network With Pump | 2014 |  | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 70 | 30 | 52 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyarusange |  |  | Gisoro- Nyundo network | 97 | 45 | 8 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 6 | 10 | 2 | 7000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Cyinzuzi | Migendezo | Rusagara |  |  | Kararama | 98 | 90 | 25 | Piped Network With Pump | 2009 | Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 12 | 22 | 12 | 22 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 5000 | 7 | 14 | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Buyoga | Ndarage | Kagozi |  |  | ndarage | 155 | 130 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 6700 | 5 |  | 1 | 6700 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Buyoga | Karama | Kajeneni |  |  | Kajeneni water point/Nyirambuga pumping system | 175 | 175 | 84 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  |  | 30 | [6 empty] | 20 |  |  | 1 | [6 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2017 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Bugarura |  |  | kirikumuryango network | 119 | 35 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Tumba | Taba | Nyirataba |  |  | Nyirataba2 water point/Nyirambuga pumping | 169 | 169 | 5 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 3 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Cyungo | Burehe | Nyagatovu |  |  | Nyamagana | 50 | 45 | 5 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Rukozo | Buraro | Kamiyove |  |  | Kabonanyoni | 70 | 65 | 92 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 3 | 1 | 1 | 1 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 100 |  | Piped Network -- Gravity Only | 2012 | Padiri | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 25 | 15 | 25 | 15 | 25 |  |  |  |  | 15 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 3 | 2 | 2 | 6450 | 3 | 3 | 2 | 6800 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Tumba | Barari | Gaseke |  |  | Water point at Gashora/Nyirambuga pumping | 149 | 149 | 10 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 30 | [6 empty] | 20 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2017 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Base | Cyohoha | Gihemba |  |  | Nyamagana | 100 | 90 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Tumba | Misezero | Taba |  |  | Water point at Taba/Nyirambuga pumping | 100 | 100 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  |  | 15 | [5 empty] | 15 |  |  |  | 1 | [5 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 |  |  |  | 2 | 0 |  |  | 0 |  | 0 |  | 1 | 2012 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kalindi |  |  | Musenge Network | 55 | 55 | 106 | Piped Network With Pump | 2014 | Wfp | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gicumbi |  |  | Musenge Network | 141 | 35 |  | Piped Network With Pump | 2014 |  | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Base | Gitare | Gihora |  |  | Gihora2 Water point/Rutomvu gravity | 101 | 101 |  | Piped Network -- Gravity Only | 2013 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 16 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | Water point at GS Rusiga/Tare-Rusiga pumping | 281 | 281 | 80 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kinihira | Marembo | Gatare |  |  | Nyamagana- Kinihira | 160 | 80 | 138 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 7 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Masoro | Kivugiza | Gasenga |  |  | Mutagata motorised network | 284 | 146 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Rusiga | Taba | Karambi |  |  | Karambi water point/Nyakabizi gravity | 109 | 109 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 16 | [9 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Cyinzuzi | Rudogo | Munoga |  |  |  | 98 | 98 | 145 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Intake Structure, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 24 | 14 | 24 | 14 | 24 |  |  |  |  | 6 | 2 | 1 | 1 | 1 | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 30000 | 5 | 6 | 1 | 30000 |  | 1 | 1 |  | 2011 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Ruhondo |  |  | Musenge network | 184 | 39 | 158 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Other Concrete Structures Distribution Line, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Bitete-Rwahi network | 188 | 30 | 9 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 600 | 6 | 6 | 1 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Base | Cyohoha | Bukangano |  |  | Migogo | 129 | 120 | 49 | Piped Network -- Gravity Only | 2009 | Italians(Lake Angels) | Groundwater (Well, Etc.)¦Lake/Reservoir | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Conduction Line, Storage Tank, Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 22 | 12 | 22 |  | 22 |  |  |  |  | 12 | 1 | 2 | 2 |  | 2 |  |  |  |  | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 2 | 3000 | 3 |  | 2 | 3000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 0 |  | 1 | 2009 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Buyoga | Gahororo | Gatare |  |  | kiruruma | 169 | 120 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 20 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 2 | 4200 | 11 |  | 3 | 4200 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Cyinzuzi | Rudogo | Kirambo |  |  | Nyamateke source | 137 | 137 | 10 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 2 | 30000 | 5 | 6 | 1 | 30000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Rukozo | Mbuye | Mujebe |  |  | Kabonanyoni | 90 | 80 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Cyinzuzi | Rudogo | Kirambo |  |  | Nyamateke network | 137 | 137 | 121 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 2 | 30000 | 5 | 14 | 1 | 30000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Murambi | Mugambazi | Buliza |  |  | Mutagata Motorised Network | 221 | 100 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Tare-Rusiga water pumping system/Nyakabingo1 water spring source | 228 | 228 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | [5 empty] | 18 | 1 | 1 | 1 | 1 | [5 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 400 | 2 | 1 |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Kiyanza I |  |  | Rwamugaza network | 1025 | 1025 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | Giko | Ngarama |  |  | Ngarama2 water point/Nkore gravity | 110 | 110 | 69 | Piped Network -- Gravity Only | 2013 | Private People Joined Hands Together To Get Water | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | [9 empty] | 16 | [9 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Ngoma | Munyarwanda | Busizi |  |  | Kabarore-Ngoma-Nyabuko network | 100 | 31 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Pump, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 2 | 1 |  |  | 2 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 4 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Tare |  |  | Nyabishengeshi gravity system | 109 | 109 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 16 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Bushoki | Giko | Rugote |  |  | Water point chez Jean de Dieu/Nyirambuga pumping system | 120 | 120 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyagasozi |  |  | Rwamugaza network | 197 | 197 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 14 | 1 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Burega | Taba | Lyinzovu |  |  | Rwamugaza | 505 | 505 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Murambi | Mvuzo | Ntyaba |  |  | Mutagata Motorised Network | 136 | 136 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at Buyoga Banque Populaire/Nyirambuga pumping | 177 | 177 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 6 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Buyoga | Karama | Kigarama |  |  | Kigarama water point/Nyirambuga pumping | 121 | 121 |  | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  |  | 30 | [6 empty] | 20 |  |  | 3 | [6 empty] | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2017 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Buhande |  |  | Buhande water point/Tare-Rusiga pumping system | 129 | 129 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 10 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Tare |  |  | Nyakariba-Tare small gravity system | 109 | 109 | 23 | Piped Network -- Gravity Only | 2015 | Local Government In Ubudehe Program | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 |  |  |  |  | 18 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 1 | 1 | 1 | 500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Gatete |  |  | gahama | 163 | 140 |  | Piped Network With Pump | 2012 | Waterforpeople | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 | 25 | 15 | [5 empty] | 15 | 1 | 1 | 1 | 1 | [5 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 12000 | 7 | 14 |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Remera water point from Rutare gravity on Tare pumping | 228 | 228 | 50 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 30 | 18 | 28 |  | 28 |  |  |  |  | 18 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 8 | 8 | 1 | 2000 | 1 |  | 1 | 2000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Cyungo | Rwili | Nyabisasa |  |  | Sakara | 570 | 520 | 82 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 29 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 1200 | 2 | 5 | 1 | 2300 | 2 | 4 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyarunyinya |  |  | Bitete-Rwahi network | 132 | 50 | 70 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Storage Tank, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 2 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 600 | 6 | 6 | 1 | 6500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Ngoma | Munyarwanda | Busizi |  |  | Kabarore-Ngoma-Nyabuko network | 100 | 30 | 94 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 |  | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 4 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gakoma |  |  | Musenge network | 146 | 52 | 35 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Other Concrete Structures Distribution Line, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Base | Gitare | Kirwa |  |  | Rwicanyoni | 136 | 101 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | [6 empty] | 19 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 8600 | 3 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  |  | 30 | 30 |  | Piped Network -- Gravity Only | 2015 | Wfp | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 |  |  |  |  | 18 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 1 | 1500 | 1 | 3 | 2 | 500 |  | 5 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Tumba | Misezero | Kavumu |  |  | Water point chez Habarugira/Nyirambuga pumping | 139 | 139 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Ngarama |  |  | Nyabishengeshi gravity system/Water point at Nyirangarama | 89 | 89 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 16 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Tumba | Taba | Mwili |  |  | Mwili2 water point/Nyirambuga pumping | 141 | 141 | 92 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | [9 empty] | 18 | [9 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 100 | 127 | Piped Network -- Gravity Only | 2012 | Padiri | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 |  |  | 25 |  |  |  |  | 15 | 1 | 1 |  |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 6450 |  |  | 1 | 4000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 0 |  | 0 |  | 1 | 2012 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Kinihira | Rebero | Kirwa |  |  | Miyove-Kinihira | 187 | 60 | 28 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures, Pump, Pump Station, Treatment Equipment, | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | -8 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1989
2017 | Rwanda | Rulindo | Base | Rwamahwa | Kabahama |  |  | Migogo | 178 | 150 | 24 | Piped Network -- Gravity Only | 2009 | Padiri(Lake Angels). | Groundwater (Well, Etc.) | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Conduction Line, Storage Tank, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 22 | 12 | 22 | [6 empty] | 12 | 1 | 2 | 2 | [6 empty] | 2 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 2 | 6200 | 1 |  |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Cyungo | Rwili | Kabanda |  |  | Nyamagana | 50 | 26 | 70 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 4 | Repair or Replace Components | Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Murambi | Bubangu | Rebero |  |  | Mutagata Motorised Network | 148 | 78 | 108 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Murambi | Bubangu | Gashubi |  |  | Mutagata Motorised Network | 140 | 32 |  | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | WATER POINT AT VTC TUMBA/Nyirambuga pumping | 169 | 169 | 261 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Masoro | Kivugiza | Rebero |  |  | Mutagata motorised network | 376 | 115 | 5 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 20 | 19 | 29 | 19 | 29 | 7 | 19 | 10 |  | 19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1900 | 39 | 17 | 6 | 40000 | 5 | 64 | 1 | "Springbox" --Intake Structure At A Spring | 2007 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2017 | 1 | 2016 | 1 | Disinfection/Chlorination | 2017 | 0 |  | 1 | 2016
2017 | Rwanda | Rulindo | Rukozo | Buraro | Shyondwe |  |  | Kabonanyoni | 125 | 120 | 12 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 10 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Buyoga | Ndarage | Karambi |  |  | Ndarage | 112 | 100 | 102 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 | [6 empty] | 17 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 6700 | 5 |  |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Mwagiro |  |  | Kirikumuryango network | 139 | 37 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 780 | 780 |  | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Distribution Line, | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kavumu |  |  | 0 | 850 | 850 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 4 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 22 | 12 | 27 | 17 | 27 | -1 | 12 |  |  | 17 | 1 | 1 | 3 | 3 | 3 | 1 | 1 |  |  | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 3 | 3 | 2 | 5000 | 2 | 8 | 2 | 3000 | 1 | 1 | 1 |  | 2009 | 1 | 2009 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Bushoki | Mukoto | Marembo |  |  | Water point at GS Bushoki/Tare-Rusiga pumping system | 90 | 90 | 12 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 |  | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 10 | 8 | 1 | 4000 | 1 |  | 1 | 8000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 0 |  | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 180 |  | Piped Network -- Gravity Only | 2012 | Padiri | Spring¦Groundwater (Well, Etc.) | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 29 | 19 | 29 | 19 | 29 |  |  |  |  | 19 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 6450 | 3 | 1 | 2 | 4500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point at ADEPR Tumba/Nyirambuga pumping | 169 | 169 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Karera |  |  | Rwamugaza network | 182 | 182 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 17 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 14 | 1 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Ruhanya |  |  | musenge | 40 | 40 | 14 | Piped Network With Pump | 2014 | Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 4 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 2 | 1 | 1 | 2 | 2 | 2 |  |  | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Base | Cyohoha | Rubanda |  |  | Gihanga | 214 | 200 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  | 19 | 29 | [6 empty] | 19 |  | 2 | 1 | [6 empty] | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 |  | 1 | 7200 | 6 |  |  |  |  | 2 | 0 |  |  | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Water point at EP Gasiza/Nyagahondo gravity system | 228 | 228 | 84 | Piped Network -- Gravity Only | 2010 | Caritas | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 13 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2010
2017 | Rwanda | Rulindo | Kinihira | Rebero | Karambi |  |  | Miyove-Kinihira | 144 | 60 | 47 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 2 | -8 | 2 | -8 | 2 |  |  |  |  | -8 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1989
2017 | Rwanda | Rulindo | Ngoma | Mugote | Rukoma |  |  | Kararama pumping network | 92 | 45 |  | Piped Network With Pump | 2007 | Government | Spring¦Collection Chamber | Low Risk | High Risk | Basic Level of Service | High Priority | 4 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 20 | 10 | 20 | 10 | 20 | -3 | 10 |  |  | 10 | 1 | 1 | 1 | 1 | 2 | 2 | 2 |  |  | 3 | 3 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 4 | 3 | 1 | 1500 | 25 | 20 | 4 | 30000 | 2 | 47 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2007 | 1 | 2007 | 1 | 2007 | 1 | 2007 | 1 | 2007 | 1 | 2007 | 1 | 2007 | 0 |  |  |  |  | 1 | 2007
2017 | Rwanda | Rulindo | Ngoma | Kabuga | Kagarama |  |  | Kabarore- Ngoma- Nyabuko network | 57 | 57 | 42 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Intake Structure, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 2 | 1 | 1 |  | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 2 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Buyoga | Gahororo | Gipfundo |  |  | rugarama | 162 | 120 | 40 | Piped Network -- Gravity Only | 2012 | G. Thierry | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 | 25 | [6 empty] | 15 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4500 | 4 |  |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Cyungo | Burehe | Sove |  |  | Nyamagana | 75 | 35 | 41 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Low Risk | Basic Level of Service | Medium Priority | 5 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 24 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2011 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Buyoga | Gahororo | Gatenderi |  |  | kiruruma | 141 | 100 |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 30 | 17 | 27 |  | 27 |  |  |  |  | 17 | 1 | 1 | 1 |  | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 11 |  | 3 | 9000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutembe | 229 | 229 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 30 | 20 | 29 | 19 | [5 empty] | 19 | 1 | 1 | 1 | 1 | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 2500 | 1 | 3 |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 1 | 2017 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rusiga | Gako | Kabuye |  |  | Kabuye water point[RW.WFP.Q3.14.166.066]/Tare-Rusiga pumping | 169 | 169 | 62 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 10 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Nyabubare |  |  | Bitete-Muvumu | 97 | 35 | 5 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Conduction Line, Other Concrete Structures | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 2 | 1 | 2 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 11 | 1 | 6 | 1 | 4000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Cyinzuzi | Rudogo | Gasiza |  |  | Rwagitare | 45 | 40 |  | Piped Network -- Gravity Only | 2009 | Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 12 | 22 | 12 | 22 |  |  |  |  | 12 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1200 | 1 | 2 | 1 | 900 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 1200 | 1200 | 124 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 28 | 18 | 24 | 14 | 24 |  |  |  |  | 14 | 1 | 1 | 1 | 1 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 2100 | 11 | 15 | 3 | 37000 |  | 29 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2011 | 1 | 2011 | 1 | 2011 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2011
2017 | Rwanda | Rulindo | Kinihira | Marembo | Cyogo |  |  | Nyamagana-Kinihira | 184 | 60 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 19 | 19 | 6 | Piped Network -- Gravity Only | 1997 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 |  |  |  |  | 0 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 700 | 1 | 2 | 2 | 800 |  | 5 | 1 | Start Chamber And Collection Chamber | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1997
2017 | Rwanda | Rulindo | Buyoga | Gitumba | Munini |  |  | Kiruruma | 158 | 152 | 156 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 |  | 27 |  |  |  |  | 17 | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 9000 | 15 |  | 3 | 9000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyakambu |  |  | rwamugaza | 186 | 30 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 6 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 3 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 3 | 1 | "Springbox" --Intake Structure At A Spring | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Murambi water point/Nyirambuga pumping | 174 | 174 | 134 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 28 | [6 empty] | 18 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 |  |  |  | 1 |  |  |  |  | 2 | 0 |  |  | 0 |  | 1 | 2015 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  |  | 186 | 52 |  | Piped Network With Pump | 2014 |  | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  |  | 214 | 214 | 78 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Rusiga | Taba | Bitare |  |  | Muvumu- Taba | 113 | 35 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Intermediate Level of Service | High Priority | 7 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 30 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 3 | 1 | 2 | 1 | 1 |  |  |  |  | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 800 | 3 | 9 | 1 | 7500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2017 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Kayenzi |  |  | Rwamugaza network | 200 | 200 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Tumba | Misezero | Kavumu |  |  | Water point at Tumba Public RS/Nyirambuga pumping | 139 | 139 | 5 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | [9 empty] | 15 | [9 empty] | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | [8 empty] | 5 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Rukozo | Buraro | Kamiyove |  |  | Kabonanyoni | 70 | 65 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 6 | 19 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 1 | 720 | 19 | 10 | 3 | 19000 | 2 | 31 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kisaro | Kigarama | Runyinya |  |  | Gahama Kisaro network | 148 | 148 |  | Piped Network -- Gravity Only | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30000 | 7 | 14 | 1 | 30000 | 2 | 1 | 1 |  | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Tumba | Barari | Rukore |  |  | Water point at Tumba Health Center/Nyirambuga pumping | 157 | 157 | 113 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 4 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kigarama |  |  | kinywamagana pumping network | 233 | 120 |  | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kinini Ya Mbogo |  |  | Musenge Network | 100 | 100 | 110 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Other Concrete Structures Distribution Line, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 135 | 25 | 108 | Piped Network With Pump | 2014 | Water For People, Wasac And Rulindo District. | Spring | Low Risk | Medium Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Other Concrete Structures Distribution Line, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Mushali | Buraro |  |  | Matyazo network | 155 | 47 |  | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | 19 | 29 |  |  |  |  | 19 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 4 | 1 | 4300 | 1 | 2 | 1 | 1800 |  | 4 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Bushoki | Giko | Cyili |  |  | Water point at GS Mugenda/ Nyirambuga pumping system | 165 | 165 | 90 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ngoma | Kabuga | Nyabuko |  |  | Kabarore-Ngoma-Nyabuko network | 122 | 32 | 107 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 |  | 27 | 4 | 17 |  |  | 17 | 2 | 1 | 1 |  | 1 | 2 | 1 |  |  | 1 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 4 | 5 | 2 | 8000 | 13 |  | 2 | 7000 | 2 | 17 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 135 | 28 |  | Piped Network With Pump | 2014 | Water For People, Wasac And Rulindo District | Spring | Low Risk | Medium Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Other Concrete Structures Distribution Line, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 203 | 203 |  | Piped Network -- Gravity Only | 1998 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 |  | 29 | 6 | 19 |  |  | 19 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 5000 | 15 |  | 2 | 5000 | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 1 | 2016 | 1 | 2016 | 1 | 2016 | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Tumba | Gahabwa | Munyinya |  |  | Munyinya water point chez Rugigana/Nyirambuga pumping system | 142 | 142 | 380 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed |  | 20 | 30 |  | 30 |  |  |  |  | 20 |  | 1 | 1 |  | 1 |  |  |  |  | 3 | 3 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 2 |  | 1 | 500 | 1 |  | 1 | 500 |  | 2 | 0 |  |  | 1 | 2017 | 1 | 2017 | 0 |  | 1 | 2017 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2017
2017 | Rwanda | Rulindo | Burega | Butangampundu | Kigarama |  |  | Rwamugaza | 380 |  | 89 | Piped Network With Pump | 2009 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 3 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 22 | 12 | 27 | 17 | 27 | -1 | 12 |  |  | 17 | 1 | 1 | 3 | 3 | 3 | 1 | 1 |  |  | 3 | 3 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 3 | 2 | 3000 | 3 | 8 | 2 | 3000 | 1 | 1 | 1 |  | 2009 | 1 | 2009 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Kinihira | Butunzi | Ndorandi |  |  | Nyamagana-Kinihira | 139 | 50 | 1125 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kamatongo |  |  | 0 | 1125 |  | 98 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 3 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 22 | 12 | 27 | 17 | 27 | -1 | 12 |  |  | 17 | 1 | 1 | 3 | 3 | 3 | 1 | 1 |  |  | 3 | 3 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 3 | 2 | 3000 | 3 | 8 | 2 | 3000 | 1 | 1 | 1 |  | 2009 | 1 | 2009 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gakoma |  |  | Musenge network | 146 | 48 | 129 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Medium Risk | High Level of Service | Low Priority | 8 | Repair or Replace Components | Other Concrete Structures Distribution Line, Pump, | Create Plan To Repair or Replace Components | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 1 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Kinihira | Marembo | Kigali |  |  | Nyamagana- Kinihira | 189 | 60 |  | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 | 5 | 18 |  |  | 18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1000 | 7 | 8 | 3 | 6000 | 2 | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Bushoki | Giko | Ngarama |  |  | Ngarama water point/Nkore gravity system | 110 | 110 | 390 | Piped Network -- Gravity Only | 2013 | Private Group Of People That Have Joined Hands To Get Clean Water | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 16 | [9 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Burega | Butangampundu | Runyinya |  |  | Rwamugaza | 390 |  |  | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 3 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 22 | 12 | 27 | 17 | 27 | -1 | 12 |  |  | 17 | 1 | 1 | 3 | 3 | 3 | 1 | 1 |  |  | 3 | 3 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 3 | 2 | 3000 | 3 | 8 | 2 | 3000 | 1 | 1 | 1 |  | 2009 | 1 | 2009 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Tumba | Taba | Mwili |  |  | Mwili water point/Nyirambuga pumping | 141 | 141 | 75 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Kabagabaga |  |  | kirikumuryango network | 181 | 106 | 29 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 229 | 200 |  | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | Low Risk | Medium Risk | Basic Level of Service | Medium Priority | 5 | Repair or Replace Components | Intake Structure, Conduction Line, | Create Plan To Repair or Replace Components | 27 | 19 | 25 | 19 | [5 empty] | 19 | 2 | 2 | 1 | 1 | [5 empty] | 1 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 2 | 1 | 1 | 4280 | 1 | 1 |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2016 | 1 | 2012 | 1 | 2016 | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Cyinzuzi | Migendezo | Remera |  |  | 0 | 975 | 975 | 50 | Piped Network With Pump | 2009 | Umushinga Witwa Ema | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 12 | 22 | 12 | 22 | -1 | 12 |  |  | 12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 2 | 5000 | 16 | 23 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2009
2017 | Rwanda | Rulindo | Kisaro | Mubuga | Nyakarekare |  |  | gahama | 150 | 100 |  | Piped Network With Pump | 2012 | Waterforpeople | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 30000 | 7 | 14 | 2 | 30000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza | 229 | 229 |  | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 3 | 1 | "Springbox" --Intake Structure At A Spring | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Byimana |  |  | Nyabishengeshi gravity system | 92 | 92 |  | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 16 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Water point1 at Kingazi/Nyakabizi2 gravity | 157 | 157 |  | Piped Network -- Gravity Only | 2015 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring |  |  | 26 | [6 empty] | 16 |  |  | 1 | [6 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 |  |  |  | 1 |  |  |  |  | 1 | 0 |  |  | 0 |  | 1 | 2013 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Burega | Butangampundu | Mayaga |  |  | Rwamugaza network | 105 | 105 | 6 | Piped Network -- Gravity Only | 2003 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 14 | 1 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Base | Gitare | Gatete |  |  | Rwicanyoni | 141 | 135 |  | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 29 | 19 | 29 | [6 empty] | 19 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 8600 | 3 |  |  |  |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2016 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2016
2017 | Rwanda | Rulindo | Burega | Karengeli | Kiziba |  |  | Rwamugaza | 400 | 400 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Kayenzi |  |  | Rwamugaza network | 200 | 200 | 14 | Piped Network -- Gravity Only | 2003 | Government | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 16 | 6 | 16 | 6 | 16 |  |  |  |  | 6 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 35000 | 7 | 12 | 2 | 35000 |  | 1 | 1 |  | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Buyoga | Butare | Gasave |  |  | KIDUHA | 114 | 100 | 5 | Piped Network -- Gravity Only | 2007 | Italians (Lake Angels) Expanded By Water For People | Groundwater (Well, Etc.) | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, | Create Plan To Repair or Replace Components | 27 | 10 | 20 | [6 empty] | 17 | 2 | 2 | 2 | [6 empty] | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2200 | 3 |  |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2007 | 1 | 2007 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Buyoga | Ndarage | Gahondo |  |  | Ndarage | 105 | 100 | 164 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 27 | 17 | 27 | [6 empty] | 17 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 6700 | 5 |  |  |  |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  | Musenge Network | 186 | 22 | 11 | Piped Network With Pump | 2014 |  | Spring | Low Risk | High Risk | Basic Level of Service | High Priority | 5 | Major Repairs or Replace System |  | Further Technical Diagnostic Needed | 27 | 17 | 27 | 17 | 27 | 4 | 17 |  |  | 17 | 1 | 1 | 1 | 2 | 2 | 2 | 1 |  |  | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3000 | 16 | 8 | 3 | 20000 | 2 | 28 | 1 | "Springbox" --Intake Structure At A Spring | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 1 | 2014 | 0 |  |  |  |  | 1 | 2014
2017 | Rwanda | Rulindo | Cyungo | Marembo | Murambo |  |  | Mugomero Murambo | 161 | 150 | 102 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 28 | 18 | 28 | 18 | 28 |  |  |  |  | 18 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 10000 | 10 | 3 | 2 | 10000 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 1 | 2015 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Mbogo | Mushali | Buraro |  |  | Kishwi network | 155 | 53 |  | Piped Network -- Gravity Only | 2003 | Goverment | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 29 | 19 | 16 |  | 16 |  |  |  |  | 6 | 1 | 1 | 1 |  | 1 |  |  |  |  | 2 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 700 | 2 |  | 2 | 680 |  | 4 | 1 | "Springbox" --Intake Structure At A Spring | 2016 | 1 | 2016 | 1 | 2003 | 0 |  | 1 | 2003 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2003
2017 | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water at Buyoga Market/Nyirambuga pumping | 177 | 177 |  | Piped Network With Pump | 2015 |  | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Kisaro | Murama | Akamanama |  |  | Gahama Kisaro network | 141 | 141 | 71 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 25 | 15 | 25 | 15 | 25 | 2 | 15 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30000 | 7 | 14 | 1 | 30000 | 2 | 1 | 1 |  | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Buhita |  |  | Miyove-Kinihira | 131 | 60 | 128 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | High Risk | Medium Risk | Intermediate Level of Service | Medium Priority | 6 | Consider Replacing Aging Components | Intake Structure, Conduction Line, Storage Tank, Pump, Pump Station, Treatment Equipment, Kiosk/Tap Stand | Further Technical Diagnostic Needed | 2 | -12 | -2 | 18 | 2 |  |  |  |  | 18 | 2 | 2 | 1 | 2 | 2 |  |  |  |  | 1 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 6 | 3 | 1 | 8000 | 4 | 18 | 2 | 15000 |  | 2 | 1 | "Springbox" --Intake Structure At A Spring | 1989 | 1 | 1985 | 1 | 1985 | 1 | 2015 | 1 | 1989 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Bushoki | Gasiza | Buhande |  |  | Water point at Pensez-y/Gasebeya gravity system | 129 | 1 |  | Piped Network -- Gravity Only | 2004 | Pensez-Y Bar Restaurant | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 7 | [9 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Water point nearby Giko cell/Nyirambuga pumping | 134 | 134 |  | Piped Network With Pump | 2012 | Gor | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 15 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 1 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point nearby Gisha/Nyirambuga pumping | 133 | 133 |  | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | [9 empty] | 18 | [9 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 11 | [8 empty] | 2 | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  |  | 1 | 2015
2017 | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 495 | 495 |  | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 6 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 22 | 15 | 25 | 15 | 25 | -1 | 12 |  |  | 15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 3 | 3 | 2 | 5000 | 16 | 8 | 2 | 5000 | 1 | 1 | 1 |  | 2009 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2012 | 1 | 2009 | 1 | 2009 | 0 |  |  |  |  | 1 | 2012
2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Rutonde |  |  | kirikumuryango network | 160 | 160 | 166 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | High Level of Service | Low Priority | 8 | Perform Routine Preventative Maintenance |  | Maintain O&M and Routine Monitoring | 26 | 16 | 26 | 16 | 26 |  |  |  |  | 16 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 500 | 17 | 6 | 2 | 3500 |  | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2013
2017 | Rwanda | Rulindo | Masoro | Shengampuri | Amataba |  |  | Mutagata Gravity network | 220 | 54 | 130 | Piped Network -- Gravity Only | 2004 |  | Spring | Low Risk | Medium Risk | Intermediate Level of Service | Low Priority | 6 | Repair or Replace Components | Intake Structure, Conduction Line, Storage Tank, Other Concrete Structures Distribution Line, Kiosk/Tap Stand | Create Plan To Repair or Replace Components | 17 | 7 | 17 | 7 | 17 |  |  |  |  | 7 | 2 | 2 | 2 | 2 | 2 |  |  |  |  | 2 | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 3500 | 6 | 4 | 2 | 4500 |  | 12 | 1 | "Springbox" --Intake Structure At A Spring | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 1 | 2004 | 0 |  |  |  | 0 |  |  |  |  | 1 | 2004
2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 165 | 35 | 0 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | Low Risk | Low Risk | Intermediate Level of Service | Low Priority | 7 | Repair or Replace Components | Pump, | Create Plan To Repair or Replace Components | 26 | 16 | 26 | 16 | 26 | 3 | 16 |  |  | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 1 |  |  | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7 | 3 | 1 | 1500 | 20 | 25 | 4 | 11000 | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 1 | 2013 | 0 |  |  |  |  | 1 | 2013

## Details and Calculations
Year Data Was Collected | Collection Date | Country Name | Geo Level 2 | Geo Level 3 | Geo Level 4 | Geo Level 5 | Geo Level 6 | Community Name | Water Point/System Unique ID | Total Number Of Families In The Community | Population Using System | Number of Water Points | Users/Water Point | Total Number Of Families With Access To An Improved Water Point/System | Total Number Of Families Without Access To An Improved Water Point/System | Calculation % of Families With No Access | Families With Access to An Improved Water Point/System. 1: 95% or Higher; 0: 94% or Lower | Number Of Users Meets Gov. Standards 1: # Of Users =< Gov.Standards; 0 # Of Users More Than Gov. Standards | Water Point/System Improved Or Unimproved. 1: Improved; 0: Unimproved | Type Of Water Point/System | Year Of Construction | Construction Funded By | Source Of Water Point/System | Number Of Sources | Is The Source Protected? 1: Yes; 0: No | Presence Of Intake Structure? 1: Yes; 0: No | Type Of Intake Structure | Number Of Intake Structures | Year The Intake Structure Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction. | Physical State Of The Intake Structure. 1: Normal; 2: Poor; 3: Does Not Function; None: Leave Blank | Seconds To Fill 20 Liter Container | Calculation Liters Per Day | Calculation Liters Provided Per Person Per Day | Does The Water Point/System Provide Adequate Water Quantity? 1: Yes; 0: No | Presence Of Conduction Line? 1: Yes; 0: No | Number Of Conduction Lines | Year Conduction Line was Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Physical State Of The Conduction Line. 1: Normal; 2: Poor; 3: Does Not Function; None: Leave Blank | Aproximate Length Of Conduction Line(s) In Meters | Presence Of Storage Tank? 1: Yes; 0: No | Number Of Storage Tanks | Year The Storage Tank Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Physical State Of The Storage Tank. 1: Normal; 2: Poor; 3: Does Not Function; None: Leave Blank | Presence Of Other Concrete Structures (Sedimentation Tank, Pressure Break Tank, etc.)? 1: Yes; 0: No | Number Of Other Concrete Structures | Type(s) Of Other Concrete Structures | Year Other Concrete Structures (Sedimentation Tank, Pressure Break Tank, etc.) Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Physical State Of The Concrete Structures (Sedimentation Tank, Pressure Break Tank, etc.) : Normal. 1: Normal; 2: Poor; 3: Does Not Function; None: Blank | Presence Of Distribution Network? 1: Yes; 0: No | Number Of Distribution Networks | Year The Distribution Network Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Physical State Of The Distribution Network: Normal. 1: Normal; 2: Poor; 3: Does Not Function; None: Leave Blank | Aproximate Length Of Distribution Networks In Meters | Presence Of Pump Including Pump Related Electrical Equiptment? 1: Yes; 0: No | Number Of Pumps | Year Pump Was Installed. If Replaced Year Of Most Recent Replacement | Physical State Of The Pump Normal. 1: Normal; 2: Poor; 3: Does Not Function; None: Leave Blank | Presence Of A Pump House/Station? 1: Yes; 0: No | Year The Pump House/Station Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Physical State Of The Pump House/Station. 1: Normal; 2: Poor; 3: Does Not Function; None: Leave Blank | Presence Of Treatment Equipment? 1: Yes; 0: No | Type Of Treatment: (Disinfection/Chlorination, Sedimentation, Filtration) | Year Treatment Equipment Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Physical State Of The Treatment Equipment. 1: Normal; 2: Poor; 3: Does Not Function; None: Leave Blank | Presence Of Treatment Housing Structure? 1: Yes; 0: No | Year Treatment Housing Structure Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Physical State Of The Treatment Housing Structure. 1: Normal; 2: Poor; 3: Does Not Function; None: Leave Blank | E Coli | Residual Chlorine | Bacteria | Turbidity | Calculation E Coli Meets Standards | Calculation Residual Chlorine Meets Standards | Calculation Bacteria Meets Standards | Calculation Turbidity Meets Standards | Does Water System Have Adequate Water Quality? (Bacteria, Turbidity, Other Contaminants Of Concern) 1: Yes; 0: No | Presence Of Public Kiosk Or Tap Stand? 1: Yes; 0: No | Number Of Kiosks Or Tap Stands | Year The Kiosk Was Constructed. If Reconstructed, Year Of Most Recent Reconstruction | Physical State Of The Kiosk/Tap Stand. 1:Normal; 2: Poor; 3:Does Not Function; None: Leave Blank | Out Of Service Or Broken | Number Of Times Broken | Number Of Days Broken | Was The Water Point/ System Out Of Service For One Day Or Less Per Month In The Last Year? 1: Yes; 0: No | Number Of Days The Water Point/System It Was Out Of Service in the Last Year | Is Water Available From The Water Point/System On The Day Of The Visit? 1: Yes; 0: No | Overall State Of The Water Point/System 1: Normal; 2: Poor; 3: Does Not Function; None: Leave Blank
2017 | 27-03-2017 08:35:32 CEST | Rwanda | Rulindo | Kisaro | Kamushenyi | Gakenke |  |  | Gahama Kisaro network | 865 | 10234 | 14 | 731 | 865 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 |  | 1 | 2012 | 2 | 3 | 576000 | 133.1792 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 |  | 2012 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 2 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 15-03-2017 06:11:16 CET | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Gihanga II | 151 |  |  |  | 151 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 15 | 115200 | 152.5828 | 1 | 1 | 1 | 2016 | 1 | 7000 | 1 | 3 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 05:48:51 CET | Rwanda | Rulindo | Cyungo | Rwili | Karambi |  |  | Nyamagana | 60 | 20456 | 36 | 568.2222 | 10 | 50 | 16.67% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 6912 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 7 | 35 | 0 | 245 | 0 | 2
2017 | 28-03-2017 09:37:35 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyagasozi |  |  | Kararama network | 197 | 6572 | 4 | 1643 | 197 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2009 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 389.8477 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 5 | 2012 | 1 | 1 | 14 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 05-04-2017 21:15:59 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Ngarama |  |  | Rutare-Nyirangarama gravity/Nyirangarama water point | 89 | 726 | 1 | 726 | 89 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 1960 | Government Of Rwanda | Spring | 1 | 1 | 0 |  |  |  |  | 20 | 86400 | 194.1573 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1960 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 09-03-2017 20:28:53 CET | Rwanda | Rulindo | Shyorongi | Kijabagwe | Gaseke |  |  | Gisoro- Nyundo network | 176 | 2297 | 10 | 229.7 | 65 | 111 | 36.93% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 13 | 132923.0769 | 408.9941 | 1 | 1 | 1 | 2013 | 1 | 30 | 1 | 6 | 2013 | 2 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 7000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 27-03-2017 15:41:31 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Kararama and Rwamugaza pumping | 965 | 6572 | 1 | 6572 | 965 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only¦Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2003 | 1 | 3.5 | 493714.2857 | 102.3242 | 1 | 1 | 1 | 2003 | 1 | 8000 | 1 | 7 | 2003 | 1 | 1 | 14 |  | 2003 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 18:25:38 CET | Rwanda | Rulindo | Kinihira | Butunzi | Gisekuru |  |  | Miyove- Kinihira | 143 | 10452 | 4 | 2613 | 80 | 63 | 55.94% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 864 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1989 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 04-06-2017 15:38:02 CEST | Rwanda | Rulindo | Mbogo | Bukoro | Gihonga |  |  |  | 20 | 510 | 31 | 16.4516 | 20 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 180 | 2016 | 1 | 180 | 9600 | 96 | 1 | 1 | 1 | 2016 | 1 | 900 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1 | 2016 | 1 | 700 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 06-06-2017 21:36:49 CEST | Rwanda | Rulindo | Base | Rwamahwa | Cyondo |  |  |  | 173 |  |  |  | 150 | 23 | 86.71% | 0 | 0 | 1 | Piped Network With Pump | 2012 | Waterforpeople | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 75 | 23040 | 30.72 | 1 | 0 |  |  |  |  | 0 |  |  |  | 1 | 14 | Pressure Break Tank¦Distribution Chamber¦Washout,Air Release | 2012 | 1 | 1 | 2 | 2012 | 1 | 30000 | 0 | [6 empty] | 0 | [6 empty] | 1 | 1 | Not Present | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 10:49:23 CET | Rwanda | Rulindo | Ngoma | Kabuga | Kirambo |  |  | Nganzo-Kabarore | 131 |  |  |  | 40 | 91 | 30.53% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 20 | 86400 | 432 | 1 | 1 | 1 | 2014 | 2 | 400 | 1 | 3 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 3 | 800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 07-03-2017 15:15:03 CET | Rwanda | Rulindo | Mbogo | Rurenge | Ruhondo |  |  | Kishwi network | 184 | 1309 | 4 | 327.25 | 46 | 138 | 25% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Goverment | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 25 | 69120 | 300.5217 | 1 | 1 | 2 | 2016 | 1 | 700 | 1 | 2 | 2003 | 1 | 0 |  |  |  |  | 1 | 2 | 2003 | 1 | 680 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 19:32:37 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Murambi 2 wpt/Nyirambuga pumping | 174 | 30604 | 1 | 30604 | 174 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 4 | 432000 | 496.5517 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 06-03-2017 10:23:00 CET | Rwanda | Rulindo | Cyungo | Marembo | Murambo |  |  |  | 586 |  |  |  | 541 | 45 | 92.32% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2012 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2012 | 1 | 2 | 864000 | 319.4085 | 1 | 0 |  |  |  |  | 1 | 5 | 2012 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 1234 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 10 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 06:55:45 CEST | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point at Refectory APEKI Tumba/Nyirambuga pumping | 115 | 30604 | 1 | 30604 | 115 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 601.0435 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 100 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 6 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 07:51:59 CET | Rwanda | Rulindo | Murambi | Gatwa | Akarambi |  |  | Mutagata Motorised Network | 206 | 26296 | 49 | 536.6531 | 100 | 106 | 48.54% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 4 | 2007 | 1 | 5 | 345600 | 691.2 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | Yes | 3 | 30 | 0 | 90 | 0 | 1
2017 | 23-03-2017 18:57:48 CET | Rwanda | Rulindo | Masoro | Kabuga | Rubaya |  |  | Mutagata motorised network | 167 | 26296 | 49 | 536.6531 | 167 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 413.8922 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 1900 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 17-03-2017 05:26:28 CET | Rwanda | Rulindo | Mbogo | Rurenge | Gitaba |  |  | Musenge network | 195 | 6074 | 29 | 209.4483 | 95 | 100 | 48.72% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 819.3457 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Washout And Air Release | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2016 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 18:11:30 CET | Rwanda | Rulindo | Ngoma | Karambo | Jyambere |  |  | Gahama network | 117 |  |  |  | 65 | 52 | 55.56% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 15 | 115200 | 354.4615 | 1 | 1 | 1 | 2014 | 1 | 1800 | 1 | 2 | 2014 | 1 | 1 | 1 | Distribution Chamber | 2014 | 1 | 1 | 1 | 2014 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 17-03-2017 05:21:09 CET | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 135 | 6074 | 29 | 209.4483 | 68 | 67 | 50.37% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1144.6741 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Washout And Air Release Chamber | 2014 | 1 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 18-04-2017 20:12:24 CEST | Rwanda | Rulindo | Tumba | Taba | Kamuragi |  |  | Water point chez Safari/Nyirambuga pumping system | 154 | 30604 | 1 | 30604 | 154 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 448.8312 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 12-03-2017 10:59:20 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Karama |  |  | Bitete-Muvumu | 121 | 1316 | 7 | 188 | 35 | 86 | 28.93% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 897.6623 | 1 | 1 | 1 | 2013 | 2 | 1000 | 1 | 4 | 2013 | 1 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 2 | 1 | 1 | 2013 | 1 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-04-2017 14:40:46 CEST | Rwanda | Gicumbi | Mutete | Nyarubuye | Rugarama |  |  | rukondo | 162 |  |  |  | 140 | 22 | 86.42% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2012 | G. Thierry | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2012 | 1 | 30 | 57600 | 82.2857 | 1 | 1 | 1 | 2012 | 1 | 4500 | 1 | 4 | 2012 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 16:59:14 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Rweya |  |  | kirikumuryango network | 212 |  |  |  | 110 | 102 | 51.89% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 285.6198 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 12:07:50 CET | Rwanda | Rulindo | Masoro | Shengampuri | Mutagata |  |  |  | 124 | 6740 | 31 | 217.4194 | 124 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 15 | 2016 | 1 | 20 | 86400 | 139.3548 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 17:26:20 CET | Rwanda | Rulindo | Buyoga | Gahororo | Bunyana |  |  | Ndarage | 108 |  |  |  | 100 | 8 | 92.59% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring¦Groundwater (Well, Etc.) | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 30 | 57600 | 115.2 | 1 | 1 | 1 | 2014 | 1 | 6700 | 1 | 5 | 2014 | 1 | 0 |  |  |  |  | 1 | 1 | 2014 | 1 | 6700 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 17:37:34 CET | Rwanda | Rulindo | Bushoki | Kayenzi | Rebero |  |  | Water point at Rebero/Matonyanga gravity | 175 |  |  |  | 175 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 49.3714 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 06:34:10 CET | Rwanda | Rulindo | Burega | Taba | Nyagisozi |  |  | Rwamugaza | 520 | 14106 | 38 | 371.2105 | 520 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 147.6923 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 09:06:09 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kanyoni |  |  | charity water 203.032 | 640 | 6572 | 1 | 6572 | 640 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 1 | 2016 | 1 | 3 | 576000 | 180 | 1 | 1 | 1 | 2016 | 1 | 2000 | 1 | 2 | 2016 | 1 | 1 | 2 |  | 2016 | 1 | 1 | 1 | 2016 | 1 | 500 | 1 | 3 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 19:52:15 CET | Rwanda | Rulindo | Bushoki | Kayenzi | Rwanzu |  |  | Rwanzu wpt behind TCT/Nyirambuga pumping | 154 | 30604 | 1 | 30604 | 154 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Gor | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 561.039 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 3 | No | 0 | 0 | 1 | 0 | 1 | 3
2017 | 14-03-2017 22:30:53 CET | Rwanda | Rulindo | Rusiga | Kirenge | Kinini |  |  | BF at GS Rukingu/Gashinge gravity | 250 |  |  |  | 250 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 60 | 28800 | 23.04 | 1 | 0 |  |  |  |  | 1 | 1 | 2013 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 21:03:33 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 165 | 6436 | 26 | 247.5385 | 80 | 85 | 48.48% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 2 | 10 | 172800 | 432 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 02-06-2017 06:57:43 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Bikamba |  |  | Rwamugaza | 205 | 14106 | 38 | 371.2105 | 20 | 185 | 9.756% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Goverment | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2003 | 1 | 3 | 576000 | 5760 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 | Sedimentation Tank¦Pressure Break Tank¦Distribution Chamber | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 15:24:12 CET | Rwanda | Rulindo | Bushoki | Gasiza | Karambi |  |  | Karambi water point/Tare-Rusiga pumping | 164 | 9577 | 1 | 9577 | 164 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 10 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 52.6829 | 1 | 1 | 1 | 2015 | 1 | 4000 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 3 | 2015 | 1 | 8000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-03-2017 19:03:50 CET | Rwanda | Rulindo | Kinihira | Butunzi | Akamiyove |  |  | Nyamagana-Kinihira | 132 |  |  |  | 60 | 72 | 45.45% | 0 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1152 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 07:47:23 CET | Rwanda | Rulindo | Murambi | Gatwa | Akarambi |  |  | Mutagata Motorised Network | 206 | 26296 | 49 | 536.6531 | 106 | 100 | 51.46% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 652.0755 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 3 | Yes | 3 | 30 | 0 | 90 | 0 | 3
2017 | 27-03-2017 15:27:54 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Kararama network | 965 | 6572 | 4 | 1643 | 965 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2009 | Government | Spring | 3 | 1 | 1 |  | 1 | 2009 | 1 | 4.5 | 384000 | 79.5855 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 14 | 2009 | 1 | 1 | 23 |  | 2009 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 10:29:09 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza network | 229 | 14106 | 35 | 403.0286 | 229 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 503.0568 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-04-2017 14:42:23 CEST | Rwanda | Rulindo | Buyoga | Mwumba | Nyamwiza |  |  | kiruruma | 149 | 8295 | 25 | 331.8 | 120 | 29 | 80.54% | 0 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 960 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 11 | 2014 | 1 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 9000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 15-03-2017 14:28:53 CET | Rwanda | Rulindo | Cyinzuzi | Migendezo | Marembo |  |  | 0 | 735 | 14106 | 15 | 940.4 | 735 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2009 | Umushinga Witwa Ema | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2009 | 1 | 4.5 | 384000 | 104.4898 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 16 | 2009 | 1 | 1 | 23 |  | 2009 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2009 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 07:35:42 CET | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 229 | 1458 | 6 | 243 | 200 | 29 | 87.34% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2005 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | Start Chamber | 1 | 2005 | 1 | 75 | 23040 | 23.04 | 1 | 1 | 1 | 2016 | 1 | 2000 | 1 | 1 | 2005 | 1 | 1 | 2 | Break Pressure | 2016 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-04-2017 23:11:06 CEST | Rwanda | Rulindo | Burega | Karengeli | Bugoboka |  |  | Rwamugaza network | 80 | 14106 | 35 | 403.0286 | 80 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 1440 | 1 | 1 | 1 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 14 |  | 2003 | 1 | 1 | 1 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 11-03-2017 20:03:44 CET | Rwanda | Rulindo | Base | Rwamahwa | Cyondo |  |  | Ruramba | 173 | 1564 | 4 | 391 | 150 | 23 | 86.71% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 60 | 28800 | 38.4 | 1 | 1 | 1 | 2016 | 3 | 4500 | 1 | 2 | 2016 | 1 | 1 | 2 | Pressure Break Tank | 2016 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 24-03-2017 11:50:03 CET | Rwanda | Rulindo | Masoro | Nyamyumba | Kabuga |  |  |  | 119 | 5544 | 31 | 178.8387 | 119 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 145.2101 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 04:57:00 CET | Rwanda | Rulindo | Murambi | Mugambazi | Nyarurembo |  |  | Mutagata motorised network | 144 | 26296 | 49 | 536.6531 | 48 | 96 | 33.33% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1440 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 16:59:08 CET | Rwanda | Rulindo | Burega | Butangampundu | Gacyamo |  |  | Rwamugaza | 550 | 14106 | 38 | 371.2105 | 550 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 139.6364 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 23 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 09:26:51 CEST | Rwanda | Rulindo | Kisaro | Kamushenyi | Karambi |  |  | Gahama Kisaro network | 184 | 10234 | 14 | 731 | 184 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 |  | 1 | 2012 | 1 | 3 | 576000 | 626.087 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 |  | 2012 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 2 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 02-01-2015 12:56:53 CET | Rwanda | Rulindo | Buyoga | Karama | Cyasenga |  |  | Water point near GS Kadendegere/Nyirambuga pumping | 165 | 30604 | 1 | 30604 | 165 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 523.6364 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 21:13:37 CET | Rwanda | Rulindo | Shyorongi | Rubona | Gishyita |  |  | Bitete-Rwahi network | 205 | 1316 | 15 | 87.7333 | 60 | 145 | 29.27% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 480 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-06-2017 06:47:34 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza | 229 | 14106 | 38 | 371.2105 | 10 | 219 | 4.367% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Goverment | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2003 | 1 | 3 | 576000 | 11520 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 12 | 2003 | 1 | 1 | 12 | Distribution Chamber | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-04-2017 22:38:22 CEST | Rwanda | Rulindo | Buyoga | Busoro | Rugarama |  |  | Water point at EP Busoro/Nyirambuga pumping system | 189 | 30604 | 1 | 30604 | 189 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 457.1429 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 17:17:56 CET | Rwanda | Rulindo | Bushoki | Kayenzi | Muduha |  |  | Muduha water point/Matonyanga gravity | 160 |  |  |  | 160 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 54 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 08-03-2017 21:14:49 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 165 | 6436 | 26 | 247.5385 | 32 | 133 | 19.39% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 1080 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 14-04-2017 22:14:15 CEST | Rwanda | Rulindo | Bushoki | Gasiza | Gitwa |  |  | Gitwa water point/Nkombe gravity system | 134 |  |  |  | 134 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Coforwa | Spring | 1 | 1 | 0 |  |  |  |  | 1.02 | 1694117.6471 | 2528.5338 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2002 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 15:18:26 CET | Rwanda | Rulindo | Mbogo | Bukoro | Kibaya |  |  | Mutungo | 133 | 510 | 3 | 170 | 73 | 60 | 54.89% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 1 | 0 | 0 |  |  |  |  | 24 | 72000 | 197.2603 | 1 | 1 | 1 | 2004 | 2 | 500 | 1 | 2 | 2004 | 2 | 0 |  |  |  |  | 1 | 1 | 2004 | 2 | 2000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2004 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 25-04-2017 17:01:39 CEST | Rwanda | Rulindo | Kisaro | Murama | Kibingwe |  |  |  | 122 |  |  |  | 122 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 1 | 1 | 1 |  | 1 | 2003 | 1 | 120 | 14400 | 23.6066 | 1 | 1 | 2 | 2003 | 1 | 30000 | 1 | 7 | 2003 | 1 | 1 | 14 |  | 2003 | 1 | 1 | 1 | 2003 | 1 | 30000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 3 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 20-03-2017 11:01:49 CET | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 27 | 5544 | 14 | 396 | 27 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 45 | 38400 | 284.4444 | 1 | 1 | 1 | 2016 | 1 | 500 | 1 | 2 | 2016 | 1 | 1 |  | Distribution Chamber | 2016 | 1 | 1 | 1 | 2016 | 1 | 500 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 05:35:51 CET | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 325 | 26296 | 49 | 536.6531 | 63 | 262 | 19.38% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1097.1429 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 10:12:55 CET | Rwanda | Rulindo | Bushoki | N.Ngarama | Byimana |  |  | Byimana water point/Tare-Rusiga pumping | 92 | 9577 | 1 | 9577 | 92 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 10 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 93.913 | 1 | 1 | 1 | 2015 | 1 | 4000 | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 24-03-2017 12:18:04 CET | Rwanda | Rulindo | Masoro | Shengampuri | Agasharu |  |  |  | 130 | 6740 | 31 | 217.4194 | 130 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 132.9231 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 05-04-2017 22:00:55 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Ngarama |  |  | Water point at Nyirangarama cell/Rutare-Nyirangarama gravity | 109 | 726 | 1 | 726 | 109 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Local Government In Ubudehe Program | Spring | 1 | 1 | 0 |  |  |  |  | 20 | 86400 | 158.5321 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:50:37 CET | Rwanda | Rulindo | Mbogo | Bukoro | Ruhanya |  |  | Musenge Network | 102 | 6074 | 29 | 209.4483 | 52 | 50 | 50.98% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Wfp | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1496.8815 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber¦Washout And Air Release | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 3 | Yes | 8 | 30 | 0 | 240 | 0 | 3
2017 | 15-03-2017 20:04:25 CET | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Marembo center water point/Nyirambuga pumping | 134 | 30604 | 1 | 30604 | 134 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Gor | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 644.7761 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 14:21:35 CET | Rwanda | Rulindo | Cyinzuzi | Migendezo | Nyamugali |  |  |  | 111 | 14106 | 31 | 455.0323 | 111 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2009 | Umushinga Witwa Ema | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2009 | 2 | 4.5 | 384000 | 691.8919 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 16 | 2009 | 1 | 1 | 23 | Vantouse, Vidange | 2009 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2009 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 19:29:38 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Gisiza |  |  | kinywamagana pumping network | 212 | 6436 | 26 | 247.5385 | 105 | 107 | 49.53% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 329.1429 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 13-03-2017 08:55:01 CET | Rwanda | Rulindo | Bushoki | N.Ngarama | Terambere |  |  | Terambere water point/Nyabishengeshi water gravity system | 79 | 893 | 1 | 893 | 79 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 2 | 1 | 0 |  |  |  |  | 50 | 34560 | 87.4937 | 1 | 1 | 1 | 2013 | 1 | 100 | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 11-03-2017 09:03:16 CET | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 50 | 20456 | 36 | 568.2222 | 45 | 5 | 90% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1536 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 2 | Yes | 12 | 30 | 0 | 360 | 0 | 2
2017 | 23-03-2017 18:05:37 CET | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 214 | 5544 | 14 | 396 | 214 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1986 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 80.7477 | 1 | 1 | 1 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 11-03-2017 20:03:31 CET | Rwanda | Rulindo | Base | Rwamahwa | Cyondo |  |  | Ruramba | 173 | 1564 | 4 | 391 | 150 | 23 | 86.71% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2017 | 1 | 60 | 28800 | 38.4 | 1 | 1 | 1 | 2016 | 3 | 4500 | 1 | 2 | 2016 | 1 | 1 | 2 | Sedimentation Tank | 2016 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 09-03-2017 22:32:54 CET | Rwanda | Rulindo | Shyorongi | Rubona | Ngona |  |  | Bitete-Rwahi network | 122 | 1316 | 15 | 87.7333 | 28 | 94 | 22.95% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 1028.5714 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 05:51:45 CET | Rwanda | Rulindo | Cyungo | Burehe | Nyagatovu |  |  | Nyamagana | 100 | 20456 | 36 | 568.2222 | 70 | 30 | 70% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2011 | 1 | 5 | 345600 | 987.4286 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 10 | 28 | 0 | 280 | 0 | 2
2017 | 24-03-2017 15:50:15 CET | Rwanda | Rulindo | Buyoga | Butare | Ryanyirakayobe |  |  | Nyagahera | 96 |  |  |  | 80 | 16 | 83.33% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 2 | 16 | 108000 | 270 | 1 | 1 | 2 | 2014 | 2 | 6800 | 1 | 3 | 2014 | 1 | 1 | 3 | Distribution Chamber | 2014 | 1 | 1 | 1 | 2014 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 23-03-2017 11:49:25 CET | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | Mutagata Gravity Network | 214 | 26296 | 12 | 2191.3333 | 52 | 162 | 24.3% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2004 | 2 | 8 | 216000 | 830.7692 | 1 | 1 | 1 | 2004 | 2 | 3500 | 1 | 6 | 2004 | 2 | 1 | 4 | Distribution Chamber¦Washout And Air Release Chamber | 2004 | 2 | 1 | 2 | 2004 | 2 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 12 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 11:39:08 CET | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 325 | 26296 | 49 | 536.6531 | 65 | 260 | 20% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1063.3846 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 06:55:52 CET | Rwanda | Rulindo | Base | Rwamahwa | Mutima |  |  | Rutare I | 229 | 345 | 5 | 69 | 200 | 29 | 87.34% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 75 | 23040 | 23.04 | 1 | 0 |  |  |  |  | 1 | 1 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 21:41:44 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 354 | 6436 | 26 | 247.5385 | 150 | 204 | 42.37% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 230.4 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 07:00:53 CET | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 495 | 14106 | 38 | 371.2105 | 495 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 155.1515 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2006 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 08-03-2017 18:53:06 CET | Rwanda | Rulindo | Base | Rwamahwa | Mutima |  |  | Rutare I | 169 | 345 | 5 | 69 | 140 | 29 | 82.84% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 20 | 86400 | 123.4286 | 1 | 1 | 1 | 2016 | 1 | 3800 | 1 | 2 | 2016 | 1 | 0 |  |  |  |  | 1 | 1 | 2016 | 1 | 3800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 2 | Yes | 3 | 8 | 0 | 24 | 1 | 2
2017 | 15-03-2017 06:06:22 CET | Rwanda | Rulindo | Base | Rwamahwa | Kiruli |  |  | Migogo | 223 | 558 | 10 | 55.8 | 200 | 23 | 89.69% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2009 | Padiri(Lake Angels). | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2009 | 2 | 50 | 34560 | 34.56 | 1 | 1 | 1 | 2009 | 2 | 6800 | 1 | 3 | 2009 | 2 | 0 |  |  |  |  | 1 | 1 | 2009 | 2 | 6800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2009 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 24-03-2017 11:44:04 CET | Rwanda | Rulindo | Masoro | Shengampuri | Mutagata |  |  |  | 124 | 6740 | 31 | 217.4194 | 124 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 1998 |  | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 139.3548 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:51:01 CET | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Musenge Network | 118 | 6074 | 29 | 209.4483 | 27 | 91 | 22.88% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Wfp | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 2882.8829 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber¦Washout And Air Release | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 3 | Yes | 8 | 30 | 0 | 240 | 0 | 3
2017 | 09-03-2017 22:47:43 CET | Rwanda | Rulindo | Shyorongi | Rubona | Rwahi |  |  | Bitete-Rwahi network | 161 | 1316 | 15 | 87.7333 | 25 | 136 | 15.53% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 1152 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 14:12:35 CET | Rwanda | Rulindo | Kinihira | Karegamazi | Mutoyi |  |  | Miyove-Kinihira | 119 | 10452 | 19 | 550.1053 | 65 | 54 | 54.62% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 1063.3846 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 23-03-2017 06:26:37 CET | Rwanda | Rulindo | Buyoga | Gitumba | Remera |  |  | Kiruruma | 130 | 8295 | 25 | 331.8 | 125 | 5 | 96.15% | 1 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 921.6 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 15 | 2014 | 1 | 1 | 5 | Pressure Break Tank | 2014 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 22:22:02 CET | Rwanda | Rulindo | Shyorongi | Rubona | Nyarunyinya |  |  | Bitete-Rwahi network | 132 | 1316 | 15 | 87.7333 | 40 | 92 | 30.3% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 720 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 14-03-2017 22:00:37 CET | Rwanda | Rulindo | Tumba | Taba | Nyirambuga |  |  | Nyirambuga pumping station2/Nyirambuga source | 128 | 30604 | 1 | 30604 | 128 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Gor | Spring | 8 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2012 | 1 | 4 | 432000 | 675 | 1 | 1 | 1 | 2012 | 1 | 50 | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 4000 | 1 | 2 | 2012 | 1 | 1 | 2012 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 07:27:19 CET | Rwanda | Rulindo | Burega | Karengeli | Kanunga |  |  | Rwamugaza | 275 | 14106 | 38 | 371.2105 | 275 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 2 | 2003 | 1 | 3.5 | 493714.2857 | 359.0649 | 1 | 1 | 1 | 2003 | 1 | 8000 | 1 | 20 | 2003 | 1 | 1 | 16 |  | 2003 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 23-03-2017 16:48:28 CET | Rwanda | Rulindo | Murambi | Bubangu | Karwa |  |  | rwiseke | 215 | 9536 | 5 | 1907.2 | 215 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2001 | 1 | 14 | 123428.5714 | 114.8173 | 1 | 1 | 1 | 2001 | 1 | 12000 | 1 | 7 | 2001 | 1 | 0 |  |  |  |  | 1 | 1 | 2001 | 1 | 12000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2001 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-04-2017 14:43:55 CEST | Rwanda | Rulindo | Buyoga | Gahororo | Gatare |  |  | Kiruruma | 175 | 8295 | 25 | 331.8 | 100 | 75 | 57.14% | 0 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 1152 | 1 | 1 | 1 | 2014 | 3 | 9000 | 0 |  |  |  | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 09-03-2017 22:39:44 CET | Rwanda | Rulindo | Shyorongi | Rubona | Rwahi |  |  | Bitete-Rwahi network | 161 | 1316 | 15 | 87.7333 | 40 | 121 | 24.84% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 720 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 22:19:44 CET | Rwanda | Rulindo | Bushoki | Giko | Karambo |  |  | Karambo water point/Buramira gravity | 104 | 1255 | 1 | 1255 | 104 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Gor | Spring | 2 | 1 | 0 |  |  |  |  | 30 | 57600 | 110.7692 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 06:23:31 CET | Rwanda | Rulindo | Burega | Taba | Lyinzovu |  |  | Rwamugaza | 505 | 14106 | 38 | 371.2105 | 505 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 152.0792 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 23-04-2017 14:41:30 CEST | Rwanda | Rulindo | Buyoga | Mwumba | Nyarubuye |  |  | kiruruma | 173 | 8295 | 25 | 331.8 | 120 | 53 | 69.36% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2014 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 960 | 1 | 1 | 1 | 2014 | 1 | 6700 | 1 | 11 | 2014 | 1 | 0 |  |  |  |  | 1 | 3 | 2016 | 1 | 6700 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 12-03-2017 12:52:28 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Mukumba |  |  | Muvumu- Taba | 92 |  |  |  | 20 | 72 | 21.74% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 25 | 69120 | 691.2 | 1 | 1 | 1 | 2013 | 1 | 800 | 1 | 3 | 2013 | 2 | 1 | 9 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 7500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | Yes | 1 | 3 | 0 | 3 | 1 | 2
2017 | 04-06-2017 13:22:46 CEST | Rwanda | Rulindo | Kisaro | Gitatsa | Ruberano |  |  | gahama | 132 | 10234 | 11 | 930.3636 | 100 | 32 | 75.76% | 0 | 0 | 1 | Piped Network With Pump | 2017 |  | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 65 | 26584.6154 | 53.1692 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 | Pressure Break Tank¦Distribution Chamber¦Washout, Air Release | 2012 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 21:22:06 CET | Rwanda | Rulindo | Shyorongi | Rubona | Gishyita |  |  | Bitete-Rwahi network | 205 | 1316 | 15 | 87.7333 | 120 | 85 | 58.54% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 240 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 12:12:53 CET | Rwanda | Rulindo | Murambi | Mvuzo | Kabuga |  |  | Gakoma network | 199 | 7108 | 2 | 3554 | 101 | 98 | 50.75% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 2 | 1 | 0 |  |  |  |  | 9 | 192000 | 380.198 | 1 | 0 |  |  |  |  | 1 | 2 | 2004 | 1 | 0 |  |  |  |  | 1 | 1 | 2004 | 2 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2004 | 3 | Yes | 6 | 30 | 0 | 180 | 0 | 3
2017 | 18-04-2017 06:48:14 CEST | Rwanda | Rulindo | Tumba | Gahabwa | Rushaki |  |  | Rushaki water point at Habimana/Nyirambuga pumping system | 152 | 30604 | 1 | 30604 | 152 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 454.7368 | 1 | 1 | 1 | 2017 | 1 | 2017 | 1 | 1 | 2017 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 12:02:41 CET | Rwanda | Rulindo | Cyungo | Marembo | Nganzo |  |  | Mugomero Murambo | 150 | 3456 | 3 | 1152 | 132 | 18 | 88% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 120 | 14400 | 21.8182 | 1 | 1 | 2 | 2015 | 1 | 10000 | 1 | 10 | 2015 | 1 | 1 | 3 | Distribution Chamber | 2015 | 1 | 1 | 2 | 2015 | 1 | 10000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 08:16:55 CET | Rwanda | Rulindo | Murambi | Mugambazi | Kigarama |  |  | Mutagata motorised network | 169 | 26296 | 49 | 536.6531 | 65 | 104 | 38.46% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1063.3846 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 18:37:57 CET | Rwanda | Rulindo | Masoro | Kabuga | Kanunga |  |  | Mutagata motorised network | 143 | 26296 | 49 | 536.6531 | 75 | 68 | 52.45% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 921.6 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 10:07:32 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Kirurumo |  |  | Bitete-Muvumu | 80 | 1316 | 7 | 188 | 5 | 75 | 6.25% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 6283.6364 | 1 | 1 | 1 | 2013 | 2 | 1000 | 1 | 4 | 2013 | 1 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 14:11:28 CET | Rwanda | Rulindo | Rukozo | Buraro | Kamiyove |  |  | Kabonanyoni | 40 | 7894 | 30 | 263.1333 | 30 | 10 | 75% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 768 | 1 | 1 | 3 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 23:48:15 CET | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point at Gisha center/Nyirambuga pumping | 133 | 30604 | 1 | 30604 | 133 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Gor | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 649.6241 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 04-06-2017 15:53:09 CEST | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 135 | 6074 | 29 | 209.4483 | 31 | 104 | 22.96% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Water For People, Wasac And Rulindo District | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 2510.898 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Washout, Air Release Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 11:20:02 CEST | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point chez Hategekimana/Nyirambuga pumping | 169 | 30604 | 1 | 30604 | 169 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 408.9941 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 07:54:08 CET | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutembe | 229 | 1012 | 7 | 144.5714 | 200 | 29 | 87.34% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 75 | 23040 | 23.04 | 1 | 1 | 1 | 2016 | 1 | 2700 | 1 | 2 | 2016 | 1 | 0 |  |  |  |  | 1 | 1 | 2016 | 1 | 2700 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 16-03-2017 08:47:40 CET | Rwanda | Rulindo | Mbogo | Bukro | Buhira |  |  | Musenge Network | 100 | 6074 | 29 | 209.4483 | 48 | 52 | 48% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1621.6216 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber¦Washout And Air Release | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 03-01-2015 04:54:05 CET | Rwanda | Rulindo | Rukozo | Mberuka | Mataba |  |  | Kabonanyoni | 70 | 7894 | 30 | 263.1333 | 65 | 5 | 92.86% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 354.4615 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 19:32:33 CET | Rwanda | Rulindo | Shyorongi | Rubona | Nyarusange |  |  | Gisoro- Nyundo network | 97 | 2297 | 10 | 229.7 | 55 | 42 | 56.7% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 13 | 132923.0769 | 483.3566 | 1 | 1 | 1 | 2013 | 1 | 30 | 1 | 6 | 2013 | 2 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 7000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 17-03-2017 05:21:46 CET | Rwanda | Rulindo | Ngoma | Kabuga | Kiruli |  |  | Musenge network | 139 | 6074 | 29 | 209.4483 | 139 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 559.9844 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Washout And Air Release Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 02-01-2015 05:51:02 CET | Rwanda | Rulindo | Cyungo | Burehe | Sove |  |  | Nyamagana | 80 | 20456 | 36 | 568.2222 | 50 | 30 | 62.5% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | Well | 1 | 2015 | 1 | 5 | 345600 | 1382.4 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 10 | 35 | 0 | 350 | 1 | 2
2017 | 28-03-2017 10:11:47 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Cyamutara |  |  | Rwamugaza network | 243 | 14106 | 35 | 403.0286 | 243 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 1 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 474.0741 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 08:19:15 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Kivubwe |  |  | Rwamugaza network | 173 | 14106 | 35 | 403.0286 | 173 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 665.896 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 10:18:45 CET | Rwanda | Rulindo | Ngoma | Karambo | Kagwa |  |  | Kabarore- Ngoma- Nyabuko network | 123 | 8284 | 3 | 2761.3333 | 41 | 82 | 33.33% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 2 | 4 | 432000 | 2107.3171 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 13 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-04-2017 23:05:46 CEST | Rwanda | Rulindo | Buyoga | Karama | Kajeneni |  |  | Karambo center water point/Nyirambuga pumping | 175 | 30604 | 1 | 30604 | 175 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 493.7143 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:29:07 CET | Rwanda | Rulindo | Murambi | Mvuzo | Ntyaba |  |  | 0 | 680 |  |  |  | 680 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 1 | 2016 | 1 | 3 | 576000 | 169.4118 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 6 | 2016 | 1 | 1 | 30 |  | 2016 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 3 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 10:51:29 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyarurama |  |  | Rwamugaza network | 168 | 14106 | 35 | 403.0286 | 168 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 685.7143 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 03-01-2015 04:52:13 CET | Rwanda | Rulindo | Rukozo | Mberuka | Kabera |  |  | Kabonanyoni | 138 | 7894 | 30 | 263.1333 | 130 | 8 | 94.2% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 177.2308 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 2 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 09:39:01 CET | Rwanda | Rulindo | Masoro | Nyamyumba | Rusenyi |  |  | marenge | 156 | 5544 | 14 | 396 | 156 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 110.7692 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 14:46:59 CEST | Rwanda | Rulindo | Mbogo | Mushali | Bukongi |  |  | Gitabage network | 168 |  |  |  | 72 | 96 | 42.86% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2008 | Catholic Church | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2008 | 1 | 40 | 43200 | 120 | 1 | 1 | 1 | 2008 | 1 | 700 | 1 | 2 | 2008 | 1 | 0 |  |  |  |  | 1 | 1 | 2008 | 1 | 500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2008 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-03-2017 14:33:40 CET | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point/AEP Kigarama gravity | 243 | 2621 | 3 | 873.6667 | 243 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 35.5556 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:18:40 CET | Rwanda | Rulindo | Murambi | Mugambazi | Ruri |  |  | 0 | 945 | 26296 | 15 | 1753.0667 | 945 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | Collection Chamber | 1 | 2016 | 1 | 3 | 576000 | 121.9048 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 45 | 2016 | 1 | 1 | 38 |  | 2016 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 3 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 10:00:03 CEST | Rwanda | Rulindo | Kisaro | Mubuga | Rutabo |  |  | Gahama Kisaro network | 148 | 10234 | 14 | 731 | 148 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 |  | 1 | 2012 | 1 | 3 | 576000 | 778.3784 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 |  | 2012 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 2 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 13-03-2017 06:51:28 CET | Rwanda | Rulindo | Ngoma | Munyarwanda | Ngaru |  |  | Kabarore-Ngoma-Nyabuko network | 106 | 8284 | 14 | 591.7143 | 50 | 56 | 47.17% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 1 | 4 | 432000 | 1728 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 4 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 2 | Yes | 1 | 10 | 0 | 10 | 1 | 1
2017 | 10-03-2017 14:27:37 CET | Rwanda | Rulindo | Bushoki | Gasiza | Gitwa |  |  | Water point at Gasiza Health Post/Tare-Rusiga pumping | 134 | 9577 | 1 | 9577 | 134 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 10 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 64.4776 | 1 | 1 | 1 | 2015 | 1 | 4000 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 3 | 2015 | 1 | 8000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 10:21:40 CET | Rwanda | Rulindo | Bushoki | Gasiza | Buhande |  |  | Water point from Rutare gravity on Tare-Rusiga pumping system | 129 | 9577 | 1 | 9577 | 129 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Government In Partnership With Water For People | Spring | 8 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 66.9767 | 1 | 1 | 2 | 2015 | 1 | 2000 | 1 | 4 | 2015 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 2000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 16-03-2017 06:14:05 CET | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 495 | 14106 | 38 | 371.2105 | 495 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 155.1515 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 16 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 10-03-2017 04:19:58 CET | Rwanda | Rulindo | Ngoma | Karambo | Butare |  |  | Shishi network | 122 |  |  |  | 40 | 82 | 32.79% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 28 | 61714.2857 | 308.5714 | 1 | 1 | 1 | 2014 | 1 | 700 | 1 | 2 | 2014 | 1 | 0 |  |  |  |  | 1 | 1 | 2014 | 1 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2014 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 10-03-2017 09:59:09 CET | Rwanda | Rulindo | Bushoki | N.Ngarama | Byimana |  |  | Water Point at College Foundation Sina Gerard/Tare-Rusiga pumping | 92 | 9577 | 1 | 9577 | 92 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 8 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 93.913 | 1 | 1 | 1 | 2015 | 1 | 4000 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 3 | 2015 | 1 | 8000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 04:48:57 CET | Rwanda | Rulindo | Masoro | Kivugiza | Rebero |  |  | Mutagata motorised network | 376 | 26296 | 49 | 536.6531 | 123 | 253 | 32.71% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 561.9512 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 16:09:15 CET | Rwanda | Rulindo | Murambi | Gatwa | Kigarama |  |  |  | 209 |  |  |  | 209 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2001 |  | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2001 | 1 | 14 | 123428.5714 | 118.1135 | 1 | 1 | 1 | 2001 | 1 | 12000 | 1 | 7 | 2001 | 1 | 0 |  |  |  |  | 1 | 1 | 2001 | 1 | 12000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-04-2017 14:44:16 CEST | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  |  | 151 |  |  |  | 100 | 51 | 66.23% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 1152 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 11 | 2014 | 2 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 20:50:27 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 165 | 6436 | 26 | 247.5385 | 40 | 125 | 24.24% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 864 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 23-03-2017 15:15:51 CET | Rwanda | Rulindo | Murambi | Bubangu | Taba |  |  | rwiseke | 193 | 9536 | 5 | 1907.2 | 193 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2001 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2001 | 1 | 14 | 123428.5714 | 127.9053 | 1 | 1 | 1 | 2001 | 1 | 1200 | 1 | 7 | 2001 | 1 | 0 |  |  |  |  | 1 | 1 | 2001 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2001 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 06:11:26 CET | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Gihanga II | 151 |  |  |  | 151 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2016 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 15 | 115200 | 152.5828 | 1 | 1 | 1 | 2016 | 1 | 7000 | 1 | 3 | 2016 | 1 | 0 |  |  |  |  | 1 | 1 | 2016 | 1 | 7000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 11-03-2017 20:02:59 CET | Rwanda | Rulindo | Base | Rwamahwa | Cyondo |  |  | Ruramba | 173 | 1564 | 4 | 391 | 150 | 23 | 86.71% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 60 | 28800 | 38.4 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 1 | 2 | Pressure Break Tank | 2016 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 09-03-2017 20:47:03 CET | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Gisoro- Nyundo network | 188 | 2297 | 10 | 229.7 | 80 | 108 | 42.55% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 13 | 132923.0769 | 332.3077 | 1 | 1 | 1 | 2013 | 1 | 13 | 1 | 6 | 2013 | 2 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 7000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 10:29:49 CET | Rwanda | Rulindo | Murambi | Bubangu | Gashubi |  |  | Mutagata Motorised Network | 140 | 26296 | 49 | 536.6531 | 35 | 105 | 25% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1974.8571 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 13-03-2017 21:36:18 CET | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Kigamba water point/Rutomvu gravity | 172 | 3015 | 1 | 3015 | 172 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 50.2326 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 25-04-2017 00:23:58 CEST | Rwanda | Rulindo | Ntarabana | Mahaza | Karera |  |  | Rwamugaza network | 182 | 14106 | 35 | 403.0286 | 182 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 632.967 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 14 |  | 2003 | 1 | 1 | 1 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 18:25:12 CET | Rwanda | Rulindo | Base | Rwamahwa | Mutima |  |  | Rutare I | 169 | 345 | 5 | 69 | 140 | 29 | 82.84% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 2 | 20 | 86400 | 123.4286 | 1 | 1 | 1 | 2017 | 1 | 3800 | 1 | 2 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 04:49:24 CET | Rwanda | Rulindo | Rukozo | Mbuye | Ruhanga |  |  | Kabonanyoni | 150 | 7894 | 30 | 263.1333 | 145 | 5 | 96.67% | 1 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 158.8966 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 2015 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 14-03-2017 23:06:49 CET | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Kingazi4 wpt/Nyakabizi1&2 | 157 | 1259 | 1 | 1259 | 157 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 20 | 86400 | 110.0637 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 23-04-2017 14:42:31 CEST | Rwanda | Rulindo | Buyoga | Gitumba | Rutabo |  |  | kiruruma | 128 | 8295 | 25 | 331.8 | 80 | 48 | 62.5% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 1440 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 11 | 2014 | 1 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 9000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 12:37:33 CET | Rwanda | Rulindo | Bushoki | Mukoto | Marembo |  |  | Marembo water point/Tare-Rusiga pumping | 90 | 9577 | 1 | 9577 | 90 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 8 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 96 | 1 | 1 | 1 | 2015 | 1 | 4000 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 8000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 10:42:17 CET | Rwanda | Rulindo | Murambi | Bubangu | Mayange |  |  | Mutagata Motorised Network | 198 | 26296 | 49 | 536.6531 | 160 | 38 | 80.81% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 432 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release Chamber | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 19:10:33 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Gatsinde |  |  | Kiringo wpt/Nyirambuga pumping | 178 | 30604 | 1 | 30604 | 178 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Gor | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 485.3933 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-03-2017 20:21:44 CET | Rwanda | Rulindo | Murambi | Mvuzo | Rurama |  |  | Mutagata Motorised Network | 155 | 26296 | 49 | 536.6531 | 60 | 95 | 38.71% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1152 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release Chamber | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 08:22:17 CEST | Rwanda | Rulindo | Tumba | Nyirabirori | Gatare |  |  | Gatare water point near cafe plantation/Nyirambuga pumping | 143 | 30604 | 1 | 30604 | 143 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 483.3566 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 1 | 2 | Pressure Break Tank¦Distribution Chamber | 2017 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 23-03-2017 06:27:26 CET | Rwanda | Rulindo | Kisaro | Sayo | Rusongati |  |  | Kiruruma | 163 | 8295 | 25 | 331.8 | 160 | 3 | 98.16% | 1 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring¦Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2014 | 1 | 3 | 576000 | 720 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 15 | 2014 | 1 | 1 | 5 | Pressure Break Tank | 2014 | 1 | 1 | 3 | 2014 | 1 | 4000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 05:54:56 CET | Rwanda | Rulindo | Shyorongi | Kijabagwe | Rimwe |  |  | kirikumuryango network | 120 |  |  |  | 60 | 60 | 50% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 523.6364 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 14:13:31 CET | Rwanda | Rulindo | Rukozo | Mbuye | Nyarusebeya |  |  | Kabonanyoni | 60 | 7894 | 30 | 263.1333 | 55 | 5 | 91.67% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 418.9091 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 21:36:45 CET | Rwanda | Rulindo | Shyorongi | Rubona | Ngona |  |  | Bitete-Rwahi network | 122 | 1316 | 15 | 87.7333 | 35 | 87 | 28.69% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 822.8571 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 06:15:39 CET | Rwanda | Rulindo | Shyorongi | Rubona | Kigali |  |  | kirikumuryango network | 220 |  |  |  | 120 | 100 | 54.55% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 261.8182 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 17:44:28 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Nyabyondo |  |  | kirikumuryango network | 312 |  |  |  | 150 | 162 | 48.08% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 209.4545 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 2 | 10000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 07:43:16 CET | Rwanda | Rulindo | Burega | Butangampundu | Karugaju |  |  | Rwamugaza | 345 | 14106 | 38 | 371.2105 | 345 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 2 | 2003 | 1 | 3.5 | 493714.2857 | 286.2112 | 1 | 1 | 1 | 2003 | 1 | 8000 | 1 | 20 | 2014 | 1 | 1 | 16 |  | 2014 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 3 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 03-01-2015 02:02:29 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point at Nyirabirori cell/Nyirambuga pumping | 169 | 30604 | 1 | 30604 | 169 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 511.2426 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 16:58:14 CET | Rwanda | Rulindo | Rusiga | Kirenge | Rebero |  |  | Kirenge water point/Tare-Rusiga pumping | 181 | 9577 | 1 | 9577 | 181 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 10 | 1 | 0 |  |  |  |  | 40 | 43200 | 47.7348 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 11:53:31 CET | Rwanda | Rulindo | Masoro | Shengampuri | Umubuga |  |  | Mutagata Gravity Network | 175 | 26296 | 12 | 2191.3333 | 58 | 117 | 33.14% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2004 | 2 | 8 | 216000 | 744.8276 | 1 | 1 | 1 | 2004 | 2 | 3500 | 1 | 6 | 2004 | 2 | 1 | 4 | Distribution Chamber¦Washout And Air Release Chamber | 2004 | 2 | 1 | 2 | 2004 | 2 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 12 | 2004 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 15-03-2017 06:56:02 CET | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare I | 229 | 345 | 5 | 69 | 200 | 29 | 87.34% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 2 | 50 | 34560 | 34.56 | 1 | 1 | 1 | 2014 | 2 | 4500 | 1 | 2 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 15-03-2017 18:57:58 CET | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Giko cell water point/Nyirambuga pumping | 134 | 30604 | 1 | 30604 | 134 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Gor | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 644.7761 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 18-04-2017 06:45:43 CEST | Rwanda | Rulindo | Tumba | Gahabwa | Rushaki |  |  | Rushaki water point Bizimana/Nyirambuga pumping system | 152 | 30604 | 1 | 30604 | 152 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 454.7368 | 1 | 0 |  |  |  |  | 0 |  |  |  | 1 | 1 | Distribution Chamber | 2017 | 1 | 1 | 1 | 2017 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 10:54:58 CET | Rwanda | Rulindo | Bushoki | N.Ngarama | Bubiro |  |  | Gakenke-Muyongwe-Karyango-Mugera Water point/Tare-Rusiga pumping | 300 | 9577 | 1 | 9577 | 300 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 8 | 1 | 0 |  |  |  |  | 40 | 43200 | 28.8 | 1 | 1 | 1 | 2015 | 1 | 4000 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 3 | 2015 | 1 | 4000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 06:19:41 CET | Rwanda | Rulindo | Kinihira | Marembo | Cyogo |  |  | Nyamagana-Kinihira | 184 |  |  |  | 65 | 119 | 35.33% | 0 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1063.3846 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 15:44:33 CET | Rwanda | Rulindo | Murambi | Gatwa | Kigarama |  |  | rwisike | 209 | 9536 | 1 | 9536 | 209 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2001 | 1 | 14 | 123428.5714 | 118.1135 | 1 | 1 | 1 | 2001 | 1 | 1200 | 1 | 7 | 2001 | 1 | 0 |  |  |  |  | 1 | 1 | 2001 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2001 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 25-03-2017 20:47:43 CET | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | Kiduha | 151 |  |  |  | 130 | 21 | 86.09% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2007 | Italians(Lake Angels) | Groundwater (Well, Etc.) | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 2 | 20 | 86400 | 132.9231 | 1 | 1 | 1 | 2007 | 2 | 2200 | 1 | 3 | 2007 | 2 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2007 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 21-03-2017 16:54:16 CET | Rwanda | Rulindo | Kinihira | Rebero | Taba |  |  | Miyove-Kinihira | 122 | 10452 | 19 | 550.1053 | 60 | 62 | 49.18% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 1152 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 21-03-2017 14:14:12 CET | Rwanda | Rulindo | Rukozo | Mbuye | Musare |  |  | Kabonanyoni | 40 | 7894 | 30 | 263.1333 | 35 | 5 | 87.5% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 658.2857 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber | 2015 | 1 | 1 | 3 | 2015 | 2 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 14-04-2017 21:19:29 CEST | Rwanda | Rulindo | Bushoki | Kayenzi | Gitaba |  |  | Murambo catchment | 118 |  |  |  | 118 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Rulindo District | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 20 | 86400 | 146.4407 | 1 | 1 | 1 | 2015 | 1 | 100 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 13:39:51 CET | Rwanda | Rulindo | Bushoki | Mukoto | Muko |  |  | Rusave water supply system/Water point at Anselme Gerant | 116 | 567 | 1 | 567 | 116 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Government | Spring | 2 | 1 | 0 |  |  |  |  | 120 | 14400 | 24.8276 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 21:35:17 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 354 | 6436 | 26 | 247.5385 | 120 | 234 | 33.9% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 288 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 28-03-2017 08:41:37 CEST | Rwanda | Rulindo | Ntarabana | Mahaza | Rusekabuye |  |  | Rwamugaza network | 195 | 14106 | 35 | 403.0286 | 195 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 590.7692 | 1 | 1 | 2 | 2003 | 1 | 3500 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-06-2017 09:28:08 CEST | Rwanda | Rulindo | Cyinzuzi | Rudogo | Musenyi |  |  | Kararama | 98 | 6572 | 4 | 1643 | 10 | 88 | 10.2% | 0 | 0 | 1 | Piped Network With Pump | 2009 | Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2009 | 1 | 4.5 | 384000 | 7680 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 7 | 2009 | 1 | 1 | 14 | Pressure Break Tank¦Distribution Chamber | 2009 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 1 | 2012 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 05-04-2017 21:06:38 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Gifuba |  |  | Rutare source catchment area | 108 | 9577 | 1 | 9577 | 108 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 1960 | Government | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 1960 | 2 | 20 | 86400 | 160 | 1 | 1 | 1 | 1960 | 2 | 100 | 0 |  |  |  | 1 | 1 | Distribution Chamber | 1960 | 2 | 1 | 1 | 1960 | 2 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  | 1960 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 15-04-2017 22:06:22 CEST | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Gasiza market water point1/Nyagahondo gravity system | 228 | 844 | 1 | 844 | 228 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2010 | Caritas | Spring | 1 | 1 | 0 |  |  |  |  | 30 | 57600 | 50.5263 | 1 | 0 |  |  |  |  | 1 | 1 | 2010 | 1 | 0 |  |  |  |  | 1 | 2 | 2010 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2010 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 06-03-2017 17:15:09 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Bugarura |  |  |  | 5000 |  |  |  | 3000 | 2000 | 60% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2000 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 4 | 2010 | 1 | 20 | 86400 | 5.76 | 0 | 1 | 1 | 2010 | 1 | 6500 | 1 | 2 | 2010 | 2 | 1 | 20 | Sedimentation Tank¦Pressure Break Tank¦Distribution Chamber | 2010 | 3 | 1 | 6 | 2010 | 2 | 10000 | 1 | 1 | 2010 | 3 | 1 | 2010 | 3 | 1 | Disinfection/Chlorination | 2010 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 14 | 2010 | 3 | Yes | 5 | 15 | 0 | 75 | 0 | 3
2017 | 12-03-2017 10:47:06 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Karama |  |  | Bitete-Muvumu | 121 | 1316 | 7 | 188 | 40 | 81 | 33.06% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 785.4545 | 1 | 1 | 1000 | 2013 | 2 | 1000 | 1 | 4 | 2013 | 1 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse,Washout | 2013 | 2 | 1 | 1 | 2013 | 1 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 06:03:20 CET | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 495 | 14106 | 38 | 371.2105 | 495 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 155.1515 | 1 | 1 | 2 | 2012 | 2 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 10-03-2017 04:16:01 CET | Rwanda | Rulindo | Ngoma | Karambo | Butare |  |  | Shishi network | 122 |  |  |  | 44 | 78 | 36.07% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 28 | 61714.2857 | 280.5195 | 1 | 1 | 1 | 2014 | 1 | 700 | 1 | 2 | 2014 | 1 | 0 |  |  |  |  | 1 | 1 | 2014 | 1 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 12-03-2017 07:21:51 CET | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 35 | 20456 | 36 | 568.2222 | 35 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1974.8571 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 10 | 30 | 0 | 300 | 1 | 2
2017 | 21-03-2017 15:58:29 CET | Rwanda | Rulindo | Kinihira | Karegamazi | Magezi |  |  | Miyove-Kinihira | 141 | 10452 | 19 | 550.1053 | 60 | 81 | 42.55% | 0 | 0 | 1 | Piped Network -- Gravity Only | 1989 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 1152 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse,Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1989 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 21-03-2017 16:40:24 CET | Rwanda | Rulindo | Kinihira | Karegamazi | Gatembe |  |  | Miyove-Kinihira | 149 | 10452 | 19 | 550.1053 | 60 | 89 | 40.27% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 1152 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1989 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 22-03-2017 18:04:28 CET | Rwanda | Rulindo | Kinihira | Butunzi | Barayi |  |  | Nyamagana-Kinihira | 151 |  |  |  | 80 | 71 | 52.98% | 0 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 864 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 13:01:19 CET | Rwanda | Rulindo | Bushoki | Mukoto | Marembo |  |  | Marembo police station/Tare-Rusiga pumping | 90 | 9577 | 1 | 9577 | 90 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 10 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 96 | 1 | 1 | 1 | 2015 | 1 | 4000 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 8000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 09:55:50 CEST | Rwanda | Rulindo | Kisaro | Mubuga | Nyakarekare |  |  | Gahama Kisaro network | 150 | 10234 | 14 | 731 | 150 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 |  | 1 | 2012 | 1 | 3 | 576000 | 768 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 |  | 2012 | 2 | 1 | 1 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 2 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 13-03-2017 06:50:42 CET | Rwanda | Rulindo | Ngoma | Munyarwanda | Kirungu |  |  | Kabarore-Ngoma-Nyabuko network | 77 | 8284 | 14 | 591.7143 | 77 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 1 | 4 | 432000 | 1122.0779 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 4 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 2 | Yes | 1 | 10 | 0 | 10 | 1 | 1
2017 | 25-04-2017 16:49:20 CEST | Rwanda | Rulindo | Kisaro | Murama | Kibingwe |  |  | Gahama Kisaro network | 122 | 10234 | 14 | 731 | 122 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 |  | 1 | 2012 | 1 | 120 | 14400 | 23.6066 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 6 | 2012 | 1 | 1 | 12 |  | 2012 | 1 | 1 | 1 | 2012 | 1 | 30000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-04-2017 23:08:28 CEST | Rwanda | Rulindo | Buyoga | Karama | Karambo |  |  | Karambo water point/Nyirambuga pumping | 165 | 30604 | 1 | 30604 | 165 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 523.6364 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 05-04-2017 21:47:27 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Tare |  |  | Tare-Rusiga pumping system/Water point at Tare | 109 | 9577 | 1 | 9577 | 109 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 79.2661 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 08:09:12 CET | Rwanda | Rulindo | Murambi | Mugambazi | Kigarama |  |  | Mutagata motorised network | 169 | 26296 | 49 | 536.6531 | 57 | 112 | 33.73% | 0 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1212.6316 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 15:45:23 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kamatongo |  |  | 0 | 1125 | 6572 | 15 | 438.1333 |  | 1125 |  | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 3 | 4.5 | 384000 |  | 0 | 1 | 2 | 2009 | 1 | 3000 | 1 | 3 | 2014 | 3 | 1 | 8 |  | 2014 | 3 | 1 | 2 | 2014 | 3 | 3000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 3 | Yes | 365 | 0 | 0 | 0 | 0 | 3
2017 | 15-04-2017 22:00:32 CEST | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Water point at Nyagahondo source1/Nyagahondo gravity system | 228 | 844 | 1 | 844 | 228 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2010 | Caritas | Spring | 2 | 0 | 0 |  |  |  |  | 30 | 57600 | 50.5263 | 1 | 1 | 1 | 2010 | 1 | 100 | 1 | 1 | 2010 | 1 | 0 |  |  |  |  | 1 | 2 | 2010 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2010 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 00:41:30 CET | Rwanda | Rulindo | Tumba | Taba | Nyirataba |  |  | Nyirataba1 water point/Nyirambuga pumping | 169 | 30604 | 1 | 30604 | 169 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 511.2426 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 02:09:09 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Bukiga water point/Nyirambuga pumping | 169 | 30604 | 1 | 30604 | 169 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 511.2426 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 18:40:59 CET | Rwanda | Rulindo | Base | Gitare | Gisiza |  |  | Rwicanyoni | 116 | 698 | 7 | 99.7143 | 115 | 1 | 99.14% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 1 | 10 | 172800 | 300.5217 | 1 | 1 | 1 | 2016 | 1 | 8600 | 1 | 3 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-04-2017 21:57:59 CEST | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Water point near Gitera/Nyagahondo water gravity system | 228 | 844 | 1 | 844 | 228 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2010 | Caritas | Spring | 1 | 1 | 0 |  |  |  |  | 30 | 57600 | 50.5263 | 1 | 1 | 1 | 2010 | 1 | 1000 | 1 | 1 | 2010 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2010 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 18:12:19 CET | Rwanda | Rulindo | Ngoma | Karambo | Karambi |  |  | Gahama network | 117 |  |  |  | 29 | 88 | 24.79% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 15 | 115200 | 794.4828 | 1 | 1 | 1 | 2014 | 1 | 1800 | 1 | 2 | 2014 | 1 | 1 | 1 | Distribution Chamber | 2014 | 1 | 1 | 1 | 2014 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 12-03-2017 07:08:55 CET | Rwanda | Rulindo | Rukozo | Buraro | Kivomo |  |  | Nyamagana | 78 | 20456 | 36 | 568.2222 | 70 | 8 | 89.74% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 987.4286 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 2 | Yes | 10 | 25 | 0 | 250 | 0 | 2
2017 | 02-01-2015 05:52:39 CET | Rwanda | Rulindo | Base | Cyohoha | Kabingo |  |  | Nyamagana | 65 | 20456 | 36 | 568.2222 | 60 | 5 | 92.31% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1152 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 07-03-2017 21:14:55 CET | Rwanda | Rulindo | Base | Rwamahwa | Kiruli |  |  | Migogo | 223 | 558 | 10 | 55.8 | 200 | 23 | 89.69% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2009 | Italians(Lake Angels) | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2009 | 2 | 20 | 86400 | 86.4 | 1 | 1 | 2 | 2009 | 2 | 3000 | 1 | 3 | 2009 | 2 | 0 |  |  |  |  | 1 | 2 | 2012 | 2 | 3000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2009 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 09-03-2017 18:12:00 CET | Rwanda | Rulindo | Ngoma | Karambo | Karambi |  |  | Gahama network | 117 | 0 | 5 | 0 | 25 | 92 | 21.37% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 15 | 115200 | 921.6 | 1 | 1 | 1 | 2014 | 1 | 1800 | 1 | 2 | 2014 | 1 | 1 | 1 | Distribution Chamber | 2014 | 1 | 1 | 1 | 2014 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2014 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 23-04-2017 14:42:15 CEST | Rwanda | Rulindo | Buyoga | Ndarage | Kagozi |  |  | ndarage | 155 | 0 | 9 | 0 | 130 | 25 | 83.87% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2014 | 1 | 60 | 28800 | 44.3077 | 1 | 1 | 1 | 2014 | 1 | 5000 | 1 | 5 | 2014 | 1 | 0 |  |  |  |  | 1 | 1 | 2014 | 1 | 6700 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 19:36:27 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Nyarushinya |  |  | kinywamagana pumping network | 238 | 6436 | 26 | 247.5385 | 150 | 88 | 63.03% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 230.4 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 09-03-2017 21:46:11 CET | Rwanda | Rulindo | Shyorongi | Rubona | Rwahi |  |  | Bitete-Rwahi network | 450 | 1316 | 15 | 87.7333 | 450 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 64 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 05-04-2017 19:22:56 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Gifuba |  |  | Rutare-Nyirangarama gravity system/Water point at ADEPR NYIRANGARAMA | 108 | 726 | 1 | 726 | 108 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Government | Spring | 1 | 1 | 0 |  |  |  |  | 20 | 86400 | 160 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-03-2017 20:20:27 CET | Rwanda | Rulindo | Murambi | Mvuzo | Munyinya |  |  | Mutagata Motorised Network | 130 | 26296 | 49 | 536.6531 | 130 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 531.6923 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release Chamber | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 07:10:57 CET | Rwanda | Rulindo | Rukozo | Buraro | Kivomo |  |  | Nyamagana | 700 | 20456 | 36 | 568.2222 | 700 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 98.7429 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 10 | 22 | 0 | 220 | 1 | 2
2017 | 15-04-2017 23:35:15 CEST | Rwanda | Rulindo | Rusiga | Gako | Gifumba |  |  | Source Murungurira/Murungurira-Nyakariba gravity system | 188 | 0 | 1 | 0 | 188 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2010 | Local Government | Spring | 2 | 0 | 0 |  |  |  |  | 50 | 34560 | 36.766 | 1 | 1 | 1 | 2010 | 2 | 100 | 1 | 1 | 2010 | 2 | 1 | 1 | Distribution Chamber | 2010 | 3 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2010 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 24-03-2017 08:54:47 CET | Rwanda | Rulindo | Masoro | Nyamyumba | Kabeza |  |  | marenge | 120 | 5544 | 14 | 396 | 120 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 1 | 20 | 86400 | 144 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 7 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 23:42:17 CET | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point at Gisha church/Nyirambuga Pumping | 133 | 30604 | 1 | 30604 | 133 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 649.6241 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 13:01:14 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Kagunda |  |  | Muvumu- Taba | 94 | 0 | 10 | 0 | 35 | 59 | 37.23% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 25 | 69120 | 394.9714 | 1 | 1 | 1 | 2013 | 1 | 800 | 1 | 3 | 2013 | 2 | 1 | 9 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 7500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | Yes | 1 | 3 | 0 | 3 | 1 | 2
2017 | 09-03-2017 17:12:10 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Nyamirembe |  |  | kirikumuryango network | 256 | 0 | 26 | 0 | 120 | 136 | 46.88% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 261.8182 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 10000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-03-2017 19:19:56 CET | Rwanda | Rulindo | Kinihira | Butunzi | Ndorandi |  |  | Nyamagana-Kinihira | 139 | 0 | 15 | 0 | 50 | 89 | 35.97% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1382.4 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 18:08:52 CEST | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | Water point chez Nsabayezu/Kivomo-Ntakara gravity | 198 | 0 | 1 | 0 | 198 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 50 | 34560 | 34.9091 | 1 | 0 |  |  |  |  | 0 |  |  |  | 1 | 1 | Water Point Valve Chamber | 2015 | 3 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 13-03-2017 22:06:38 CET | Rwanda | Rulindo | Bushoki | Giko | Kivomo |  |  | Kivomo water point/Buramira gravity | 127 | 1255 | 1 | 1255 | 127 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only¦Private Tap With Piped Supply | 2015 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 30 | 57600 | 90.7087 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 17:05:26 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Rweya |  |  | kirikumuryango network | 212 | 0 | 26 | 0 | 90 | 122 | 42.45% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 349.0909 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 10000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 23:38:00 CET | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point 2 at Gisha/Nyirambuga pumping | 133 | 30604 | 1 | 30604 | 133 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 649.6241 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 10:17:27 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Gitambi |  |  | Rwamugaza network | 230 | 14106 | 35 | 403.0286 | 230 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 1 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 500.8696 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 25-03-2017 20:47:10 CET | Rwanda | Rulindo | Buyoga | Butare | Giko |  |  | Kiduha | 151 | 0 | 7 | 0 | 130 | 21 | 86.09% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2007 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 2 | 20 | 86400 | 132.9231 | 1 | 1 | 1 | 2007 | 2 | 2200 | 1 | 3 | 2007 | 2 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2007 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 02-01-2015 05:48:18 CET | Rwanda | Rulindo | Cyungo | Rwili | Karambi |  |  | Nyamagana | 80 | 20456 | 36 | 568.2222 | 20 | 60 | 25% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 3456 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 7 | 60 | 0 | 420 | 0 | 2
2017 | 21-04-2017 16:34:16 CEST | Rwanda | Rulindo | Rusiga | Taba | Bitare |  |  | Bitare-Gahondo sources catchment area | 113 | 9577 | 1 | 9577 | 113 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2017 | Government Of Rwanda | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2017 | 1 | 10 | 172800 | 305.8407 | 1 | 1 | 2 | 2017 | 1 | 400 | 1 | 2 | 2017 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 10:23:31 CET | Rwanda | Rulindo | Ngoma | Kabuga | Nyabuko |  |  | Kabarore-Ngoma-Nyabuko network | 122 | 8284 | 14 | 591.7143 | 25 | 97 | 20.49% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring¦Groundwater (Well, Etc.) | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 2 | 4 | 432000 | 3456 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 21:39:13 CET | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Kigamba2 water point/Rutomvu gravity | 172 | 3015 | 1 | 3015 | 172 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 50.2326 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 22:00:18 CET | Rwanda | Rulindo | Shyorongi | Rubona | Nyarunyinya |  |  | Bitete-Rwahi network | 132 | 1316 | 15 | 87.7333 | 35 | 97 | 26.52% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 822.8571 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 21:27:57 CET | Rwanda | Rulindo | Bushoki | Kayenzi | Gitaba |  |  | Ngarama water point/Rutomvu gravity | 110 | 3015 | 1 | 3015 | 110 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 78.5455 | 1 | 0 |  |  |  |  | 1 | 1 | 2013 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 10:58:16 CEST | Rwanda | Rulindo | Kisaro | Kamushenyi | Karambi |  |  | Gahama Kisaro network | 184 | 10234 | 14 | 731 | 184 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 |  | 1 | 2012 | 1 | 3 | 576000 | 626.087 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 |  | 2012 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 2 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 10-03-2017 12:20:17 CET | Rwanda | Rulindo | Mbogo | Bukoro | Rwambogo |  |  | Rwambogo | 156 | 934 | 3 | 311.3333 | 50 | 106 | 32.05% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 1 | 60 | 28800 | 115.2 | 1 | 1 | 1 | 2016 | 1 | 700 | 1 | 1 | 2016 | 2 | 0 |  |  |  |  | 1 | 1 | 2016 | 1 | 350 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 23-03-2017 17:25:45 CET | Rwanda | Rulindo | Buyoga | Ndarage | Karambi |  |  | Ndarage | 112 | 0 | 9 | 0 | 100 | 12 | 89.29% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 30 | 57600 | 115.2 | 1 | 1 | 1 | 2014 | 1 | 6700 | 1 | 5 | 2014 | 1 | 0 |  |  |  |  | 1 | 1 | 2014 | 1 | 6700 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 14:50:31 CEST | Rwanda | Rulindo | Mbogo | Mushali | Bukongi |  |  | Gitabage network | 168 | 0 | 3 | 0 | 45 | 123 | 26.79% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2008 | Catholic Church | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2008 | 1 | 40 | 43200 | 192 | 1 | 1 | 1 | 2008 | 1 | 700 | 1 | 2 | 2008 | 1 | 0 |  |  |  |  | 1 | 1 | 2008 | 1 | 500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2008 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 07:38:18 CET | Rwanda | Rulindo | Burega | Butangampundu | Kisigiro |  |  | Rwamugaza | 605 | 14106 | 38 | 371.2105 | 605 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 2 | 2003 | 1 | 3.5 | 493714.2857 | 163.2113 | 1 | 1 | 1 | 2003 | 1 | 8000 | 1 | 20 | 2003 | 1 | 1 | 16 |  | 2003 | 2 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 2 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 23-03-2017 10:02:03 CET | Rwanda | Rulindo | Murambi | Bubangu | Gashubi |  |  | Mutagata Motorised Network | 140 | 26296 | 49 | 536.6531 | 39 | 101 | 27.86% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1772.3077 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-04-2017 22:01:00 CEST | Rwanda | Rulindo | Base | Gitare | Mugenda I |  |  | Water point at Innocent's/Nyirambuga pumping system | 117 | 30604 | 1 | 30604 | 117 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 738.4615 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 17:25:53 CET | Rwanda | Rulindo | Buyoga | Busoro | Rugarama |  |  | Ndarage | 189 | 0 | 9 | 0 | 170 | 19 | 89.95% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 30 | 57600 | 67.7647 | 1 | 1 | 1 | 2014 | 1 | 6700 | 1 | 5 | 2014 | 1 | 0 |  |  |  |  | 1 | 1 | 2014 | 1 | 6700 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 10:33:47 CET | Rwanda | Rulindo | Murambi | Bubangu | Rebero |  |  | Mutagata Motorised Network | 148 | 26296 | 49 | 536.6531 | 70 | 78 | 47.3% | 0 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 987.4286 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 18-04-2017 07:06:07 CEST | Rwanda | Rulindo | Tumba | Barari | Gaseke |  |  | Water point chez Rujugiro/Nyirambuga pumping system | 149 | 30604 | 1 | 30604 | 149 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 463.8926 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-04-2017 21:46:10 CEST | Rwanda | Rulindo | Bushoki | Mukoto | Buvumo |  |  | Rukungeri-Bushoki cafe washing factory gravity system | 124 | 0 | 1 | 0 | 124 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2007 | Local Government In Partnership With Bushoki Cafe Washing Factory | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 69.6774 | 1 | 1 | 100 | 2007 | 1 | 800 | 1 | 1 | 2007 | 2 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2007 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 15-03-2017 07:36:13 CET | Rwanda | Rulindo | Base | Gitare | Nyamugali |  |  | Rutembe | 229 | 1012 | 7 | 144.5714 | 200 | 29 | 87.34% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 50 | 34560 | 34.56 | 1 | 1 | 1 | 2016 | 2 | 3500 | 1 | 2 | 2016 | 3 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 15-03-2017 17:12:21 CET | Rwanda | Rulindo | Burega | Butangampundu | Kisigiro |  |  | Rwamugaza | 605 | 14106 | 38 | 371.2105 | 605 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 126.9421 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 23 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 10-03-2017 12:31:20 CET | Rwanda | Rulindo | Mbogo | Bukoro | Rwambogo |  |  | Rwambogo | 156 | 934 | 3 | 311.3333 | 52 | 104 | 33.33% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2 | 2016 | 1 | 60 | 28800 | 110.7692 | 1 | 1 | 1 | 2016 | 1 | 700 | 1 | 1 | 2016 | 2 | 0 |  |  |  |  | 1 | 1 | 2016 | 1 | 350 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2016 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 16-04-2017 22:49:51 CEST | Rwanda | Rulindo | Buyoga | Busoro | Rugarama |  |  | Water at Kaziba chez Verene/Nyirambuga pumping system | 189 | 30604 | 1 | 30604 | 189 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 457.1429 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 15:05:55 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kamatongo |  |  | 0 | 1125 | 6572 | 15 | 438.1333 |  | 1125 |  | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2009 | 1 | 4.5 | 384000 |  | 0 | 1 | 2 | 2014 | 3 | 3000 | 1 | 6 | 2014 | 3 | 1 | 13 |  | 2014 | 3 | 1 | 2 | 2014 | 3 | 3000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 3 | Yes | 365 | 0 | 0 | 0 | 0 | 3
2017 | 21-03-2017 18:05:25 CET | Rwanda | Rulindo | Kinihira | Butunzi | Barayi |  |  | Miyove- Kinihira | 1600 | 10452 | 4 | 2613 | 1600 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 43.2 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 1989 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1989 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 02-06-2017 08:58:12 CEST | Rwanda | Rulindo | Cyinzuzi | Migendezo | Gitabage |  |  | Kararama | 120 | 6572 | 4 | 1643 | 110 | 10 | 91.67% | 0 | 0 | 1 | Piped Network With Pump | 2009 | Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2009 | 1 | 4.5 | 384000 | 698.1818 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 7 | 2012 | 1 | 1 | 14 | Sedimentation Tank¦Pressure Break Tank¦Distribution Chamber | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 13:12:04 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Muvumu |  |  | Muvumu- Taba | 132 | 0 | 10 | 0 | 75 | 57 | 56.82% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 25 | 69120 | 184.32 | 1 | 1 | 1 | 2013 | 1 | 800 | 1 | 3 | 2013 | 2 | 1 | 9 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 7500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | Yes | 1 | 3 | 0 | 3 | 1 | 2
2017 | 06-04-2017 19:18:02 CEST | Rwanda | Rulindo | Bushoki | Mukoto | Buyogoma |  |  | Buyogoma water point | 130 | 0 | 1 | 0 | 130 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Government Of Rwanda | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 66.4615 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 24-04-2017 23:23:19 CEST | Rwanda | Rulindo | Burega | Butangampundu | Karambi |  |  | Rwamugaza network | 73 | 14106 | 35 | 403.0286 | 73 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 1578.0822 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 14 |  | 2003 | 1 | 1 | 1 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 09-03-2017 06:00:41 CET | Rwanda | Rulindo | Shyorongi | Kijabagwe | Rimwe |  |  | kirikumuryango network | 120 | 0 | 26 | 0 | 60 | 60 | 50% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 523.6364 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 06:52:39 CET | Rwanda | Rulindo | Base | Cyohoha | Rubanda |  |  | Migogo | 170 | 558 | 10 | 55.8 | 120 | 50 | 70.59% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Lake Angels | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2009 | 2 | 60 | 28800 | 48 | 1 | 1 | 2 | 2009 | 2 | 3000 | 1 | 3 | 2009 | 2 | 0 |  |  |  |  | 1 | 2 | 2009 | 2 | 3000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2013 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 21-03-2017 17:46:27 CET | Rwanda | Rulindo | Kinihira | Karegamazi | Ntunguru |  |  | Miyove-Kinihira | 168 | 10452 | 19 | 550.1053 | 70 | 98 | 41.67% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 987.4286 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1989 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 25-03-2017 11:31:56 CET | Rwanda | Rulindo | Masoro | Kivugiza | Musenga |  |  | Mutagata Gravity network | 185 | 26296 | 12 | 2191.3333 | 140 | 45 | 75.68% | 0 | 0 | 1 | Piped Network -- Gravity Only | 1987 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2004 | 2 | 8 | 216000 | 308.5714 | 1 | 1 | 1 | 2004 | 2 | 3500 | 1 | 6 | 2004 | 2 | 1 | 4 | Distribution Chamber¦Washout And Air Release | 2004 | 2 | 1 | 2 | 2004 | 2 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 12 | 2015 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 10-03-2017 11:29:29 CET | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | Nganzo-Kabarore | 198 | 0 | 5 | 0 | 98 | 100 | 49.49% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 20 | 86400 | 176.3265 | 1 | 1 | 1 | 2014 | 2 | 400 | 1 | 3 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 3 | 800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2014 | 3 | Yes | 5 | 30 | 0 | 150 | 0 | 3
2017 | 09-03-2017 08:43:49 CET | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 77 | 1458 | 6 | 243 | 70 | 7 | 90.91% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2005 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2005 | 1 | 75 | 23040 | 65.8286 | 1 | 1 | 1 | 2005 | 1 | 7000 | 1 | 2 | 2005 | 1 | 1 | 2 | Pressure Break Tank | 2017 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 22:02:44 CET | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Nkore source catchment | 172 | 0 | 1 | 0 | 172 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 50.2326 | 1 | 1 | 1 | 2013 | 1 | 50 | 1 | 1 | 2013 | 1 | 0 |  |  |  |  | 1 | 1 | 2013 | 1 | 2000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 21-03-2017 14:30:24 CET | Rwanda | Rulindo | Kinihira | Karegamazi | Magezi |  |  | Miyove-Kinihira | 141 | 10452 | 19 | 550.1053 | 80 | 61 | 56.74% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 864 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1989 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 21-03-2017 13:55:34 CET | Rwanda | Rulindo | Rukozo | Buraro | Kabingo |  |  | Kabonanyoni | 38 | 7894 | 30 | 263.1333 | 35 | 3 | 92.11% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 658.2857 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 06-04-2017 19:13:07 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Remera |  |  | Kinyankera gravity system | 105 | 0 | 1 | 0 | 105 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2010 | Local Government And Community | Spring | 1 | 1 | 0 |  |  |  |  | 20 | 86400 | 164.5714 | 1 | 1 | 1 | 2015 | 1 | 100 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2010 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 18:11:13 CET | Rwanda | Rulindo | Ngoma | Karambo | Jyambere |  |  | Gahama network | 117 | 0 | 5 | 0 | 52 | 65 | 44.44% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 15 | 115200 | 443.0769 | 1 | 1 | 1 | 2014 | 1 | 1800 | 1 | 2 | 2014 | 1 | 1 | 1 | Distribution Chamber | 2014 | 1 | 1 | 1 | 2014 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 18-04-2017 06:56:47 CEST | Rwanda | Rulindo | Tumba | Gahabwa | Kabuga |  |  | Water point chez Ntuyenabo/Nyirambuga pumping system | 155 | 30604 | 1 | 30604 | 155 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 445.9355 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 15-03-2017 08:00:12 CET | Rwanda | Rulindo | Base | Cyohoha | Kabuga |  |  | Gihanga | 73 | 2456 | 10 | 245.6 | 60 | 13 | 82.19% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 2 | 15 | 115200 | 384 | 1 | 1 | 1 | 2016 | 2 | 7200 | 1 | 6 | 2016 | 2 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 3 | Yes | 7 | 7 | 0 | 49 | 0 | 2
2017 | 20-04-2017 10:42:00 CEST | Rwanda | Rulindo | Tumba | Nyirabirori | Gihanga |  |  | Water point at Gihanga under road/Nyirambuga pumping | 152 | 30604 | 1 | 30604 | 152 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 454.7368 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 1 | 1 | 1 | Washout | 2017 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 26-03-2017 23:13:51 CEST | Rwanda | Rulindo | Mbogo | Rurenge | Gitaba |  |  | Musenge network | 195 | 6074 | 29 | 209.4483 | 100 | 95 | 51.28% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 778.3784 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Washout And Air Release | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 04:35:44 CET | Rwanda | Rulindo | Masoro | Kivugiza | Gasenga |  |  | Mutagata motorised network | 284 | 26296 | 49 | 536.6531 | 138 | 146 | 48.59% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 500.8696 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 05:16:20 CET | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 1789 | 14 | 127.7857 | 180 | 12 | 93.75% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2012 | Padiri | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 30 | 57600 | 64 | 1 | 1 | 1 | 2016 | 1 | 6450 | 1 | 2 | 2012 | 1 | 1 | 2 | Distribution Chamber | 2012 | 1 | 1 | 1 | 2012 | 1 | 6450 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-04-2017 16:22:36 CEST | Rwanda | Rulindo | Rusiga | Taba | Karenge |  |  | Water point at Kukabuga/Bitare-Gahondo gravity | 112 | 9577 | 1 | 9577 | 112 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 1989 | Catholic Church | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2017 | 1 | 10 | 172800 | 308.5714 | 1 | 1 | 2 | 2017 | 1 | 400 | 1 | 1 | 1989 | 3 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1989 | 3 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 15-03-2017 19:58:10 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Water point at Kayenzi cell near TCT/Nyirambuga pumping system | 174 | 30604 | 1 | 30604 | 174 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Gor | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 496.5517 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 05:16:46 CET | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 1789 | 14 | 127.7857 | 180 | 12 | 93.75% | 0 | 1 | 1 | Piped Network -- Gravity Only¦Private Tap With Piped Supply | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2016 | 1 | 30 | 57600 | 64 | 1 | 1 | 2 | 2012 | 1 | 6450 | 1 | 2 | 2012 | 1 | 1 | 2 | Distribution Chamber | 2012 | 1 | 1 | 2 | 2016 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 14-03-2017 22:35:17 CET | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point/AEP Kigarama | 243 | 2621 | 1 | 2621 | 243 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 35.5556 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 07:05:32 CET | Rwanda | Rulindo | Rukozo | Buraro | Kivomo |  |  | Nyamagana | 1100 | 20456 | 36 | 568.2222 | 1100 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 62.8364 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 10 | 25 | 0 | 250 | 0 | 2
2017 | 28-03-2017 10:35:17 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza network | 229 | 14106 | 35 | 403.0286 | 229 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 503.0568 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 13:38:41 CET | Rwanda | Rulindo | Buyoga | Karama | Karambo |  |  | Water point at Karama cell/Nyirambuga pumping | 165 | 30604 | 1 | 30604 | 165 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 523.6364 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-04-2017 12:23:03 CEST | Rwanda | Rulindo | Murambi | Mugambazi | Gahama |  |  |  | 115 | 26296 | 31 | 848.2581 | 115 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 1 | 0 | 0 |  |  |  |  | 87 | 19862.069 | 34.5427 | 1 | 0 |  |  |  |  | 1 | 1 | 2003 | 2 | 0 |  |  |  |  | 1 | 1 | 2003 | 2 | 100 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 03-01-2015 01:06:32 CET | Rwanda | Rulindo | Tumba | Gahabwa | Mafene |  |  | Water point at Gahabwa cell(near EP Gahabwa)/Nyirambuga pumping | 172 | 30604 | 1 | 30604 | 172 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 502.3256 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 18:10:47 CET | Rwanda | Rulindo | Ngoma | Karambo | Karambi |  |  | Gahama network | 117 | 0 | 5 | 0 | 33 | 84 | 28.21% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 15 | 115200 | 698.1818 | 1 | 1 | 1 | 2014 | 1 | 1800 | 1 | 2 | 2014 | 1 | 1 | 1 | Distribution Chamber | 2014 | 1 | 1 | 1 | 2014 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2014 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 28-03-2017 10:32:24 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza network | 229 | 14106 | 35 | 403.0286 | 229 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 2 | 2003 | 1 | 3 | 576000 | 503.0568 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 14 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 12:49:35 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Kagunda |  |  | Muvumu- Taba | 94 | 0 | 10 | 0 | 20 | 74 | 21.28% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 25 | 69120 | 691.2 | 1 | 1 | 1 | 2013 | 1 | 800 | 1 | 3 | 2013 | 2 | 1 | 9 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 7500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | Yes | 1 | 3 | 0 | 3 | 1 | 2
2017 | 16-03-2017 06:18:13 CET | Rwanda | Rulindo | Burega | Karengeli | Rwamiko |  |  | Rwamugaza | 440 | 14106 | 38 | 371.2105 | 440 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 174.5455 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 12:46:37 CET | Rwanda | Rulindo | Rusiga | Taba | Bitare |  |  | Muvumu-Taba | 113 | 0 | 2 | 0 | 20 | 93 | 17.7% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 25 | 69120 | 691.2 | 1 | 1 | 1 | 2013 | 1 | 800 | 1 | 3 | 2013 | 2 | 1 | 9 | Pressure Break Tank¦Distribution Chamber¦Washout, Ventouse | 2013 | 1 | 1 | 1 | 2013 | 1 | 7500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 2 | Yes | 1 | 3 | 0 | 3 | 1 | 2
2017 | 10-03-2017 13:36:21 CET | Rwanda | Rulindo | Bushoki | Mukoto | Gatare |  |  | Gatare water point/Tare-Rusiga pumping | 129 | 9577 | 1 | 9577 | 129 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 10 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 66.9767 | 1 | 1 | 1 | 2015 | 1 | 4000 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 8000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 25-04-2017 00:12:47 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Kazi |  |  | Rwamugaza network | 184 | 14106 | 35 | 403.0286 | 184 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 626.087 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 14 |  | 2003 | 1 | 1 | 1 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 08:34:10 CEST | Rwanda | Rulindo | Ntarabana | Mahaza | Gitwa |  |  | Rwamugaza network | 120 | 14106 | 35 | 403.0286 | 120 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 960 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 18-04-2017 20:05:03 CEST | Rwanda | Rulindo | Tumba | Taba | Ruvumba |  |  | Water point chez Darage/Nyirambuga pumping system | 109 | 30604 | 1 | 30604 | 109 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 634.1284 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 08-03-2017 16:42:54 CET | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 1789 | 14 | 127.7857 | 100 | 92 | 52.08% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 2 | 45 | 38400 | 76.8 | 1 | 1 | 2 | 2016 | 3 | 1000 | 1 | 3 | 2012 | 2 | 1 | 1 | Distribution Chamber | 2012 | 1 | 1 | 2 | 2016 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 09-03-2017 08:15:30 CET | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Gisoro-Nyundo network | 188 | 2297 | 2 | 1148.5 | 30 | 158 | 15.96% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 13 | 132923.0769 | 886.1538 | 1 | 1 | 2013 | 2013 | 1 | 30 | 1 | 6 | 2013 | 2 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 7000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:55:02 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Gihinga |  |  | 0 | 850 | 6572 | 15 | 438.1333 | 850 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 1 | 2016 | 1 | 3 | 576000 | 135.5294 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 2 | 2016 | 1 | 1 | 6 |  | 2016 | 1 | 1 | 1 | 2016 | 1 | 1000 | 1 | 3 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 06:11:05 CET | Rwanda | Rulindo | Rukozo | Bwimo | Gatiba |  |  | Gihanga II | 151 | 0 | 5 | 0 | 151 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2012 | 1 | 15 | 115200 | 152.5828 | 1 | 1 | 1 | 2016 | 1 | 7000 | 1 | 3 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 18:17:08 CET | Rwanda | Rulindo | Kinihira | Butunzi | Kiniihira |  |  | Miyove- Kinihira | 118 | 10452 | 4 | 2613 | 60 | 58 | 50.85% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 1152 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1989 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 09-03-2017 20:34:41 CET | Rwanda | Rulindo | Shyorongi | Rubona | Kigali |  |  | Gisoro- Nyundo network | 220 | 2297 | 10 | 229.7 | 25 | 195 | 11.36% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 13 | 132923.0769 | 1063.3846 | 1 | 1 | 1 | 2013 | 1 | 30 | 1 | 6 | 2013 | 2 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 7000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 12:32:19 CET | Rwanda | Rulindo | Buyoga | Mwumba | Gakoma |  |  | Water point at Gakoma/Nyirambuga pumping | 176 | 30604 | 1 | 30604 | 176 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 490.9091 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 04-06-2017 07:40:17 CEST | Rwanda | Rulindo | Kisaro | Mubuga | Rutabo |  |  | gahama | 148 | 10234 | 11 | 930.3636 | 120 | 28 | 81.08% | 0 | 0 | 1 | Piped Network With Pump | 2017 |  | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2017 | 1 | 65 | 26584.6154 | 44.3077 | 1 | 1 | 1 | 2017 | 1 | 12000 | 1 | 2012 | 2012 | 1 | 0 |  |  |  |  | 1 | 2 | 2012 | 1 | 12000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 07:29:19 CET | Rwanda | Rulindo | Ngoma | Mugote | Kiboha |  |  | Kabarore-Ngoma- Nyabuko network | 74 | 8284 | 1 | 8284 | 35 | 39 | 47.3% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 1 | 4 | 432000 | 2468.5714 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 4 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 1 | Yes | 1 | 10 | 0 | 10 | 1 | 1
2017 | 07-03-2017 11:09:04 CET | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 118 | 911 | 5 | 182.2 | 32 | 86 | 27.12% | 0 | 1 | 1 | Piped Network -- Gravity Only | 1997 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | Start And Collection Chamber | 2 | 2016 | 1 | 30 | 57600 | 360 | 1 | 1 | 1 | 2016 | 1 | 700 | 1 | 1 | 2016 | 1 | 1 | 2 | Washout And Air Release Chambers | 2016 | 1 | 1 | 2 | 2016 | 1 | 800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 20:49:35 CET | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  | Kibuye | 186 | 1232 | 3 | 410.6667 | 37 | 149 | 19.89% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | Start And Collection Chamber | 2 | 2016 | 1 | 45 | 38400 | 207.5676 | 1 | 1 | 1 | 2016 | 1 | 1500 | 0 |  |  |  | 1 | 1 | Washout Chamber | 2016 | 1 | 1 | 1 | 2016 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-04-2017 23:32:30 CEST | Rwanda | Rulindo | Rusiga | Gako | Gifumba |  |  | Gifumba gravity system | 188 | 0 | 1 | 0 | 188 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2010 | Local Government | Spring | 1 | 1 | 0 |  |  |  |  | 50 | 34560 | 36.766 | 1 | 1 | 1 | 2010 | 3 | 700 | 1 | 1 | 2010 | 2 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  | 2010 | 3 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 22-03-2017 14:32:00 CET | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point/AEP Kigarama gravity | 243 | 2621 | 3 | 873.6667 | 243 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 35.5556 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 15:07:32 CET | Rwanda | Rulindo | Bushoki | Gasiza | Ruhanga |  |  | Ruhanga2 water point/Tare-Rusiga pumping | 147 | 9577 | 1 | 9577 | 147 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 10 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 58.7755 | 1 | 1 | 1 | 2015 | 1 | 4000 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 3 | 2015 | 1 | 8000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:48:57 CET | Rwanda | Rulindo | Mbogo | Rurenge | Gicumbi |  |  | Musenge Network | 141 | 6074 | 29 | 209.4483 | 35 | 106 | 24.82% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 2223.9382 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber¦Washout And Air Release Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 06:48:53 CET | Rwanda | Rulindo | Ngoma | Munyarwanda | Ngaru |  |  | Kabarore-Ngoma-Nyabuko network | 106 | 8284 | 14 | 591.7143 | 56 | 50 | 52.83% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 1 | 4 | 432000 | 1542.8571 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 4 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 2 | Yes | 1 | 10 | 0 | 10 | 1 | 1
2017 | 09-03-2017 06:43:17 CET | Rwanda | Rulindo | Shyorongi | Kijabagwe | Kabagabaga |  |  | kirikumuryango network | 850 | 0 | 26 | 0 | 850 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 36.9626 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse ,Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 14:37:41 CEST | Rwanda | Rulindo | Mbogo | Bukoro | Karindi |  |  |  | 120 | 510 | 31 | 16.4516 | 45 | 75 | 37.5% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2007 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 180 | 9600 | 42.6667 | 1 | 1 | 1 | 2007 | 1 | 1000 | 1 | 1 | 1998 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 10:31:03 CET | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 118 | 911 | 5 | 182.2 | 21 | 97 | 17.8% | 0 | 1 | 1 | Piped Network -- Gravity Only | 1997 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | Start And Collection Chamber | 2 | 2016 | 1 | 30 | 57600 | 548.5714 | 1 | 1 | 1 | 2016 | 1 | 700 | 1 | 1 | 2016 | 1 | 1 | 2 | Washout And Valve Chamber | 2016 | 1 | 1 | 2 | 2016 | 1 | 800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 12:05:56 CET | Rwanda | Rulindo | Murambi | Gatwa | Gatare |  |  | rwiseke | 179 | 9536 | 5 | 1907.2 | 179 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 0 |  |  |  |  | 55 | 31418.1818 | 35.1041 | 1 | 1 | 1 | 2001 | 1 | 1200 | 1 | 7 | 2001 | 1 | 0 |  |  |  |  | 1 | 1 | 2001 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2001 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 10:24:35 CET | Rwanda | Rulindo | Ngoma | Kabuga | Kirambo |  |  | Kabarore-Ngoma-Nyabuko network | 131 | 8284 | 14 | 591.7143 | 48 | 83 | 36.64% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 1 | 4 | 432000 | 1800 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 1 | Yes | 1 | 10 | 0 | 10 | 1 | 1
2017 | 11-03-2017 10:12:28 CET | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 50 | 20456 | 36 | 568.2222 | 45 | 5 | 90% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1536 | 1 | 1 | 2 | 2011 | 1 | 5 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 10 | 25 | 0 | 250 | 0 | 2
2017 | 11-03-2017 10:06:20 CET | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 450 | 20456 | 36 | 568.2222 | 450 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 153.6 | 1 | 1 | 2 | 2011 | 1 | 5 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 10 | 22 | 0 | 220 | 1 | 2
2017 | 13-03-2017 06:49:46 CET | Rwanda | Rulindo | Ngoma | Munyarwanda | Busizi |  |  | Kabarore-Ngoma-Nyabuko network | 100 | 8284 | 14 | 591.7143 | 21 | 79 | 21% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 1 | 4 | 432000 | 4114.2857 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 4 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 3 | Yes | 1 | 10 | 0 | 10 | 1 | 2
2017 | 28-03-2017 08:51:12 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Bikamba |  |  | Rwamugaza network | 205 | 14106 | 35 | 403.0286 | 205 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 561.9512 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 05:14:09 CET | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 1789 | 14 | 127.7857 | 180 | 12 | 93.75% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2012 | Padiri | Spring¦Groundwater (Well, Etc.) | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 1 | 30 | 57600 | 64 | 1 | 1 | 1 | 2016 | 1 | 6450 | 1 | 2 | 2012 | 1 | 1 | 2 | Distribution Chamber | 2012 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 25-03-2017 11:21:50 CET | Rwanda | Rulindo | Masoro | Shengampuri | Umubuga |  |  | Mutagata Gravity network | 175 | 26296 | 12 | 2191.3333 | 63 | 112 | 36% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2004 | 2 | 8 | 216000 | 685.7143 | 1 | 1 | 1 | 2004 | 2 | 3500 | 1 | 6 | 2004 | 2 | 1 | 4 | Distribution Chamber¦Washout And Air Release | 2004 | 2 | 1 | 2 | 2004 | 2 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 12 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 13-03-2017 21:09:46 CET | Rwanda | Rulindo | Base | Gitare | Gihora |  |  | Gihora2 water point/Rutomvu gravity | 101 | 3015 | 2 | 1507.5 | 101 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 85.5446 | 1 | 0 |  |  |  |  | 1 | 1 | 2013 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 01:22:57 CET | Rwanda | Rulindo | Tumba | Gahabwa | Kagusa |  |  | Kagusa water point/Nyirambuga pumping | 146 | 30604 | 1 | 30604 | 146 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 591.7808 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 14:01:28 CET | Rwanda | Rulindo | Kinihira | Karegamazi | Buhita |  |  | Miyove-Kinihira | 131 | 10452 | 19 | 550.1053 | 60 | 71 | 45.8% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 1152 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 12-03-2017 13:19:37 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Muvumu |  |  | Muvumu- Taba | 400 | 0 | 10 | 0 | 400 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 25 | 69120 | 34.56 | 1 | 1 | 1 | 2013 | 1 | 800 | 1 | 3 | 2013 | 2 | 1 | 9 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 7500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | Yes | 1 | 3 | 0 | 3 | 1 | 2
2017 | 10-03-2017 13:13:09 CET | Rwanda | Rulindo | Bushoki | Mukoto | Marembo |  |  | Water point at Marembo school/Tare-Rusiga pumping | 90 | 9577 | 1 | 9577 | 90 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 10 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 96 | 1 | 1 | 1 | 2015 | 1 | 4000 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 8000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 14:37:25 CET | Rwanda | Rulindo | Bushoki | Gasiza | Ruhanga |  |  | Ruhanga center Water point/Tare-Rusiga pumping | 147 | 9577 | 1 | 9577 | 147 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 10 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 58.7755 | 1 | 1 | 1 | 2015 | 1 | 4000 | 0 |  |  |  | 0 |  |  |  |  | 1 | 3 | 2015 | 1 | 8000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2015 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 21:12:55 CET | Rwanda | Rulindo | Bushoki | Giko | Rugote |  |  | Rugote water point/Rutomvu gravity system | 147 | 3015 | 1 | 3015 | 147 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 58.7755 | 1 | 0 |  |  |  |  | 1 | 1 | 2013 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-04-2017 07:11:34 CEST | Rwanda | Rulindo | Murambi | Mugambazi | Gashinge |  |  | Mutagata motorised network | 229 | 26296 | 49 | 536.6531 | 149 | 80 | 65.07% | 0 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 463.8926 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release Chamber | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-04-2017 14:42:46 CEST | Rwanda | Rulindo | Buyoga | Gitumba | Rutabo |  |  |  | 128 | 0 | 31 | 0 | 80 | 48 | 62.5% | 0 | 1 | 1 | Piped Network With Pump | 2014 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 1440 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 11 | 2014 | 1 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 9000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:45:32 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Gihinga |  |  | 0 | 850 | 6572 | 15 | 438.1333 | 850 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 1 | 2016 | 1 | 3 | 576000 | 135.5294 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 2 | 2016 | 1 | 1 | 6 |  | 2016 | 2 | 1 | 1 | 2016 | 1 | 1000 | 1 | 3 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 12:26:49 CET | Rwanda | Rulindo | Mbogo | Mushali | Nyakabuye |  |  | Matyazo network | 147 | 0 | 4 | 0 | 147 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 4 | 2016 | 1 | 17 | 101647.0588 | 138.2953 | 1 | 1 | 1 | 2016 | 1 | 4300 | 1 | 1 | 2016 | 1 | 1 | 2 | Air Release Chamber, Washout Chamber | 2016 | 1 | 1 | 1 | 2016 | 1 | 1800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2016 | 3 | Yes | 1 | 30 | 0 | 30 | 0 | 2
2017 | 12-03-2017 07:19:35 CET | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Nyamagana | 100 | 20456 | 36 | 568.2222 | 95 | 5 | 95% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 727.5789 | 1 | 1 | 2 | 2011 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 1 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 7 | 25 | 0 | 175 | 1 | 2
2017 | 15-03-2017 05:14:18 CET | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 1789 | 14 | 127.7857 | 180 | 12 | 93.75% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2012 | Padiri | Spring¦Groundwater (Well, Etc.) | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring¦Well | 2 | 2016 | 1 | 30 | 57600 | 64 | 1 | 1 | 1 | 2016 | 1 | 6450 | 1 | 3 | 2012 | 1 | 1 | 2 | Distribution Chamber | 2016 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 04:51:27 CET | Rwanda | Rulindo | Shyorongi | Kijabagwe | Kabagabaga |  |  | kirikumuryango network | 181 | 0 | 26 | 0 | 75 | 106 | 41.44% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 418.9091 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse,Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 22:55:11 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Rutonde |  |  | kirikumuryango network | 241 | 0 | 26 | 0 | 98 | 143 | 40.66% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 320.5937 | 1 | 1 | 1 | 2013 | 1 | 11 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-04-2017 22:04:20 CEST | Rwanda | Rulindo | Base | Gitare | Mugenda I |  |  | Gitare center water point/Nyirambuga pumping system | 117 | 30604 | 1 | 30604 | 117 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Local Government | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 738.4615 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 09-03-2017 11:06:38 CET | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Gasiza center water point served by gravity before Tare pumping | 228 | 9577 | 1 | 9577 | 228 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Gvt And Water For People | Spring | 8 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 37.8947 | 1 | 1 | 1 | 2015 | 1 | 4000 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 2000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 17-03-2017 05:22:57 CET | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 135 | 6074 | 29 | 209.4483 | 67 | 68 | 49.63% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1161.7588 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Washout And Air Release Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 20:29:26 CET | Rwanda | Rulindo | Shyorongi | Rubona | Nyarunyinya |  |  | kinywamagana pumping network | 132 | 6436 | 26 | 247.5385 | 92 | 40 | 69.7% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 375.6522 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 1 | 3
2017 | 08-03-2017 23:02:18 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Rutonde |  |  | kirikumuryango network | 1350 | 0 | 26 | 0 | 1350 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 23.2727 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-04-2017 21:50:47 CEST | Rwanda | Rulindo | Base | Gitare | Mugenda I |  |  | Gitare cell water point/Nyirambuga pumping system | 117 | 30604 | 1 | 30604 | 117 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 4 | 432000 | 738.4615 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 6 | 2012 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 28-03-2017 10:25:40 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza network | 229 | 14106 | 35 | 403.0286 | 229 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 503.0568 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 11-03-2017 09:24:23 CET | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Nyamagana | 850 | 20456 | 36 | 568.2222 | 850 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 81.3176 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 10 | 22 | 0 | 220 | 1 | 2
2017 | 24-03-2017 15:49:45 CET | Rwanda | Rulindo | Buyoga | Butare | Ryanyirakayobe |  |  | Nyagahera | 96 | 0 | 4 | 0 | 80 | 16 | 83.33% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 16 | 108000 | 270 | 1 | 1 | 1 | 2014 | 1 | 6800 | 1 | 3 | 2014 | 1 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 09:17:43 CEST | Rwanda | Rulindo | Kisaro | Kamushenyi | Amahoro |  |  | Gicumbi Mutete network | 109 | 0 | 1 | 0 | 109 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 2009 | Government | Spring | 3 | 1 | 1 |  | 1 | 2009 | 1 | 30 | 57600 | 105.6881 | 1 | 1 | 2 | 2009 | 1 | 30000 | 1 | 5 | 2009 | 1 | 1 | 10 |  | 2009 | 1 | 1 | 2 | 2009 | 1 | 30000 | 1 | 1 | 2009 | 2 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2009 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 21:20:14 CET | Rwanda | Rulindo | Bushoki | Giko | Cyili |  |  | Rutomvu source catchment area and intake structures | 169 | 3015 | 1 | 3015 | 169 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2013 | 1 | 40 | 43200 | 51.1243 | 1 | 1 | 1 | 2013 | 1 | 100 | 1 | 1 | 2013 | 1 | 0 |  |  |  |  | 1 | 2 | 2013 | 1 | 2000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 10:21:55 CEST | Rwanda | Rulindo | Tumba | Nyirabirori | Gihanga |  |  | Water point at Rusura Primary school/Nyirambuga pumping | 152 | 30604 | 1 | 30604 | 152 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 454.7368 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:50:19 CET | Rwanda | Rulindo | Mbogo | Bukoro | Kalindi |  |  | Musenge Network | 120 | 6074 | 29 | 209.4483 | 65 | 55 | 54.17% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Wfp | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1197.5052 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber¦Washout And Air Release | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 3 | Yes | 8 | 30 | 0 | 240 | 0 | 3
2017 | 21-03-2017 15:02:15 CET | Rwanda | Rulindo | Kinihira | Rebero | Ndusu |  |  | Miyove-Kinihira | 146 | 10452 | 19 | 550.1053 | 60 | 86 | 41.1% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 1152 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 08-03-2017 22:16:46 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Mwagiro |  |  | Kirikumuryango network | 139 | 0 | 26 | 0 | 50 | 89 | 35.97% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 628.3636 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 07:41:57 CET | Rwanda | Rulindo | Masoro | Kabuga | Karambi |  |  | Mutagata motorised network | 127 | 26296 | 49 | 536.6531 | 127 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 544.252 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 22:16:58 CET | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Buramira water point/Buramira gravity | 104 | 1255 | 1 | 1255 | 104 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Gor | Spring | 2 | 1 | 0 |  |  |  |  | 30 | 57600 | 110.7692 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 20:43:19 CET | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | kinywamagana pumping network | 281 | 6436 | 26 | 247.5385 | 80 | 201 | 28.47% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 432 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 08-03-2017 19:50:43 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Kigarama |  |  | kinywamagana pumping network | 233 | 6436 | 26 | 247.5385 | 69 | 164 | 29.61% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 500.8696 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 07-03-2017 12:05:42 CET | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 118 | 911 | 5 | 182.2 | 31 | 87 | 26.27% | 0 | 1 | 1 | Piped Network -- Gravity Only | 1997 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | Start And Collection Chamber | 2 | 2016 | 1 | 30 | 57600 | 371.6129 | 1 | 1 | 1 | 2016 | 1 | 700 | 1 | 1 | 2016 | 1 | 1 | 2 | Washout And Air Release Chamber | 2016 | 1 | 1 | 2 | 2016 | 1 | 800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 16-03-2017 07:34:17 CET | Rwanda | Rulindo | Burega | Karengeli | Kiziba |  |  | Rwamugaza | 400 | 14106 | 38 | 371.2105 | 400 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 2 | 2003 | 1 | 3.5 | 493714.2857 | 246.8571 | 1 | 1 | 1 | 2003 | 1 | 8000 | 1 | 20 | 2003 | 1 | 1 | 16 |  | 2003 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 23-04-2017 14:44:03 CEST | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | nyiragahera | 151 | 0 | 1 | 0 | 105 | 46 | 69.54% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 1097.1429 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 11 | 2014 | 1 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 18:52:55 CET | Rwanda | Rulindo | Base | Rwamahwa | Mutima |  |  | Rutare I | 169 | 345 | 5 | 69 | 140 | 29 | 82.84% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 123.4286 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 11:25:37 CET | Rwanda | Rulindo | Base | Cyohoha | Buramba |  |  | Gihanga | 163 | 2456 | 10 | 245.6 | 120 | 43 | 73.62% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 15 | 115200 | 192 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 07:29:27 CET | Rwanda | Rulindo | Murambi | Mugambazi | Kigarama |  |  | Mutagata motorised network | 169 | 26296 | 49 | 536.6531 | 47 | 122 | 27.81% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1470.6383 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 11:01:57 CET | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 1789 | 14 | 127.7857 | 100 | 92 | 52.08% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2012 | Padiri | Spring | 3 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 50 | 34560 | 69.12 | 1 | 1 | 1 | 2012 | 1 | 6450 | 1 | 1 | 2 | 1 | 1 | 3 | Distribution Chamber | 2017 | 1 | 1 | 2 | 2012 | 1 | 6800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-04-2017 14:42:39 CEST | Rwanda | Rulindo | Buyoga | Gahororo | Gitabura |  |  | kiruruma | 129 | 8295 | 25 | 331.8 | 96 | 33 | 74.42% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 1200 | 1 | 1 | 4 | 2014 | 1 | 9000 | 1 | 4 | 20147 | 1 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 9633 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 14-04-2017 22:18:55 CEST | Rwanda | Rulindo | Bushoki | Mukoto | Gatare |  |  | Nkombe gravity system catchment area | 129 | 0 | 1 | 0 | 129 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2002 | Coforwa | Spring¦Lake/Reservoir | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring |  | 2002 | 1 | 18 | 96000 | 148.8372 | 1 | 1 | 3 | 2002 | 1 | 100 | 1 | 1 | 2002 | 1 | 0 |  |  |  |  | 1 | 1 | 2002 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2002 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 06:10:52 CET | Rwanda | Rulindo | Rukozo | Bwimo | Gatiba |  |  | Gihanga II | 151 | 0 | 5 | 0 | 151 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 15 | 115200 | 152.5828 | 1 | 1 | 1 | 2016 | 1 | 7000 | 1 | 3 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 21:44:00 CET | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Water point at GS Ngarama/Rutumvo gravity | 172 | 0 | 1 | 0 | 172 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 50.2326 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 21:22:46 CET | Rwanda | Rulindo | Bushoki | Giko | Cyili |  |  | Cyili2 water point/Rutomvu gravity | 169 | 3015 | 1 | 3015 | 169 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 51.1243 | 1 | 0 |  |  |  |  | 1 | 1 | 2013 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 1 | 3
2017 | 16-03-2017 06:29:08 CET | Rwanda | Rulindo | Burega | Taba | Nyagisozi |  |  | Rwamugaza | 505 | 14106 | 38 | 371.2105 | 505 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 2 | 2009 | 1 | 4.5 | 384000 | 152.0792 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 28-03-2017 08:58:31 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Gatobotobo |  |  | Rwamugaza network | 103 | 14106 | 35 | 403.0286 | 103 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 1118.4466 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 28-03-2017 08:45:12 CEST | Rwanda | Rulindo | Ntarabana | Mahaza | Rugogwe |  |  | Rwamugaza network | 192 | 14106 | 35 | 403.0286 | 192 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 600 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 16:52:08 CET | Rwanda | Rulindo | Rusiga | Gako | Kabunigu |  |  | Gako-Kabunigo water point/Tare-Rusiga pumping | 219 | 9577 | 1 | 9577 | 219 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 10 | 1 | 0 |  |  |  |  | 40 | 43200 | 39.4521 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 23:21:15 CET | Rwanda | Rulindo | Tumba | Gahabwa | Rushaki |  |  | Water point at Marembo center/Nyirambuga pumping | 152 | 30604 | 1 | 30604 | 152 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 568.4211 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 12:48:41 CET | Rwanda | Rulindo | Buyoga | Karama | Cyasenga |  |  | Water point at Cyasenga/Nyirambuga pumping | 165 | 30604 | 1 | 30604 | 165 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 523.6364 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 17:08:53 CET | Rwanda | Rulindo | Kinihira | Rebero | Kirwa |  |  | Miyove-Kinihira | 187 | 10452 | 19 | 550.1053 | 80 | 107 | 42.78% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 864 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 22-03-2017 20:16:33 CET | Rwanda | Rulindo | Murambi | Mvuzo | Rurama |  |  | Mutagata Motorised Network | 155 | 26296 | 49 | 536.6531 | 52 | 103 | 33.55% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1329.2308 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 00:23:34 CET | Rwanda | Rulindo | Tumba | Taba | Nyirataba |  |  | Water point at Nyirataba/Nyirambuga pumping | 169 | 30604 | 1 | 30604 | 169 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 511.2426 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 10:46:06 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Rwamugaza network | 193 | 14106 | 35 | 403.0286 | 193 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 596.8912 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 11-03-2017 10:18:28 CET | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 45 | 20456 | 36 | 568.2222 | 30 | 15 | 66.67% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 2304 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 2 | Yes | 10 | 22 | 0 | 220 | 0 | 2
2017 | 07-03-2017 12:27:42 CET | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 1789 | 14 | 127.7857 | 100 | 92 | 52.08% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2012 | Padiri | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 20 | 86400 | 172.8 | 1 | 1 | 2 | 2012 | 1 | 6450 | 1 | 3 | 2012 | 1 | 1 | 2 | Distribution Chamber | 2012 | 1 | 1 | 2 | 2017 | 2 | 1500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | Yes | 365 | 0 | 0 | 0 | 0 | 3
2017 | 23-03-2017 08:03:05 CET | Rwanda | Rulindo | Murambi | Mugambazi | Amahoro |  |  | Mutagata motorised network | 120 | 26296 | 49 | 536.6531 | 120 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 576 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 25-03-2017 20:47:52 CET | Rwanda | Rulindo | Buyoga | Butare | Gasave |  |  | KIDUHA | 114 | 0 | 7 | 0 | 100 | 14 | 87.72% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2007 | Italians(Lake Angels) | Groundwater (Well, Etc.) | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 2 | 20 | 86400 | 172.8 | 1 | 1 | 1 | 2007 | 2 | 2200 | 1 | 3 | 2007 | 1 | 0 |  |  |  |  | 1 | 1 | 2007 | 2 | 2200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 23-03-2017 06:39:19 CET | Rwanda | Rulindo | Kinihira | Marembo | Kigali |  |  | Nyamagana-Kinihira | 189 | 0 | 15 | 0 | 60 | 129 | 31.75% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1152 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 06:47:46 CET | Rwanda | Rulindo | Kinihira | Marembo | Kigali |  |  | Nyamagana- Kinihira | 189 | 0 | 4 | 0 | 70 | 119 | 37.04% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 987.4286 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 11:06:26 CET | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo |  |  | marenge | 203 | 5544 | 14 | 396 | 203 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1998 |  | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 85.1232 | 1 | 1 | 1 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 1 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 17:37:11 CET | Rwanda | Rulindo | Kinihira | Karegamazi | Bwishya |  |  | Miyove-Kinihira | 181 | 10452 | 19 | 550.1053 | 60 | 121 | 33.15% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 1152 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1989 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 07-03-2017 14:13:53 CET | Rwanda | Rulindo | Mbogo | Bukoro | Ruhanya |  |  | Mutungo | 102 | 510 | 3 | 170 | 50 | 52 | 49.02% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 1 | 0 | 0 |  |  |  |  | 24 | 72000 | 288 | 1 | 1 | 1 | 2004 | 1 | 500 | 1 | 2 | 2004 | 2 | 0 |  |  |  |  | 1 | 1 | 2004 | 2 | 2000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2004 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 15-04-2017 16:33:48 CEST | Rwanda | Rulindo | Cyungo | Burehe | Gitandi |  |  | Nyamagana | 40 | 20456 | 36 | 568.2222 | 35 | 5 | 87.5% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 120 | 14400 | 82.2857 | 1 | 1 | 1 | 2011 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 1 | 2011 | 1 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 2 | Yes | 15 | 30 | 0 | 450 | 0 | 2
2017 | 16-03-2017 08:34:25 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kanyoni |  |  | 0 | 640 | 6572 | 15 | 438.1333 | 640 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 1 | 2016 | 1 | 3 | 576000 | 180 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 10 | 2016 | 1 | 1 | 8 |  | 2016 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 3 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-04-2017 16:26:12 CEST | Rwanda | Rulindo | Rusiga | Taba | Gahondo |  |  | Gahondo water point chez Safari/Bitare-Gahondo gravity | 83 | 9577 | 1 | 9577 | 83 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 1989 | Catholic Church | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2017 | 1 | 10 | 172800 | 416.3855 | 1 | 1 | 2 | 2017 | 1 | 400 | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1989 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 07-03-2017 11:45:45 CET | Rwanda | Rulindo | Mbogo | Mushali | Buraro |  |  | Matyazo network | 155 | 0 | 4 | 0 | 55 | 100 | 35.48% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 4 | 2016 | 1 | 17 | 101647.0588 | 369.6257 | 1 | 1 | 1 | 2016 | 1 | 4300 | 1 | 1 | 2016 | 1 | 1 | 2 | Air Release Chamber, Washout Chamber | 2016 | 1 | 1 | 1 | 2016 | 1 | 1800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 05:51:32 CET | Rwanda | Rulindo | Cyungo | Burehe | Sove |  |  | Nyamagana | 30 | 20456 | 36 | 568.2222 | 15 | 15 | 50% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 4608 | 1 | 1 | 2 | 2015 | 2 | 2100 | 1 | 29 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 2 | Yes | 10 | 30 | 0 | 300 | 0 | 2
2017 | 24-03-2017 12:47:07 CET | Rwanda | Rulindo | Masoro | Nyamyumba | Kigomwa |  |  | marenge | 118 | 5544 | 14 | 396 | 118 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 1 | 20 | 86400 | 146.4407 | 1 | 1 | 2 | 2016 | 1 | 500 | 1 | 15 | 2016 | 1 | 1 |  | Sedimentation Tank | 2016 | 1 | 1 | 2 | 2016 | 1 | 500 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 1 | Filtration | 2016 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 19:44:51 CET | Rwanda | Rulindo | Shyorongi | Rubona | Kigali |  |  | Gisoro- Nyundo network | 220 | 2297 | 10 | 229.7 | 110 | 110 | 50% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 13 | 132923.0769 | 241.6783 | 1 | 1 | 1 | 2013 | 1 | 30 | 1 | 6 | 2013 | 2 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 7000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:41:47 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Gatagara |  |  | 0 | 725 | 6572 | 15 | 438.1333 | 725 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 1 | 2016 | 1 | 3 | 576000 | 158.8966 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 10 | 2016 | 1 | 1 | 6 |  | 2016 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 3 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 11:58:22 CET | Rwanda | Rulindo | Bushoki | Mukoto | Rusave |  |  | Rusave water point/Tare-Rusiga pumping | 101 | 567 | 1 | 567 | 101 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 8 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 85.5446 | 1 | 1 | 1 | 2015 | 1 | 4000 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 8000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 10:34:23 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Mukumba |  |  | Bitete-Muvumu | 92 | 1316 | 7 | 188 |  | 92 |  | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 |  | 0 | 1 | 1 | 2013 | 2 | 1000 | 1 | 4 | 2013 | 1 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 2 | 1 | 1 | 2013 | 1 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 07-03-2017 09:42:53 CET | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 118 | 911 | 5 | 182.2 | 25 | 93 | 21.19% | 0 | 1 | 1 | Piped Network -- Gravity Only | 1997 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | Start Chamber And Collection Chamber | 2 | 2016 | 1 | 30 | 57600 | 460.8 | 1 | 1 | 1 | 2016 | 1 | 700 | 1 | 1 | 2016 | 1 | 1 | 2 | Washout And Valve Chamber | 2016 | 1 | 1 | 2 | 2016 | 1 | 800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 14:09:05 CET | Rwanda | Rulindo | Murambi | Mvuzo | Kabuga |  |  |  | 199 | 0 | 31 | 0 | 199 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2001 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 14 | 123428.5714 | 124.0488 | 1 | 1 | 1 | 2001 | 1 | 12000 | 1 | 7 | 2001 | 1 | 0 |  |  |  |  | 1 | 1 | 2001 | 1 | 12000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 7 | 2001 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 08:54:33 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Gatobotobo |  |  | Rwamugaza network | 103 | 14106 | 35 | 403.0286 | 103 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 1118.4466 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 23-03-2017 07:35:26 CET | Rwanda | Rulindo | Masoro | Kabuga | Kanunga |  |  | Mutagata motorised network | 143 | 26296 | 49 | 536.6531 | 68 | 75 | 47.55% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1016.4706 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 10:54:02 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Karama |  |  | Bitete-Muvumu | 121 | 1316 | 7 | 188 | 45 | 76 | 37.19% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 698.1818 | 1 | 1 | 1 | 2013 | 2 | 1000 | 1 | 4 | 2013 | 1 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 2 | 1 | 1 | 2013 | 1 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 10:24:13 CET | Rwanda | Rulindo | Ngoma | Kabuga | Nyabuko |  |  | Kabarore-Ngoma-Nyabuko network | 122 | 8284 | 14 | 591.7143 | 35 | 87 | 28.69% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 2 | 4 | 432000 | 2468.5714 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 14 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 11:04:05 CET | Rwanda | Rulindo | Mbogo | Mushali | Gitaba |  |  | Matyazo network | 118 | 0 | 4 | 0 | 100 | 18 | 84.75% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 4 | 2016 | 1 | 17 | 101647.0588 | 203.2941 | 1 | 1 | 1 | 2016 | 1 | 4300 | 1 | 1 | 2016 | 1 | 1 | 2 | Air Release Chamber, Washout Chamber | 2016 | 1 | 1 | 1 | 2016 | 1 | 1800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2016 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 14-04-2017 21:14:54 CEST | Rwanda | Rulindo | Bushoki | Kayenzi | Gitaba |  |  | Rutembe catchment area | 118 | 673 | 1 | 673 | 118 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Rulindo District | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 20 | 86400 | 146.4407 | 1 | 1 | 1 | 2015 | 1 | 100 | 1 | 1 | 2015 | 1 | 1 | 1 | Overflow Where People Are Currently Fetching Due To Water Point That Has No Sufficient Water | 2015 | 1 | 1 | 1 | 2015 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 04:40:01 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Rutonde |  |  | kirikumuryango network | 241 | 0 | 26 | 0 | 150 | 91 | 62.24% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 209.4545 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 06:25:11 CET | Rwanda | Rulindo | Buyoga | Gitumba | Munini |  |  | Kiruruma | 158 | 8295 | 25 | 331.8 | 153 | 5 | 96.84% | 1 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 752.9412 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 15 | 2014 | 1 | 1 | 5 | Pressure Break Tank | 2014 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 20:42:08 CET | Rwanda | Rulindo | Mbogo | Bukoro | Kibaya |  |  | Mutungo | 133 | 510 | 3 | 170 | 60 | 73 | 45.11% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 1 | 0 | 0 |  |  |  |  | 24 | 72000 | 240 | 1 | 1 | 1 | 2004 | 2 | 2000 | 1 | 2 | 2004 | 2 | 0 |  |  |  |  | 1 | 1 | 2004 | 2 | 2000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2004 | 3 | Yes | 5 | 15 | 0 | 75 | 0 | 3
2017 | 15-03-2017 14:20:10 CET | Rwanda | Rulindo | Cyinzuzi | Migendezo | Gitabage |  |  | 0 | 735 | 14106 | 15 | 940.4 | 735 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2009 | Umushinga Witwa Ema | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2009 | 1 | 4.5 | 384000 | 104.4898 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 16 | 2009 | 1 | 1 | 23 | Vantouse | 2009 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2009 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 11:57:50 CET | Rwanda | Rulindo | Bushoki | Gasiza | Budaha |  |  | Water point at Budaha nearby pumping station/Tare pumping | 205 | 9577 | 1 | 9577 | 205 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Gvt And Water For People | Spring | 8 | 1 | 0 |  |  |  |  | 40 | 43200 | 42.1463 | 1 | 1 | 1 | 2015 | 1 | 4000 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 2000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 05:53:47 CET | Rwanda | Rulindo | Base | Cyohoha | Kabingo |  |  | Nyamagana | 70 | 20456 | 36 | 568.2222 | 60 | 10 | 85.71% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1152 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 07:35:30 CET | Rwanda | Rulindo | Base | Rwamahwa | Kiruli |  |  | Migogo | 129 | 558 | 10 | 55.8 | 120 | 9 | 93.02% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2009 | Italians(Lake Angels) | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2009 | 1 | 20 | 86400 | 144 | 1 | 0 |  |  |  |  | 1 | 3 | 2009 | 2 | 0 |  |  |  |  | 1 | 2 | 2009 | 2 | 3000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2009 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 28-03-2017 11:46:09 CEST | Rwanda | Rulindo | Ngoma | Mugote | Sakara |  |  | Kararama pumping network | 99 | 6572 | 3 | 2190.6667 | 99 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2007 | Government | Spring | 4 | 0 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 3 | 2007 | 2 | 6 | 288000 | 581.8182 | 1 | 1 | 1 | 2007 | 1 | 1500 | 1 | 25 | 2007 | 1 | 1 | 20 | Distribution Chamber¦Washout And Air Release Chamber | 2007 | 1 | 1 | 4 | 2007 | 1 | 30000 | 1 | 2 | 2007 | 2 | 1 | 2007 | 2 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 47 | 2007 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 28-03-2017 08:38:13 CEST | Rwanda | Rulindo | Ntarabana | Mahaza | Karera |  |  | Rwamugaza network | 182 | 14106 | 35 | 403.0286 | 182 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 632.967 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 06:27:42 CET | Rwanda | Rulindo | Buyoga | Gitumba | Nyarubuye |  |  | Kiruruma | 146 | 8295 | 25 | 331.8 | 140 | 6 | 95.89% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 822.8571 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 15 | 2014 | 1 | 1 | 5 | Pressure Break Tank | 2014 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 27-03-2017 08:20:58 CEST | Rwanda | Rulindo | Kisaro | Mubuga | Rutabo |  |  | Gahama Kisaro network | 740 | 10234 | 14 | 731 | 740 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 |  | 1 | 2012 | 1 | 3 | 576000 | 155.6757 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 |  | 2012 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 2 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 23-03-2017 06:28:33 CET | Rwanda | Rulindo | Buyoga | Gitumba | Munini |  |  | Kiruruma | 158 | 8295 | 25 | 331.8 | 150 | 8 | 94.94% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 2 | 864000 | 1152 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 15 | 2014 | 1 | 1 | 5 | Pressure Break Tank | 2014 | 1 | 1 | 3 | 2014 | 1 | 9000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 27-03-2017 08:43:53 CEST | Rwanda | Rulindo | Kisaro | Mubuga | Gako |  |  | Gahama Kisaro network | 955 | 10234 | 14 | 731 | 955 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 |  | 1 | 2012 | 1 | 3 | 576000 | 120.6283 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 |  | 2012 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 2 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 13-03-2017 22:13:55 CET | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Kivure source/Buramira gravity system | 134 | 1255 | 1 | 1255 | 134 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Gor | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 30 | 57600 | 85.9701 | 1 | 1 | 1 | 2015 | 1 | 100 | 1 | 2 | 2015 | 1 | 1 | 2 | Distribution Chamber | 2015 | 1 | 1 | 1 | 2015 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:50:19 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Rugaragara |  |  | charity water 203.033 | 815 | 6572 | 1 | 6572 | 815 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 1 | 2016 | 1 | 3 | 576000 | 141.3497 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 10 | 2016 | 1 | 1 | 6 |  | 2016 | 1 | 1 | 1 | 2016 | 1 | 1000 | 1 | 3 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 03:26:09 CET | Rwanda | Rulindo | Murambi | Mugambazi | Ruri |  |  | Mutagata Gravity network | 189 | 26296 | 12 | 2191.3333 | 40 | 149 | 21.16% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2004 | 2 | 8 | 216000 | 1080 | 1 | 1 | 1 | 2004 | 2 | 3500 | 1 | 6 | 2004 | 2 | 1 | 4 | Distribution Chamber¦Washout, Air Release Chamber | 2004 | 2 | 1 | 2 | 2004 | 2 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 12 | 2004 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 16-03-2017 07:15:57 CET | Rwanda | Rulindo | Burega | Butangampundu | Kigabiro |  |  | Rwamugaza | 565 | 14106 | 38 | 371.2105 | 565 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | 2 | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 135.9292 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 08:20:24 CET | Rwanda | Rulindo | Bushoki | N.Ngarama | Karambi |  |  | Nyabishengeshi source/Nyabishengeshi gravity system | 79 | 893 | 1 | 893 | 79 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Government | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2013 | 1 | 50 | 34560 | 87.4937 | 1 | 1 | 1 | 2013 | 1 | 1000 | 1 | 1 | 2013 | 1 | 0 |  |  |  |  | 1 | 4 | 2013 | 1 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 12:27:43 CET | Rwanda | Rulindo | Masoro | Nyamyumba | Rusenyi |  |  | marenge | 156 | 5544 | 14 | 396 | 156 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 20 | 86400 | 110.7692 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 07:19:52 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatimba |  |  | kinywamagana pumping network | 217 | 6436 | 26 | 247.5385 | 10 | 207 | 4.608% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 3456 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 16-03-2017 09:02:23 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kanyoni |  |  | charity water 203.037 | 640 | 6572 | 1 | 6572 | 640 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 1 | 2016 | 1 | 3 | 576000 | 180 | 1 | 1 | 1 | 2016 | 1 | 2000 | 1 | 3 | 2016 | 1 | 1 | 6 |  | 2016 | 1 | 1 | 1 | 2016 | 1 | 2000 | 1 | 3 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 04:54:41 CET | Rwanda | Rulindo | Rukozo | Mberuka | Mataba |  |  | Kabonanyoni | 75 | 7894 | 30 | 263.1333 | 70 | 5 | 93.33% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 329.1429 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-04-2017 23:17:04 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Kabirizi |  |  | Rwamugaza network | 148 | 14106 | 35 | 403.0286 | 148 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 778.3784 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 14 |  | 2003 | 1 | 1 | 1 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 10:10:42 CET | Rwanda | Rulindo | Murambi | Bubangu | Ruhunga |  |  | Mutagata Motorised Network | 112 | 26296 | 49 | 536.6531 | 112 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 617.1429 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 6 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:53:24 CET | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  | Musenge Network | 186 | 6074 | 29 | 209.4483 | 41 | 145 | 22.04% | 0 | 1 | 1 | Piped Network With Pump | 2014 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1898.4838 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 3 | Yes | 8 | 30 | 0 | 240 | 0 | 3
2017 | 24-04-2017 23:36:24 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyagasozi |  |  | Rwamugaza network | 197 | 14106 | 35 | 403.0286 | 197 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | Null | 1 | 2014 | 1 | 3 | 576000 | 584.7716 | 1 | 1 | 2 | 2014 | 1 | 35000 | 1 | 7 | 2014 | 1 | 1 | 14 |  | 2014 | 1 | 1 | 1 | 2014 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 2 | Yes | 2 | 120 | 0 | 240 | 0 | 2
2017 | 11-03-2017 09:10:48 CET | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Nyamagana | 850 | 20456 | 36 | 568.2222 | 850 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 81.3176 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 10 | 32 | 0 | 320 | 1 | 2
2017 | 12-03-2017 18:41:14 CET | Rwanda | Rulindo | Base | Gitare | Gisiza |  |  | Rwicanyoni | 116 | 698 | 7 | 99.7143 | 110 | 6 | 94.83% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 1 | 10 | 172800 | 314.1818 | 1 | 1 | 1 | 2016 | 1 | 8600 | 1 | 3 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 22:37:09 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Bugarura |  |  | kirikumuryango network | 119 | 0 | 26 | 0 | 61 | 58 | 51.26% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 515.0522 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:48:35 CET | Rwanda | Rulindo | Mbogo | Rurenge | Gicumbi |  |  | Musenge Network | 141 | 6074 | 29 | 209.4483 | 30 | 111 | 21.28% | 0 | 1 | 1 | Piped Network With Pump | 2014 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 2594.5946 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 05:08:15 CET | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 325 | 26296 | 49 | 536.6531 | 70 | 255 | 21.54% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 987.4286 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 12:58:05 CET | Rwanda | Rulindo | Cyungo | Marembo | Murambo |  |  | Mugomero Marembo | 161 | 3456 | 5 | 691.2 | 150 | 11 | 93.17% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 120 | 14400 | 19.2 | 0 | 1 | 2 | 2015 | 1 | 10000 | 1 | 10 | 2015 | 1 | 1 | 3 | Distribution Chamber | 2015 | 1 | 1 | 2 | 2015 | 1 | 10000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 14:08:20 CET | Rwanda | Rulindo | Rukozo | Buraro | Murwa |  |  | Kabonanyoni | 800 | 7894 | 30 | 263.1333 | 800 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 28.8 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 02:18:26 CET | Rwanda | Rulindo | Tumba | Barari | Gaseke |  |  | Water point at Rukore Primary School/Nyirambuga pumping | 149 | 30604 | 1 | 30604 | 149 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 579.8658 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 12:51:35 CET | Rwanda | Rulindo | Buyoga | Karama | Cyasenga |  |  | Water point at GS Kadendegere/Nyirambuga pumping | 165 | 30604 | 1 | 30604 | 165 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 523.6364 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 07:40:10 CET | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutembe | 229 | 1012 | 7 | 144.5714 | 200 | 29 | 87.34% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 2 | 50 | 34560 | 34.56 | 1 | 1 | 1 | 2016 | 2 | 4000 | 1 | 2 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 3 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 23-03-2017 08:07:07 CET | Rwanda | Rulindo | Murambi | Mvuzo | Iraro |  |  | Mutagata Motorised Network | 147 | 26296 | 49 | 536.6531 | 147 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 470.2041 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 20-04-2017 07:56:11 CEST | Rwanda | Rulindo | Tumba | Misezero | Taba |  |  | Water point chez Nsekanabo/Nyirambuga pumping | 100 | 30604 | 1 | 30604 | 100 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 691.2 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 16:43:06 CET | Rwanda | Rulindo | Base | Gitare | Nyamugali |  |  | Rutembe | 121 | 1012 | 7 | 144.5714 | 65 | 56 | 53.72% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 2 | 60 | 28800 | 88.6154 | 1 | 1 | 1 | 2017 | 2 | 2500 | 1 | 2 | 2016 | 3 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 3 | Yes | 1 | 300 | 0 | 300 | 0 | 3
2017 | 08-03-2017 22:08:43 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Mwagiro |  |  | Kirikumuryango network | 139 | 0 | 26 | 0 | 22 | 117 | 15.83% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 1428.0992 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse,Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 01:57:17 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Water point at EP Murambi Publique/Nyirambuga pumping | 174 | 30604 | 1 | 30604 | 174 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 496.5517 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 08:04:09 CET | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 214 | 2456 | 10 | 245.6 | 200 | 14 | 93.46% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 15 | 115200 | 115.2 | 1 | 1 | 1 | 2016 | 1 | 7200 | 1 | 6 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-04-2017 21:55:56 CEST | Rwanda | Rulindo | Base | Gitare | Mugenda I |  |  | Water point near Gitare school/Nyirambuga pumping system | 117 | 30604 | 1 | 30604 | 117 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 4 | 432000 | 738.4615 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 15-04-2017 22:12:54 CEST | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Water point2 at Gasiza market/Nyagahondo gravity system | 228 | 844 | 1 | 844 | 228 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2010 | Caritas | Spring | 1 | 1 | 0 |  |  |  |  | 30 | 57600 | 50.5263 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2010 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 27-03-2017 08:31:58 CEST | Rwanda | Rulindo | Kisaro | Murama | Ryarubuguza |  |  | Gahama Kisaro network | 495 | 10234 | 14 | 731 | 495 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 |  | 1 | 2012 | 1 | 3 | 576000 | 232.7273 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 |  | 2012 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 21-03-2017 14:18:22 CET | Rwanda | Rulindo | Rukozo | Mbuye | Kibare |  |  | Kabonanyoni | 90 | 7894 | 30 | 263.1333 | 85 | 5 | 94.44% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 271.0588 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-03-2017 14:26:02 CET | Rwanda | Rulindo | Rusiga | Taba | Nyakarama |  |  | Nyakarama water point/Nyakabizi gravity | 101 | 1259 | 1 | 1259 | 101 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 40 | 43200 | 85.5446 | 1 | 0 |  |  |  |  | 1 | 1 | 2013 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 14:50:42 CET | Rwanda | Rulindo | Kinihira | Karegamazi | Magezi |  |  | Miyove-Kinihira | 141 | 10452 | 19 | 550.1053 | 70 | 71 | 49.65% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 987.4286 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1989 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 23-03-2017 09:52:59 CET | Rwanda | Rulindo | Murambi | Gatwa | Amataba |  |  | Mutagata Motorised Network | 134 | 26296 | 49 | 536.6531 | 134 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2017 | 1 | 5 | 345600 | 515.8209 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 14-04-2017 22:21:42 CEST | Rwanda | Rulindo | Bushoki | Gasiza | Budaha |  |  | Nkombe water point/Nkombe gravity | 205 | 0 | 1 | 0 | 205 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2002 | Coforwa | Spring | 1 | 1 | 0 |  |  |  |  | 18 | 96000 | 93.6585 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2002 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 01:17:13 CET | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point at EP Tumba Public/Nyirambuga pumping | 115 | 30604 | 1 | 30604 | 115 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 751.3043 | 1 | 0 |  |  |  |  | 1 | 2 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 11:20:18 CET | Rwanda | Rulindo | Cyungo | Marembo | Gahinga |  |  | Mugomero Marembo | 652 | 3456 | 5 | 691.2 | 602 | 50 | 92.33% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 120 | 14400 | 4.7841 | 0 | 1 | 2 | 2015 | 1 | 10000 | 1 | 10 | 2015 | 1 | 1 | 3 | Distribution Chamber | 2015 | 1 | 1 | 2 | 2015 | 1 | 10000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 8 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 15:50:56 CET | Rwanda | Rulindo | Mbogo | Rurenge | Ruhondo |  |  | Kishwi network | 184 | 1309 | 4 | 327.25 | 41 | 143 | 22.28% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Goverment | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2003 | 1 | 25 | 69120 | 337.1707 | 1 | 1 | 2 | 2016 | 1 | 700 | 1 | 2 | 2003 | 1 | 0 |  |  |  |  | 1 | 2 | 2003 | 1 | 680 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2003 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 06-06-2017 21:15:01 CEST | Rwanda | Rulindo | Base | Cyohoha | Gihemba |  |  | kazabazana | 163 | 0 | 1 | 0 | 140 | 23 | 85.89% | 0 | 1 | 1 | Piped Network With Pump | 1998 |  | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 65 | 26584.6154 | 37.978 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 | Pressure Break Tank¦Distribution Chamber¦Washout,Air Release | 2012 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 12-03-2017 10:21:00 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Mukumba |  |  | Bitete-Muvumu | 92 | 1316 | 7 | 188 | 20 | 72 | 21.74% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 1570.9091 | 1 | 1 | 1 | 2013 | 2 | 1000 | 1 | 4 | 2013 | 1 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 2 | 1 | 4 | 2013 | 1 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 1 | 3
2017 | 19-03-2017 19:57:54 CET | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo |  |  | Cyaruzinge | 120 | 0 | 1 | 0 | 80 | 40 | 66.67% | 0 | 1 | 1 | Piped Network -- Gravity Only | 1998 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 3 | 60 | 28800 | 72 | 1 | 0 |  |  |  |  | 1 | 5 | 2017 | 1 | 1 | 8 | Distribution Chamber | 2017 | 2 | 0 |  |  |  |  | 1 | 2 | 2017 | 1 | 0 |  |  | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 06-06-2017 15:34:42 CEST | Rwanda | Rulindo | Kisaro | Kamushenyi | Gatete |  |  | gahama | 163 | 10234 | 11 | 930.3636 | 140 | 23 | 85.89% | 0 | 0 | 1 | Piped Network With Pump | 2012 |  | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 65 | 26584.6154 | 37.978 | 1 | 1 | 2 | 2012 | 1 | 12000 | 1 | 7 | 2012 | 1 | 1 | 14 | Pressure Break Tank¦Distribution Chamber¦Washout,Air Release | 2012 | 1 | 1 | 2 | 2012 | 1 | 12000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 16-03-2017 17:46:48 CET | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | Rwintare2 water point/Tare-Rusiga pumping | 281 | 9577 | 1 | 9577 | 281 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 30.7473 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 17-03-2017 05:23:31 CET | Rwanda | Rulindo | Mbogo | Rurenge | Munini |  |  | Musenge network | 111 | 6074 | 29 | 209.4483 | 62 | 49 | 55.86% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1255.449 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Washout And Air Release Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 10:41:02 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Kararama network | 193 | 6572 | 4 | 1643 | 193 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2009 | Umushinga Witwa Ema | Spring | 3 | 1 | 1 |  | 1 | 2009 | 1 | 4.5 | 384000 | 397.9275 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 7 | 2003 | 1 | 1 | 14 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 09-03-2017 07:15:41 CET | Rwanda | Rulindo | Shyorongi | Kijabagwe | Kabakene |  |  | kirikumuryango network | 99 | 0 | 26 | 0 | 99 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 317.3554 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-03-2017 14:35:13 CET | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point/AEP Kigarama gravity | 243 | 2621 | 3 | 873.6667 | 243 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 35.5556 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 08:25:40 CEST | Rwanda | Rulindo | Tumba | Nyirabirori | Rusura |  |  | Water point chez Senzoga/Nyirambuga pumping | 157 | 30604 | 1 | 30604 | 157 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 440.2548 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 08:43:37 CET | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 77 | 1458 | 6 | 243 | 70 | 7 | 90.91% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2005 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2005 | 1 | 60 | 28800 | 82.2857 | 1 | 1 | 1 | 2005 | 1 | 4500 | 1 | 1 | 2005 | 1 | 1 | 2 | Pressure Break Tank | 2016 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 04-06-2017 13:33:21 CEST | Rwanda | Rulindo | Kisaro | Murama | Mugomero |  |  | gahama | 129 | 10234 | 11 | 930.3636 | 100 | 29 | 77.52% | 0 | 0 | 1 | Piped Network With Pump | 2012 | Waterforpeople | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 15 | 115200 | 230.4 | 1 | 1 | 2 | 2012 | 1 | 12000 | 1 | 7 | 2012 | 1 | 1 | 14 | Pressure Break Tank¦Distribution Chamber¦Washout,Air Release | 2012 | 1 | 1 | 2 | 2012 | 1 | 12000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 01-01-2015 20:07:39 CET | Rwanda | Rulindo | Cyungo | Rwili | Kivumu |  |  | Sakara | 570 | 0 | 4 | 0 | 520 | 50 | 91.23% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 132.9231 | 1 | 1 | 1 | 2015 | 1 | 1200 | 1 | 2 | 2016 | 1 | 1 | 5 | Distribution Chamber | 2016 | 1 | 1 | 1 | 2016 | 1 | 2300 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 28-03-2017 11:46:35 CEST | Rwanda | Rulindo | Ngoma | Mugote | Rukoma |  |  | Kararama pumping network | 92 | 6572 | 3 | 2190.6667 | 47 | 45 | 51.09% | 0 | 0 | 1 | Piped Network With Pump | 2007 | Government | Spring | 4 | 0 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 3 | 2007 | 1 | 6 | 288000 | 1225.5319 | 1 | 1 | 1 | 2007 | 1 | 1500 | 1 | 25 | 2007 | 1 | 1 | 20 | Distribution Chamber¦Washout And Air Release Chamber | 2007 | 1 | 1 | 4 | 2007 | 2 | 30000 | 1 | 2 | 2007 | 2 | 1 | 2007 | 2 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 47 | 2007 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 02-01-2015 23:58:46 CET | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point behind Gisha center/Nyirambuga pumping | 133 | 30604 | 1 | 30604 | 133 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 649.6241 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 12:18:26 CET | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at Buyoga secondary school/Nyirambuga pumping | 177 | 30604 | 1 | 30604 | 177 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 488.1356 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 6 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 12:06:16 CET | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at Buyoga Health Center/Nyirambuga pumping | 177 | 30604 | 1 | 30604 | 177 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 488.1356 | 1 | 0 |  |  |  |  | 1 |  | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 6 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 06:05:10 CET | Rwanda | Rulindo | Base | Cyohoha | Bukangano |  |  | Migogo | 129 | 558 | 10 | 55.8 | 120 | 9 | 93.02% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2009 | Padiri | Groundwater (Well, Etc.) | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2009 | 1 | 50 | 34560 | 57.6 | 1 | 1 | 1 | 2009 | 2 | 6800 | 1 | 3 | 2009 | 2 | 0 |  |  |  |  | 1 | 1 | 2009 | 2 | 6800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 07-03-2017 13:11:12 CET | Rwanda | Rulindo | Cyungo | Marembo | Murambo |  |  | Mugomero Marembo | 161 | 3456 | 5 | 691.2 | 150 | 11 | 93.17% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 120 | 14400 | 19.2 | 0 | 1 | 2 | 2015 | 1 | 10000 | 1 | 10 | 2015 | 1 | 1 | 3 | Distribution Chamber | 2015 | 1 | 1 | 2 | 2015 | 1 | 10000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-04-2017 12:29:35 CEST | Rwanda | Rulindo | Murambi | Mugambazi | Amahoro |  |  | Nyakagezi | 120 | 26296 | 1 | 26296 | 43 | 77 | 35.83% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2017 | 2 | 38 | 45473.6842 | 211.5055 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 23-03-2017 06:27:56 CET | Rwanda | Rulindo | Kisaro | Sayo | Rugarama |  |  | Kiruruma | 109 | 8295 | 25 | 331.8 | 101 | 8 | 92.66% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 1140.5941 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 15 | 2014 | 1 | 1 | 5 | Pressure Break Tank | 2014 | 1 | 1 | 3 | 2014 | 1 | 4000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 25-03-2017 20:47:24 CET | Rwanda | Rulindo | Buyoga | Butare | Giko |  |  | Kiduha-muyanza | 115 | 0 | 1 | 0 | 100 | 15 | 86.96% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2007 | Italians(Lake Angels) | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 20 | 86400 | 172.8 | 1 | 1 | 1 | 2014 | 1 | 2200 | 1 | 3 | 2007 | 2 | 0 |  |  |  |  | 1 | 1 | 2007 | 2 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 04-06-2017 13:25:17 CEST | Rwanda | Rulindo | Kisaro | Kamushenyi | Kabeza |  |  | gahama | 92 | 10234 | 11 | 930.3636 | 80 | 12 | 86.96% | 0 | 0 | 1 | Piped Network With Pump | 2012 | Gouverment | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 65 | 26584.6154 | 66.4615 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 | Pressure Break Tank¦Distribution Chamber¦Washout,Air Release | 2012 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 11-03-2017 20:03:15 CET | Rwanda | Rulindo | Base | Rwamahwa | Cyondo |  |  | Ruramba | 173 | 1564 | 4 | 391 | 140 | 33 | 80.92% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 60 | 28800 | 41.1429 | 1 | 1 | 1 | 2016 | 1 | 4500 | 1 | 2 | 2016 | 1 | 1 | 2 | Sedimentation Tank | 2016 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 06-06-2017 15:05:12 CEST | Rwanda | Rulindo | Kisaro | Gitatsa | Ndago |  |  | gahama | 148 | 10234 | 11 | 930.3636 | 40 | 108 | 27.03% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2012 | Waterfor People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 50 | 34560 | 172.8 | 1 | 0 |  |  |  |  | 1 | 7 | 2012 | 1 | 1 | 14 | Sedimentation Tank | 1998 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1998 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 04:42:10 CET | Rwanda | Rulindo | Masoro | Kivugiza | Rebero |  |  | Mutagata motorised network | 376 | 26296 | 49 | 536.6531 | 138 | 238 | 36.7% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 500.8696 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 05-04-2017 21:11:44 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Ngarama |  |  | Nyirangarama water point/Rutare-Nyirangarama gravity system | 89 | 726 | 1 | 726 | 89 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 1960 | Government Of Rwanda | Spring | 1 | 1 | 0 |  |  |  |  | 20 | 86400 | 194.1573 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1960 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 14-03-2017 22:25:46 CET | Rwanda | Rulindo | Rusiga | Kirenge | Rebero |  |  | Gashinge source/Gashinge gravity | 181 | 0 | 1 | 0 | 181 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Government | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 60 | 28800 | 31.8232 | 1 | 1 | 1 | 2015 | 1 | 800 | 1 | 1 | 2013 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 19:29:22 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Wpt at Murambi Central Catholic Church/Nyirambuga pumping | 174 | 30604 | 1 | 30604 | 174 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Gor | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 496.5517 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 16-04-2017 22:24:06 CEST | Rwanda | Rulindo | Base | Gitare | Rugerero |  |  | Water point at Gasana/Nyirambuga pumping system | 143 | 30604 | 1 | 30604 | 143 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 604.1958 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 2 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 23-03-2017 18:43:30 CET | Rwanda | Rulindo | Murambi | Mugambazi | Nyarurembo |  |  | Mutagata motorised network | 144 | 26296 | 49 | 536.6531 | 40 | 104 | 27.78% | 0 | 0 | 1 | Piped Network -- Gravity Only | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1728 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:59:49 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Rugaragara |  |  | charity water 203.207 | 815 | 6572 | 1 | 6572 | 815 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 1 | 2016 | 1 | 3 | 576000 | 141.3497 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 2 | 2016 | 1 | 1 | 2 |  | 2016 | 1 | 1 | 1 | 2016 | 1 | 1000 | 1 | 3 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 05:50:45 CET | Rwanda | Rulindo | Base | Cyohoha | Gihemba |  |  | Nyamagana | 85 | 20456 | 36 | 568.2222 | 75 | 10 | 88.24% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 921.6 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 10 | 30 | 0 | 300 | 1 | 2
2017 | 02-01-2015 05:52:28 CET | Rwanda | Rulindo | Base | Cyohoha | Gihemba |  |  | Nyamagana | 75 | 20456 | 36 | 568.2222 | 60 | 15 | 80% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1152 | 1 | 1 | 2 | 2015 | 2 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 23-03-2017 11:36:36 CET | Rwanda | Rulindo | Masoro | Kigarama | Rukurazo |  |  | Mutagata Gravity Network | 247 | 26296 | 12 | 2191.3333 | 107 | 140 | 43.32% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2004 |  | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2004 | 2 | 8 | 216000 | 403.7383 | 1 | 1 | 1 | 2004 | 2 | 3500 | 1 | 6 | 2004 | 2 | 1 | 4 | Distribution Chamber¦Washout And Air Release Chamber | 2004 | 2 | 1 | 2 | 2004 | 2 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 12 | 2007 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 24-03-2017 15:50:35 CET | Rwanda | Rulindo | Buyoga | Butare | Karambi |  |  | Nyagahera | 107 | 0 | 4 | 0 | 100 | 7 | 93.46% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2017 | 2 | 16 | 108000 | 216 | 1 | 1 | 1 | 2014 | 1 | 6800 | 1 | 3 | 2014 | 1 | 1 | 3 | Distribution Chamber | 2014 | 1 | 1 | 1 | 2014 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 07:54:12 CET | Rwanda | Rulindo | Murambi | Mugambazi | Ruri |  |  | Mutagata Motorised Network | 189 | 26296 | 49 | 536.6531 | 70 | 119 | 37.04% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 987.4286 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 11:02:40 CET | Rwanda | Rulindo | Cyungo | Marembo | Gahinga |  |  | Mugomero Murambo | 652 | 3456 | 3 | 1152 | 602 | 50 | 92.33% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 120 | 14400 | 4.7841 | 0 | 1 | 2 | 2015 | 1 | 10000 | 1 | 10 | 2015 | 1 | 1 | 3 | Distribution Chamber | 2015 | 1 | 1 | 2 | 2015 | 1 | 10000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 8 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 19:19:50 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Gisiza |  |  | kinywamagana pumping network | 212 | 6436 | 26 | 247.5385 | 60 | 152 | 28.3% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 576 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 13:04:21 CET | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo |  |  |  | 203 | 0 | 31 | 0 | 203 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 85.1232 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 05:14:33 CET | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 1789 | 14 | 127.7857 | 180 | 12 | 93.75% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Padiri Gitovu | Spring¦Groundwater (Well, Etc.) | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2012 | 1 | 30 | 57600 | 64 | 1 | 1 | 1 | 2016 | 1 | 6450 | 1 | 2 | 2012 | 1 | 1 | 2 | Distribution Chamber | 2016 | 1 | 1 | 1 | 2012 | 1 | 6450 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 25-04-2017 00:31:08 CEST | Rwanda | Rulindo | Kisaro | Murama | Ryarubuguza |  |  | Gahama Kisaro network | 99 | 10234 | 14 | 731 | 99 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Government | Spring | 1 | 1 | 1 |  | 1 | 2012 | 1 | 3 | 576000 | 1163.6364 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 |  | 2012 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 18:39:52 CET | Rwanda | Rulindo | Base | Gitare | Kirwa |  |  | Rwicanyoni | 136 | 698 | 7 | 99.7143 | 100 | 36 | 73.53% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 2 | 1 | 1 | Start Chamber | 2 | 2016 | 1 | 10 | 172800 | 345.6 | 1 | 0 |  |  |  |  | 1 | 3 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 13:53:45 CET | Rwanda | Rulindo | Rukozo | Buraro | Kabingo |  |  | Kabonanyoni | 40 | 7894 | 30 | 263.1333 | 40 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 576 | 1 | 1 | 1 | 2015 | 1 | 19000 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 11:40:45 CET | Rwanda | Rulindo | Masoro | Shengampuri | Amataba |  |  | Mutagata Gravity Network | 178 | 26296 | 12 | 2191.3333 | 60 | 118 | 33.71% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2004 | 2 | 8 | 216000 | 720 | 1 | 1 | 1 | 2004 | 2 | 3500 | 1 | 6 | 2004 | 2 | 1 | 4 | Distribution Chamber¦Washout And Air Release Chamber | 2004 | 2 | 1 | 2 | 2004 | 2 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 12 | 2004 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 24-03-2017 08:34:26 CET | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 214 | 5544 | 14 | 396 | 214 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1986 |  | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 80.7477 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 04:53:28 CET | Rwanda | Rulindo | Rukozo | Mbuye | Mujebe |  |  | Kabonanyoni | 50 | 7894 | 30 | 263.1333 | 46 | 4 | 92% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 500.8696 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 08:03:07 CET | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 214 | 2456 | 10 | 245.6 | 200 | 14 | 93.46% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 15 | 115200 | 115.2 | 1 | 1 | 1 | 2016 | 2 | 7200 | 1 | 6 | 2016 | 1 | 0 |  |  |  |  | 1 | 1 | 2016 | 2 | 7200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 3 | Yes | 7 | 7 | 0 | 49 | 0 | 3
2017 | 23-03-2017 10:25:30 CET | Rwanda | Rulindo | Murambi | Mvuzo | Kabuga |  |  | rwiseke | 199 | 9536 | 5 | 1907.2 | 195 | 4 | 97.99% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2001 | 1 | 14 | 123428.5714 | 126.5934 | 1 | 1 | 1 | 2001 | 1 | 1200 | 1 | 7 | 2001 | 1 | 0 |  |  |  |  | 1 | 1 | 2001 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2001 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 06:25:45 CET | Rwanda | Rulindo | Buyoga | Gahororo | Bunyana |  |  | Kiruruma | 108 | 8295 | 25 | 331.8 | 102 | 6 | 94.44% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.)¦Null | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 1129.4118 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 15 | 2014 | 1 | 1 | 5 | Pressure Break Tank | 2014 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-04-2017 14:40:57 CEST | Rwanda | Rulindo | Buyoga | Ndarage | Kimagali |  |  | kiruruma | 125 | 8295 | 25 | 331.8 | 100 | 25 | 80% | 0 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 1152 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 11 | 2014 | 1 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 09-03-2017 21:05:54 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Kirurumo |  |  | Bitete-Rwahi network | 80 | 1316 | 15 | 87.7333 | 50 | 30 | 62.5% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 576 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 05:52:51 CET | Rwanda | Rulindo | Cyungo | Rwili | Karambi |  |  | Nyamagana | 50 | 20456 | 36 | 568.2222 | 45 | 5 | 90% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1536 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 1 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 10 | 30 | 0 | 300 | 0 | 2
2017 | 10-03-2017 11:33:57 CET | Rwanda | Rulindo | Bushoki | Mukoto | Buyogoma |  |  | Buyogoma water point/Tare-Rusiga pumping system | 130 | 9577 | 1 | 9577 | 130 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 8 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 66.4615 | 1 | 1 | 1 | 2015 | 1 | 4000 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 8000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 14-03-2017 21:58:08 CET | Rwanda | Rulindo | Tumba | Gahabwa | Mafene |  |  | Nyirambuga 2Pumping station/Source Nyakagezi | 172 | 30604 | 1 | 30604 | 172 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Gor | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 10 | 172800 | 200.9302 | 1 | 1 | 1 | 2012 | 1 | 200 | 1 | 1 | 2012 | 2 | 1 | 2 | Distribution Chamber | 2012 | 1 | 1 | 1 | 2012 | 1 | 800 | 1 | 2 | 2012 | 2 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 05:15:05 CET | Rwanda | Rulindo | Base | Rwamahwa | Gitovu |  |  | Rwankende | 154 | 1789 | 14 | 127.7857 | 130 | 24 | 84.42% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 1 | 30 | 57600 | 88.6154 | 1 | 1 | 1 | 2012 | 1 | 6450 | 1 | 3 | 2016 | 1 | 1 | 2 | Distribution Chamber | 2016 | 1 | 1 | 1 | 2016 | 1 | 6450 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 02-01-2015 05:51:21 CET | Rwanda | Rulindo | Cyungo | Burehe | Sove |  |  | Nyamagana | 74 | 20456 | 36 | 568.2222 | 45 | 29 | 60.81% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1536 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 2 | Yes | 10 | 30 | 0 | 300 | 0 | 2
2017 | 15-04-2017 22:58:11 CEST | Rwanda | Rulindo | Rusiga | Kirenge | Ntaruka |  |  | Ntaruka water point/Ntaruka-Nyange gravity system | 176 | 1567 | 1 | 1567 | 176 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2010 | Local Government And Nyange Girls School | Spring | 1 | 1 | 0 |  |  |  |  | 30 | 57600 | 65.4545 | 1 | 1 | 1 | 2010 | 1 | 100 | 1 | 1 | 2010 | 2 | 0 |  |  |  |  | 1 | 1 | 2010 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2010 | 3 | No | 0 | 0 | 1 | 0 | 1 | 3
2017 | 24-03-2017 14:44:09 CET | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 214 | 5544 | 14 | 396 | 214 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1986 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 80.7477 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 1 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 21 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 06-04-2017 18:46:56 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Bubiro |  |  | Bubiro water point/Rutomvu gravity system | 158 | 3015 | 1 | 3015 | 158 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Government Of Rwanda | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 54.6835 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 16-03-2017 07:57:34 CET | Rwanda | Rulindo | Burega | Butangampundu | Gashinge |  |  | Rwamugaza | 435 | 14106 | 38 | 371.2105 | 435 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 2 | 2003 | 1 | 3.5 | 493714.2857 | 226.9951 | 1 | 1 | 1 | 2003 | 2 | 8000 | 1 | 10 | 2003 | 1 | 1 | 8 |  | 2003 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 02-01-2015 05:53:35 CET | Rwanda | Rulindo | Cyungo | Rwili | Kabanda |  |  | Nyamagana | 69 | 20456 | 36 | 568.2222 | 59 | 10 | 85.51% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1171.5254 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 1 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 2 | Yes | 12 | 30 | 0 | 360 | 0 | 2
2017 | 21-03-2017 15:11:05 CET | Rwanda | Rulindo | Kinihira | Rebero | Kabuga |  |  | Miyove-Kinihira | 191 | 10452 | 19 | 550.1053 | 80 | 111 | 41.88% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 864 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 21-03-2017 15:47:28 CET | Rwanda | Rulindo | Kinihira | Rebero | Taba |  |  | Miyove-Kinihira | 122 | 10452 | 19 | 550.1053 | 70 | 52 | 57.38% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 987.4286 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1989 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 09-03-2017 08:44:14 CET | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 77 | 1458 | 6 | 243 | 70 | 7 | 90.91% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2005 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2005 | 1 | 75 | 23040 | 65.8286 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2005 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 08-03-2017 21:23:15 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 354 | 6436 | 26 | 247.5385 | 45 | 309 | 12.71% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 768 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 02-01-2015 23:27:34 CET | Rwanda | Rulindo | Tumba | Misezero | Kavumu |  |  | Water point at Kavumu/Nyirambuga pumping | 139 | 30604 | 1 | 30604 | 139 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 621.5827 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2015 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 08:29:43 CEST | Rwanda | Rulindo | Tumba | Nyirabirori | Rusura |  |  | Water point chez Gidasi/Nyirambuga pumping | 157 | 30604 | 1 | 30604 | 157 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 440.2548 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 06:10:20 CET | Rwanda | Rulindo | Rukozo | Bwimo | Gatiba |  |  | Gihanga II | 151 | 0 | 5 | 0 | 151 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 15 | 115200 | 152.5828 | 1 | 1 | 1 | 2016 | 1 | 7000 | 1 | 3 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 17:43:10 CET | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | Rwintare1water point[RW.WFP.Q3.14.166.028]/Tare-Rusiga pumping | 281 | 9577 | 1 | 9577 | 281 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 30.7473 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 28-03-2017 10:04:14 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyagasozi |  |  | Kararama network | 197 | 6572 | 4 | 1643 | 197 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 1 | 2009 | 1 | 4.5 | 384000 | 389.8477 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 7 | 2012 | 1 | 1 | 14 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 16-03-2017 08:13:30 CET | Rwanda | Rulindo | Burega | Butangampundu | Kigabiro |  |  | Rwamugaza | 565 | 14106 | 38 | 371.2105 | 565 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 2 | 2003 | 1 | 3.5 | 493714.2857 | 174.7661 | 1 | 1 | 1 | 2003 | 1 | 8000 | 1 | 20 | 2003 | 2 | 1 | 16 |  | 2003 | 2 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 24-03-2017 10:23:11 CET | Rwanda | Rulindo | Masoro | Nyamyumba | Kigomwa |  |  | marenge | 118 | 5544 | 14 | 396 | 118 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1997 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 15 | 2016 | 1 | 20 | 86400 | 146.4407 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 19:14:55 CET | Rwanda | Rulindo | Masoro | Kabuga | Kigarama |  |  | Mutagata motorised network | 176 | 26296 | 49 | 536.6531 | 95 | 81 | 53.98% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Water For People And Government Will | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2017 | 1 | 5 | 345600 | 727.5789 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 01:51:38 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Water point near TCT/Nyirambuga pumping | 174 | 30604 | 1 | 30604 | 174 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 496.5517 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 1 | 1 | Distribution Chamber | 2015 | 1 | 1 | 2 | 2015 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 06:29:52 CET | Rwanda | Rulindo | Kinihira | Marembo | Cyogo |  |  | Nyamagana-Kinihira | 420 | 0 | 15 | 0 | 420 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 164.5714 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 02:23:33 CET | Rwanda | Rulindo | Tumba | Barari | Gaseke |  |  | Gaseke center water point/Nyirambuga pumping | 149 | 30604 | 1 | 30604 | 149 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 579.8658 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 15-03-2017 08:04:48 CET | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 214 | 2456 | 10 | 245.6 | 185 | 29 | 86.45% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 15 | 115200 | 124.5405 | 1 | 1 | 2 | 2016 | 2 | 7200 | 1 | 6 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 16-03-2017 08:51:17 CET | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  |  | 186 | 510 | 31 | 16.4516 | 38 | 148 | 20.43% | 0 | 1 | 1 | Piped Network With Pump | 2014 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 2048.3642 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 3 | Yes | 8 | 30 | 0 | 240 | 0 | 3
2017 | 23-03-2017 08:00:44 CET | Rwanda | Rulindo | Murambi | Gatwa | Kabeza |  |  | Mutagata Motorised Network | 134 | 26296 | 49 | 536.6531 | 134 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 515.8209 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release Chamber | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 05-04-2017 21:40:02 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Karambi |  |  | Nyabishengeshi gravity system/Karambi water point | 79 | 893 | 1 | 893 | 79 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 50 | 34560 | 87.4937 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  | 2013 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 16-03-2017 08:48:14 CET | Rwanda | Rulindo | Mbogo | Bukoro | Kibamba |  |  | Musenge Network | 176 | 6074 | 29 | 209.4483 | 100 | 76 | 56.82% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 778.3784 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber¦Washout And Air Release | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 3 | Yes | 8 | 30 | 0 | 240 | 0 | 3
2017 | 15-03-2017 16:08:49 CET | Rwanda | Rulindo | Burega | Butangampundu | Muhomdo |  |  | Rwamugaza | 305 | 14106 | 38 | 371.2105 |  | 305 |  | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 |  | 0 | 1 | 2 | 2009 | 1 | 3000 | 1 | 3 | 2014 | 3 | 1 | 8 |  | 2014 | 3 | 1 | 2 | 2014 | 3 | 3000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 3 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 3 | Yes | 365 | 0 | 0 | 0 | 0 | 3
2017 | 03-01-2015 00:59:17 CET | Rwanda | Rulindo | Tumba | Taba | Nkinda |  |  | Nkinda water point/Nyirambuga pumping | 127 | 30604 | 1 | 30604 | 127 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 680.315 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 17:51:38 CEST | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | NKANGA SCHOOL WATER POINT/KIVOMO-NTAKARA GRAVITY | 129 | 0 | 1 | 0 | 129 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 50 | 34560 | 53.5814 | 1 | 0 |  |  |  |  | 0 |  |  |  | 1 | 1 | Water Point Valve Chamber | 2015 | 3 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 24-03-2017 12:56:10 CET | Rwanda | Rulindo | Masoro | Nyamyumba | Kigomwa |  |  |  | 118 | 5544 | 31 | 178.8387 | 118 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 146.4407 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 20:40:24 CET | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Gisoro- Nyundo network | 188 | 2297 | 10 | 229.7 | 35 | 153 | 18.62% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 13 | 132923.0769 | 759.5604 | 1 | 1 | 1 | 2013 | 1 | 30 | 1 | 6 | 2013 | 2 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 7000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 10:49:51 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Rwamugaza network | 193 | 14106 | 35 | 403.0286 | 193 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 596.8912 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 3 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 23-04-2017 14:43:47 CEST | Rwanda | Rulindo | Buyoga | Gahororo | Gatenderi |  |  | Kiruruma | 141 | 8295 | 25 | 331.8 | 102 | 39 | 72.34% | 0 | 0 | 1 | Piped Network With Pump | 2014 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 1129.4118 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 11 | 2014 | 1 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 03-01-2015 00:04:58 CET | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point at GS Gisha/Nyirambuga pumping | 133 | 30604 | 1 | 30604 | 133 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 649.6241 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-06-2017 07:20:03 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | rwamugaza | 200 | 14106 | 38 | 371.2105 | 200 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2003 | 1 | 3 | 576000 | 576 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 | Sedimentation Tank¦Pressure Break Tank¦Distribution Chamber | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 04:45:48 CET | Rwanda | Rulindo | Rukozo | Buraro | Shyondwe |  |  | Kabonanyoni | 75 | 7894 | 30 | 263.1333 | 70 | 5 | 93.33% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 10 | 2015 | 1 | 15 | 115200 | 329.1429 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 10:18:22 CET | Rwanda | Rulindo | Ngoma | Karambo | Kagwa |  |  | Kabarore- Ngoma- Nyabuko network | 123 | 8284 | 3 | 2761.3333 | 38 | 85 | 30.89% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 2 | 4 | 432000 | 2273.6842 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:02:49 CET | Rwanda | Rulindo | Burega | Butangampundu | Mayaga |  |  | Rwamugaza | 525 | 14106 | 38 | 371.2105 | 525 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 2 | 2003 | 1 | 3.5 | 493714.2857 | 188.0816 | 1 | 1 | 1 | 2003 | 1 | 8000 | 1 | 10 | 2014 | 1 | 1 | 8 |  | 2014 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 23-03-2017 08:12:11 CET | Rwanda | Rulindo | Murambi | Mugambazi | Ruri |  |  | Mutagata Motorised Network | 189 | 26296 | 49 | 536.6531 | 79 | 110 | 41.8% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 874.9367 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release Chamber | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 19:25:47 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Gatsinde |  |  | Gatsinde water point/Nyirambuga pumping | 178 | 30604 | 1 | 30604 | 178 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Gor | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 485.3933 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 07:15:39 CET | Rwanda | Rulindo | Rukozo | Buraro | Kivomo |  |  | Nyamagana | 80 | 20456 | 36 | 568.2222 | 30 | 50 | 37.5% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 2 | 5 | 345600 | 2304 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 2 | Yes | 10 | 30 | 0 | 300 | 0 | 2
2017 | 24-03-2017 12:45:56 CET | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 214 | 5544 | 14 | 396 | 214 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 1 | 20 | 86400 | 80.7477 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-04-2017 23:53:36 CEST | Rwanda | Rulindo | Rusiga | Gako | Ntakara |  |  | Kivomo water point/Kivomo-Ntakara | 200 | 0 | 1 | 0 | 200 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2015 | Local Government With Partnering With The Community | Spring | 1 | 1 | 0 |  |  |  |  | 50 | 34560 | 34.56 | 1 | 1 | 1 | 2015 | 1 | 100 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 05:48:42 CET | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 229 | 1458 | 6 | 243 | 190 | 39 | 82.97% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2017 | 1 | 75 | 23040 | 24.2526 | 1 | 1 | 1 | 2016 | 1 | 3000 | 1 | 1 | 2016 | 1 | 1 | 1 | Pressure Break Tank | 2016 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 19:43:30 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Kigarama |  |  | kinywamagana pumping network | 233 | 6436 | 26 | 247.5385 | 89 | 144 | 38.2% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 388.3146 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 23-04-2017 14:42:54 CEST | Rwanda | Rulindo | Buyoga | Gahororo | Gipfundo |  |  | rukondo | 162 | 0 | 2 | 0 | 120 | 42 | 74.07% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2012 | G.Thierry | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2012 | 1 | 30 | 57600 | 96 | 1 | 1 | 1 | 2012 | 1 | 4500 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 13:25:04 CEST | Rwanda | Rulindo | Tumba | Nyirabirori | Rugando |  |  | Water point at Rugando chez Ndayambaje/Nyirambuga pumping | 161 | 30604 | 1 | 30604 | 161 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 429.3168 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 10-03-2017 11:15:30 CET | Rwanda | Rulindo | Bushoki | N.Ngarama | Nyenyeri |  |  | Nyenyeri water point/Tare-Rusiga pumping | 68 | 9577 | 1 | 9577 | 68 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 10 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 70 | 24685.7143 | 72.605 | 1 | 1 | 1 | 2015 | 1 | 4000 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 3 | 2015 | 1 | 8000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 17-03-2017 05:24:05 CET | Rwanda | Rulindo | Mbogo | Rurenge | Munini |  |  | Musenge network | 111 | 6074 | 29 | 209.4483 | 49 | 62 | 44.14% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1588.5273 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Washout And Air Release Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 16-03-2017 06:40:03 CET | Rwanda | Rulindo | Burega | Taba | Nyagisozi |  |  | Rwamugaza | 520 | 14106 | 38 | 371.2105 | 520 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 147.6923 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 19:51:11 CET | Rwanda | Rulindo | Shyorongi | Rubona | Gishyita |  |  | Gisoro- Nyundo network | 205 | 2297 | 10 | 229.7 | 110 | 95 | 53.66% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 13 | 132923.0769 | 241.6783 | 1 | 1 | 1 | 2013 | 1 | 30 | 1 | 6 | 2013 | 2 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 7000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 17:04:58 CET | Rwanda | Rulindo | Burega | Butangampundu | Gacyamo |  |  | Rwamugaza | 550 | 14106 | 38 | 371.2105 | 550 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 139.6364 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 23 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 07-03-2017 10:08:01 CET | Rwanda | Rulindo | Cyungo | Marembo | Rusayo |  |  | Nyabirarama | 150 | 0 | 2 | 0 | 100 | 50 | 66.67% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 150 | 11520 | 23.04 | 1 | 1 | 1 | 2015 | 1 | 1200 | 1 | 1 | 2015 | 1 | 1 | 1 | Distribution Chamber | 2015 | 1 | 1 | 1 | 2015 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-04-2017 23:02:00 CEST | Rwanda | Rulindo | Buyoga | Karama | Kigarama |  |  | Kigarama water point/Nyirambuga pumping system | 121 | 30604 | 1 | 30604 | 121 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 714.0496 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 02-01-2015 05:57:43 CET | Rwanda | Rulindo | Cyungo | Rwili | Karambi |  |  | Nyamagana | 50 | 20456 | 36 | 568.2222 | 5 | 45 | 10% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 13824 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 2 | Yes | 10 | 30 | 0 | 300 | 0 | 2
2017 | 24-03-2017 11:58:50 CET | Rwanda | Rulindo | Masoro | Shengampuri | Agasharu |  |  |  | 130 | 6740 | 31 | 217.4194 | 130 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 132.9231 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 13:56:52 CET | Rwanda | Rulindo | Rukozo | Buraro | Kabingo |  |  | Kabonanyoni | 35 | 7894 | 30 | 263.1333 | 35 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 658.2857 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 2 | 1 | 1 | 2015 | 1 | 720 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 04:52:44 CET | Rwanda | Rulindo | Rukozo | Mbuye | Mujebe |  |  | Kabonanyoni | 800 | 7894 | 30 | 263.1333 | 800 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 28.8 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 15:33:30 CET | Rwanda | Rulindo | Mbogo | Rurenge | Ruhondo |  |  | Kishwi network | 184 | 1309 | 4 | 327.25 | 58 | 126 | 31.52% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Goverment | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 25 | 69120 | 238.3448 | 1 | 1 | 2 | 2016 | 1 | 700 | 1 | 2 | 2003 | 1 | 0 |  |  |  |  | 1 | 2 | 2003 | 1 | 680 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2003 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 20-04-2017 06:51:05 CEST | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point Kumanga /Nyirambuga pumping | 115 | 30604 | 1 | 30604 | 115 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 601.0435 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 2 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 09-03-2017 20:15:56 CET | Rwanda | Rulindo | Shyorongi | Kijabagwe | Rimwe |  |  | Gisoro- Nyundo network | 120 | 2297 | 10 | 229.7 | 25 | 95 | 20.83% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 13 | 132923.0769 | 1063.3846 | 1 | 1 | 1 | 2013 | 1 | 30 | 1 | 6 | 2013 | 2 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 7000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-03-2017 18:19:47 CET | Rwanda | Rulindo | Kinihira | Rebero | Karambi |  |  | Nyamagana-Kinihira | 144 | 0 | 15 | 0 | 80 | 64 | 55.56% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 864 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 10:25:08 CET | Rwanda | Rulindo | Ngoma | Kabuga | Nyabuko |  |  | Kabarore-Ngoma-Nyabuko network | 122 | 8284 | 14 | 591.7143 | 30 | 92 | 24.59% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 1 | 4 | 432000 | 2880 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 18:40:43 CET | Rwanda | Rulindo | Base | Gitare | Gatete |  |  | Rwicanyoni | 141 | 698 | 7 | 99.7143 | 135 | 6 | 95.74% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 1 | 10 | 172800 | 256 | 1 | 1 | 1 | 2016 | 1 | 8600 | 1 | 3 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 14:17:15 CET | Rwanda | Rulindo | Rukozo | Mbuye | Nyarusebeya |  |  | Kabonanyoni | 80 | 7894 | 30 | 263.1333 | 70 | 10 | 87.5% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 329.1429 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 21:09:08 CET | Rwanda | Rulindo | Mbogo | Bukoro | Gihonga |  |  | Kibuye | 110 | 1232 | 3 | 410.6667 | 60 | 50 | 54.55% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | Start And Collection Chamber | 2 | 2016 | 1 | 45 | 38400 | 128 | 1 | 1 | 1 | 2016 | 1 | 1500 | 0 |  |  |  | 1 | 1 | Washout Chamber | 2016 | 1 | 1 | 1 | 2016 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1998 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 09-03-2017 06:35:57 CET | Rwanda | Rulindo | Shyorongi | Rubona | Gishyita |  |  | kirikumuryango network | 205 | 0 | 26 | 0 | 120 | 85 | 58.54% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 261.8182 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-04-2017 21:51:54 CEST | Rwanda | Rulindo | Kisaro | Kigarama | Runyinya |  |  | wasac network towards Mutete in Gicumbi district | 148 | 0 | 1 | 0 | 148 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2000 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 5 | 345600 | 467.027 | 1 | 1 | 1 | 2003 | 1 | 30000 | 1 | 7 | 2003 | 1 | 1 | 14 |  | 2003 | 1 | 1 | 1 | 2003 | 1 | 30000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 20:13:11 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatimba |  |  | kinywamagana pumping network | 217 | 6436 | 26 | 247.5385 | 82 | 135 | 37.79% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 421.4634 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 23-03-2017 07:17:40 CET | Rwanda | Rulindo | Kinihira | Marembo | Gatare |  |  | Nyamagana- Kinihira | 168 | 0 | 4 | 0 | 70 | 98 | 41.67% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 987.4286 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 18 | Distribution Chamber¦Washout, Ventouse | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 04:33:27 CET | Rwanda | Rulindo | Cyungo | Rwili | Nturo |  |  | Nyamabara | 2785 | 0 | 1 | 0 | 1450 | 1335 | 52.06% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 47.669 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 10 | 30 | 0 | 300 | 1 | 2
2017 | 23-03-2017 16:19:15 CET | Rwanda | Rulindo | Murambi | Bubangu | Taba |  |  | rwiseke | 193 | 9536 | 5 | 1907.2 | 193 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2001 | 1 | 14 | 123428.5714 | 127.9053 | 1 | 1 | 1 | 2001 | 1 | 12000 | 1 | 7 | 2001 | 1 | 0 |  |  |  |  | 1 | 1 | 2001 | 1 | 12000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2001 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 17:53:49 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Ngendo |  |  | kirikumuryango network | 180 | 0 | 26 | 0 | 180 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 174.5455 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 10000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 12:56:33 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Kagunda |  |  | Muvumu- Taba | 94 | 0 | 10 | 0 | 25 | 69 | 26.6% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 25 | 69120 | 552.96 | 1 | 1 | 1 | 2013 | 1 | 800 | 1 | 3 | 2013 | 2 | 1 | 9 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 7500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | Yes | 1 | 3 | 0 | 3 | 1 | 2
2017 | 20-04-2017 12:01:13 CEST | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point chez Haguma/Nyirambuga pumping | 169 | 30604 | 1 | 30604 | 169 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 408.9941 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 1 | 1 | 1 | Pressure Break Tank | 2017 | 1 | 1 | 1 | 2017 | 1 | 100 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 21:52:47 CET | Rwanda | Rulindo | Shyorongi | Rubona | Rwahi |  |  | Bitete-Rwahi network | 360 | 1316 | 15 | 87.7333 | 360 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 80 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Washout, Ventouse | 2013 | 1 | 1 | 1 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 06:13:46 CET | Rwanda | Rulindo | Kinihira | Marembo | Cyogo |  |  | Nyamagana-Kinihira | 184 | 0 | 15 | 0 | 60 | 124 | 32.61% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1152 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 12:13:23 CET | Rwanda | Rulindo | Mbogo | Bukoro | Rwambogo |  |  | Rwambogo | 156 | 934 | 3 | 311.3333 | 54 | 102 | 34.62% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 2 | 2016 | 1 | 60 | 28800 | 106.6667 | 1 | 1 | 1 | 2016 | 1 | 700 | 1 | 1 | 2016 | 2 | 0 |  |  |  |  | 1 | 1 | 2016 | 2 | 350 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 19:38:40 CET | Rwanda | Rulindo | Shyorongi | Rubona | Kigali |  |  | Gisoro- Nyundo network | 300 | 2297 | 10 | 229.7 | 300 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 13 | 132923.0769 | 88.6154 | 1 | 1 | 1 | 2013 | 1 | 30 | 1 | 6 | 2013 | 2 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 7000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 14:45:58 CEST | Rwanda | Rulindo | Mbogo | Bukoro | Kinini/Mbogo |  |  |  | 188 | 510 | 31 | 16.4516 | 80 | 108 | 42.55% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 180 | 9600 | 24 | 1 | 1 | 1 | 2016 | 1 | 1000 | 1 | 1 | 2003 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2004 | 2004 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 22-03-2017 18:38:18 CET | Rwanda | Rulindo | Kinihira | Butunzi | Bunahi |  |  | Nyamagana-Kinihira | 105 | 0 | 15 | 0 | 60 | 45 | 57.14% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1152 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 04-06-2017 13:25:00 CEST | Rwanda | Rulindo | Kisaro | Gitatsa | Ruberano |  |  | gahama | 132 | 10234 | 11 | 930.3636 | 100 | 32 | 75.76% | 0 | 0 | 1 | Piped Network With Pump | 2012 | Waterforpeople | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 65 | 26584.6154 | 53.1692 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 | Pressure Break Tank¦Distribution Chamber¦Washout, Air Release | 2012 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 05:52:14 CET | Rwanda | Rulindo | Base | Cyohoha | Kabingo |  |  | Nyamagana | 50 | 20456 | 36 | 568.2222 | 45 | 5 | 90% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 2 | 5 | 345600 | 1536 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 23-03-2017 17:26:01 CET | Rwanda | Rulindo | Buyoga | Ndarage | Gahondo |  |  | Ndarage | 105 | 0 | 9 | 0 | 100 | 5 | 95.24% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2014 | 1 | 30 | 57600 | 115.2 | 1 | 1 | 1 | 2014 | 1 | 6300 | 1 | 5 | 2014 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 18:33:32 CET | Rwanda | Rulindo | Masoro | Kabuga | Nyakizu |  |  | Mutagata motorised network | 196 | 26296 | 49 | 536.6531 | 106 | 90 | 54.08% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 652.0755 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 06:26:54 CET | Rwanda | Rulindo | Buyoga | Gitumba | Munini |  |  | Kiruruma | 158 | 8295 | 25 | 331.8 | 150 | 8 | 94.94% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 768 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 15 | 2014 | 1 | 1 | 5 | Pressure Break Tank | 2014 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 3 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 16-03-2017 08:49:21 CET | Rwanda | Rulindo | Mbogo | Rurenge | Gicumbi |  |  | Musenge Network | 141 | 6074 | 29 | 209.4483 | 41 | 100 | 29.08% | 0 | 1 | 1 | Piped Network With Pump | 2014 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1898.4838 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 08-03-2017 21:29:54 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 354 | 6436 | 26 | 247.5385 | 89 | 265 | 25.14% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 388.3146 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 09-03-2017 19:20:00 CET | Rwanda | Rulindo | Shyorongi | Rubona | Nyabitare |  |  | Gisaro-Nyundo network | 130 | 0 | 1 | 0 | 50 | 80 | 38.46% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 13 | 132923.0769 | 531.6923 | 1 | 1 | 1 | 2013 | 1 | 38 | 1 | 6 | 2013 | 2 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 7000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 10:39:41 CET | Rwanda | Rulindo | Cyungo | Marembo | Gahinga |  |  | Mugomero Marembo | 652 | 3456 | 5 | 691.2 | 602 | 50 | 92.33% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 120 | 14400 | 4.7841 | 0 | 1 | 2 | 2015 | 1 | 10000 | 1 | 10 | 2015 | 1 | 1 | 3 | Distribution Chamber | 2015 | 1 | 1 | 2 | 2015 | 1 | 10000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 8 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 17:53:30 CET | Rwanda | Rulindo | Kinihira | Karegamazi | Ntunguru |  |  | Miyove- Kinihira | 168 | 10452 | 4 | 2613 | 60 | 108 | 35.71% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 1152 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2001 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 15-03-2017 08:07:33 CET | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 214 | 2456 | 10 | 245.6 | 200 | 14 | 93.46% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 15 | 115200 | 115.2 | 1 | 1 | 2 | 2016 | 2 | 7200 | 1 | 6 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 2 | 7200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | Yes | 7 | 7 | 0 | 49 | 0 | 2
2017 | 20-04-2017 15:58:34 CEST | Rwanda | Rulindo | Bushoki | Giko | Karambo |  |  | Water point at Buramira Primary school/Buramira-Kivure gravity system | 250 | 1255 | 1 | 1255 | 250 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 40 | 43200 | 34.56 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 21:51:35 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 354 | 6436 | 26 | 247.5385 | 30 | 324 | 8.475% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 1152 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 2 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 27-03-2017 08:27:23 CEST | Rwanda | Rulindo | Kisaro | Murama | Kibingwe |  |  | Gahama Kisaro network | 610 | 10234 | 14 | 731 | 610 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 |  | 1 | 2012 | 1 | 3 | 576000 | 188.8525 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 |  | 2012 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 2 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 10:56:52 CET | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo |  |  | marenge | 203 | 5544 | 14 | 396 | 203 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1986 |  | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 85.1232 | 1 | 1 | 1 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 01:27:51 CET | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at ADEPR Buyoga/Nyirambuga pumping | 177 | 30604 | 1 | 30604 | 177 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 488.1356 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 11:42:15 CET | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | Nganzo-Kabarore | 198 | 0 | 5 | 0 | 100 | 98 | 50.51% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 20 | 86400 | 172.8 | 1 | 1 | 1 | 2014 | 2 | 400 | 1 | 3 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 3 | 800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2014 | 3 | Yes | 5 | 30 | 0 | 150 | 0 | 3
2017 | 28-03-2017 08:48:30 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Rukore |  |  | Rwamugaza network | 184 | 14106 | 35 | 403.0286 | 184 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 626.087 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 08:16:53 CEST | Rwanda | Rulindo | Tumba | Nyirabirori | Rusura |  |  | Water point chez Ntihabose/Nyirambuga pumping | 157 | 30604 | 1 | 30604 | 157 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 |  | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 440.2548 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 23-03-2017 12:00:37 CET | Rwanda | Rulindo | Masoro | Kabuga | Kigarama |  |  | Mutagata motorised network | 176 | 26296 | 49 | 536.6531 | 81 | 95 | 46.02% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 853.3333 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-04-2017 23:07:41 CEST | Rwanda | Rulindo | Rusiga | Gako | Kabuye |  |  | Ruganzu-Kabuye gravity system | 169 | 0 | 1 | 0 | 169 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2010 | Private Operator And Local Government | Spring | 1 | 1 | 0 | [7 empty] | 0 | 1 | 1 | 2010 | 3 | 100 | 1 | 1 | 2010 | 3 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  | 2010 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 15-03-2017 19:19:31 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Gatsinde |  |  | Gatsinde wpt/Nyirambuga | 178 | 30604 | 1 | 30604 | 178 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Gor | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 485.3933 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 09:08:02 CET | Rwanda | Rulindo | Cyungo | Marembo | Buyaga |  |  | Mugomero Marembo | 652 | 3456 | 5 | 691.2 | 602 | 50 | 92.33% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 120 | 14400 | 4.7841 | 0 | 1 | 1 | 2015 | 1 | 10000 | 1 | 10 | 2015 | 1 | 1 | 3 | Distribution Chamber | 2015 | 1 | 1 | 2 | 2015 | 1 | 10000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 8 | 2015 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 06:58:55 CEST | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point at APEKI Accommodation/Nyirambuga pumping | 115 | 30604 | 1 | 30604 | 115 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 601.0435 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 100 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 6 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 08:06:03 CEST | Rwanda | Rulindo | Tumba | Misezero | Karambi |  |  | Water point chez Nkurunziza/Nyirambuga pumping | 160 | 30604 | 2 | 15302 | 160 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 432 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 12:23:50 CET | Rwanda | Rulindo | Masoro | Kabuga | Gisiza |  |  | Mutagata motorised network | 135 | 26296 | 49 | 536.6531 | 135 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 512 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 06-06-2017 16:22:15 CEST | Rwanda | Rulindo | Kisaro | Murama | Akamanama |  |  | kano | 141 | 0 | 1 | 0 | 120 | 21 | 85.11% | 0 | 1 | 1 | Piped Network With Pump | 2012 | Waterforpeople | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 15 | 115200 | 192 | 1 | 0 |  |  |  |  | 1 | 7 | 2012 | 1 | 1 | 14 | Sedimentation Tank¦Pressure Break Tank¦Distribution Chamber¦Null | 1998 | 1 | 1 | 2 | 2012 | 1 | 30000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1998 | 1 | Yes | 1 | 3 | 0 | 3 | 0 | 1
2017 | 14-04-2017 22:24:50 CEST | Rwanda | Rulindo | Bushoki | Gasiza | Budaha |  |  | Budaha water point/Nkome gravity system | 205 | 0 | 1 | 0 | 205 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2002 | Coforwa | Spring | 1 | 1 | 0 |  |  |  |  | 18 | 96000 | 93.6585 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2002 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 12:35:27 CET | Rwanda | Rulindo | Masoro | Nyamyumba | Marembo |  |  | marenge | 173 | 5544 | 14 | 396 | 173 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1998 |  | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 99.8844 | 1 | 1 | 1 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 14:06:52 CET | Rwanda | Rulindo | Rukozo | Buraro | Murwa |  |  | Kabonanyoni | 75 | 7894 | 30 | 263.1333 | 70 | 5 | 93.33% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 329.1429 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 20:36:51 CET | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | kinywamagana pumping network | 281 | 6436 | 26 | 247.5385 | 50 | 231 | 17.79% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 691.2 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 28 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse;,Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 23-03-2017 06:28:54 CET | Rwanda | Rulindo | Buyoga | Gitumba | Remera |  |  | Kiruruma | 130 | 8295 | 25 | 331.8 | 126 | 4 | 96.92% | 1 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 914.2857 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 15 | 2014 | 1 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 11-03-2017 10:23:15 CET | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 45 | 20456 | 36 | 568.2222 | 40 | 5 | 88.89% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1728 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 2 | Yes | 10 | 22 | 0 | 220 | 0 | 2
2017 | 02-06-2017 06:24:37 CEST | Rwanda | Rulindo | Ntarabana | Mahaza | Kayenzi |  |  | Rwamugaza | 200 | 14106 | 38 | 371.2105 | 20 | 180 | 10% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Goverment | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2003 | 1 | 3 | 576000 | 5760 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 | Sedimentation Tank | 2003 | 1 | 1 | 2 | 2003 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 12:23:10 CET | Rwanda | Rulindo | Masoro | Nyamyumba | Kabuga |  |  |  | 119 | 0 | 31 | 0 | 119 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 145.2101 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 22:14:51 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Kirurumo |  |  | Bitete-Rwahi network | 80 | 1316 | 15 | 87.7333 | 35 | 45 | 43.75% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 822.8571 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 14:13:07 CET | Rwanda | Rulindo | Mbogo | Mushali | Rwambogo |  |  | Rwambogo Extension network | 69 | 934 | 1 | 934 | 69 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | Suction Tank | 1 | 2009 | 2 | 3 | 576000 | 1669.5652 | 1 | 1 | 1 | 2016 | 1 | 600 | 1 | 1 | 2016 | 1 | 1 | 1 | Washout Chamber | 2016 | 1 | 1 | 1 | 2016 | 3 | 100 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 15-03-2017 06:06:37 CET | Rwanda | Rulindo | Base | Rwamahwa | Kiruli |  |  | Migogo | 223 | 558 | 10 | 55.8 | 200 | 23 | 89.69% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2009 | Padiri(Lake Angels). | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2009 | 2 | 50 | 34560 | 34.56 | 1 | 1 | 1 | 2009 | 2 | 6800 | 1 | 3 | 2009 | 2 | 0 |  |  |  |  | 1 | 1 | 2009 | 2 | 6800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2009 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 08-03-2017 22:49:44 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Nyabisindu |  |  | kirikumuryango network | 149 | 0 | 26 | 0 | 62 | 87 | 41.61% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 506.7449 | 1 | 1 | 1 | 2013 | 2 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 20:02:18 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatimba |  |  | kinywamagana pumping network | 217 | 6436 | 26 | 247.5385 | 180 | 37 | 82.95% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 192 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 21-03-2017 13:49:17 CET | Rwanda | Rulindo | Rukozo | Buraro | Rukingu |  |  | Kabonanyoni | 100 | 7894 | 30 | 263.1333 | 95 | 5 | 95% | 1 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 242.5263 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 14-03-2017 22:59:23 CET | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Kingazi 2water point/Nyakabizi1&2 | 157 | 1259 | 1 | 1259 | 157 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 2 | 1 | 0 |  |  |  |  | 20 | 86400 | 110.0637 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 01-01-2015 19:57:53 CET | Rwanda | Rulindo | Cyungo | Rwili | Nyabisasa |  |  | Sakara | 570 | 0 | 4 | 0 | 520 | 50 | 91.23% | 0 | 1 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 132.9231 | 1 | 1 | 1 | 2015 | 1 | 1200 | 1 | 2 | 2015 | 1 | 1 | 5 | Distribution Chamber | 2015 | 1 | 1 | 1 | 2016 | 1 | 2300 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 16-03-2017 05:58:45 CET | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 495 | 14106 | 38 | 371.2105 | 495 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 155.1515 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 11:17:20 CET | Rwanda | Rulindo | Ngoma | Kabuga | Kirambo |  |  | Nganzo-Kabarore | 131 | 0 | 5 | 0 | 43 | 88 | 32.82% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 3 | 20 | 86400 | 401.8605 | 1 | 1 | 2 | 2014 | 2 | 400 | 1 | 3 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 3 | 800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2014 | 3 | Yes | 5 | 30 | 0 | 150 | 0 | 3
2017 | 24-03-2017 11:25:11 CET | Rwanda | Rulindo | Masoro | Kigarama | Nyakibungo |  |  |  | 229 | 0 | 31 | 0 | 229 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 1998 |  | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 75.4585 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 09:58:08 CET | Rwanda | Rulindo | Murambi | Mvuzo | Kabuga |  |  | Mutagata Motorised Network | 199 | 26296 | 49 | 536.6531 | 98 | 101 | 49.25% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 705.3061 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 12:14:43 CET | Rwanda | Rulindo | Murambi | Bubangu | Nyagisozi |  |  | Gakoma network | 154 | 7108 | 2 | 3554 | 154 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 2 | 1 | 0 |  |  |  |  | 9 | 192000 | 249.3506 | 1 | 0 |  |  |  |  | 1 | 2 | 2004 | 1 | 0 |  |  |  |  | 1 | 1 | 2004 | 2 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2004 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 21:02:07 CET | Rwanda | Rulindo | Base | Gitare | Gihora |  |  | Gihora Water point/Rutomvu gravity system | 101 | 3015 | 1 | 3015 | 101 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 85.5446 | 1 | 0 |  |  |  |  | 1 | 1 | 2013 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 22:01:02 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Mwagiro |  |  | Kirikumuryango network | 139 | 0 | 26 | 0 | 20 | 119 | 14.39% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 1570.9091 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 07:11:39 CET | Rwanda | Rulindo | Burega | Butangampundu | Kisigiro |  |  | Rwamugaza | 605 | 14106 | 38 | 371.2105 | 605 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 126.9421 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 10-03-2017 11:04:35 CET | Rwanda | Rulindo | Ngoma | Karambo | Kagwa |  |  | Nganzo-Kabarore | 123 | 0 | 5 | 0 | 44 | 79 | 35.77% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 20 | 86400 | 392.7273 | 1 | 1 | 1 | 2014 | 2 | 400 | 1 | 3 | 2017 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 3 | 800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2014 | 2 | Yes | 5 | 30 | 0 | 150 | 0 | 3
2017 | 13-03-2017 06:52:35 CET | Rwanda | Rulindo | Ngoma | Mugote | Kiboha |  |  | Kabarore-Ngoma-Nyabuko network | 74 | 8284 | 14 | 591.7143 | 39 | 35 | 52.7% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 1 | 4 | 432000 | 2215.3846 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 4 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 1 | Yes | 1 | 10 | 0 | 10 | 1 | 1
2017 | 12-03-2017 18:41:26 CET | Rwanda | Rulindo | Base | Gitare | Kirwa |  |  | Rwicanyoni | 116 | 698 | 7 | 99.7143 | 113 | 3 | 97.41% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 1 | 10 | 172800 | 305.8407 | 1 | 1 | 1 | 2016 | 1 | 8600 | 1 | 3 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-06-2017 09:32:31 CEST | Rwanda | Rulindo | Cyinzuzi | Rudogo | Gasiza |  |  | Rwagitare | 76 | 0 | 2 | 0 | 66 | 10 | 86.84% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2009 | Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2009 | 1 | 1.2 | 1440000 | 4363.6364 | 1 | 1 | 1 | 2009 | 1 | 1200 | 1 | 1 | 2009 | 1 | 1 | 2 | Pressure Break Tank¦Distribution Chamber | 2009 | 1 | 1 | 1 | 2009 | 1 | 900 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2009 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 06:26:13 CET | Rwanda | Rulindo | Buyoga | Gahororo | Shagasha |  |  | Kiruruma | 209 | 8295 | 25 | 331.8 | 200 | 9 | 95.69% | 1 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 576 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 15 | 2014 | 1 | 1 | 5 | Pressure Break Tank | 2014 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 09:33:33 CEST | Rwanda | Rulindo | Tumba | Misezero | Karambi |  |  | Water point chez Nkurunziza/Nyirambuga pumping | 160 | 30604 | 2 | 15302 | 160 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 432 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2017 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 18:57:13 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Nyakaruri |  |  | kinywamagana pumping network | 127 | 6436 | 26 | 247.5385 | 127 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 272.126 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 06-04-2017 19:07:46 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Remera |  |  | Kinyankeri water point at Buyogoma-Remera border | 105 | 0 | 1 | 0 | 105 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2007 | Local Government In Collaboration With The Community | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 82.2857 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2010 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 06:25:26 CET | Rwanda | Rulindo | Buyoga | Gitumba | Rutabo |  |  | Kiruruma | 128 | 8295 | 25 | 331.8 | 125 | 3 | 97.66% | 1 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 2 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2014 | 1 | 3 | 576000 | 921.6 | 1 | 1 | 3 | 2014 | 1 | 4000 | 1 | 15 | 2014 | 1 | 1 | 5 | Pressure Break Tank | 2014 | 1 | 1 | 3 | 2014 | 1 | 4000 | 1 | 2 | 2014 | 1 | 0 |  |  | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 07:56:12 CET | Rwanda | Rulindo | Murambi | Mugambazi | Buliza |  |  | Mutagata Motorised Network | 221 | 26296 | 49 | 536.6531 | 121 | 100 | 54.75% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 571.2397 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 05:15:29 CET | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 1789 | 14 | 127.7857 | 180 | 12 | 93.75% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2012 | Padiri | Spring¦Groundwater (Well, Etc.) | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 30 | 57600 | 64 | 1 | 1 | 1 | 2016 | 1 | 6450 | 1 | 2 | 2012 | 1 | 1 | 2 | Distribution Chamber | 2012 | 1 | 1 | 1 | 2016 | 1 | 6450 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 07:01:14 CEST | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point at APEKI Tumba Boys Dormitory/Nyirambuga pumping | 115 | 30604 | 1 | 30604 | 115 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 601.0435 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 100 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 6 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 07:15:18 CET | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 325 | 26296 | 49 | 536.6531 | 58 | 267 | 17.85% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1191.7241 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2016 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 06:06:10 CET | Rwanda | Rulindo | Base | Rwamahwa | Kabahama |  |  | Migogo | 178 | 558 | 10 | 55.8 | 150 | 28 | 84.27% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2009 | Padiri(Lake Angels). | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2009 | 2 | 50 | 34560 | 46.08 | 1 | 1 | 1 | 2009 | 2 | 6800 | 1 | 2 | 2009 | 2 | 0 |  |  |  |  | 1 | 1 | 2009 | 2 | 6800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2009 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 25-03-2017 20:48:07 CET | Rwanda | Rulindo | Buyoga | Butare | Gasave |  |  | Kiduha | 114 | 0 | 7 | 0 | 100 | 14 | 87.72% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2007 | Governement (District, Wasac) And Water For People | Spring¦Null | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 20 | 86400 | 172.8 | 1 | 1 | 1 | 2007 | 2 | 2200 | 1 | 3 | 2007 | 2 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 20-04-2017 14:39:34 CEST | Rwanda | Rulindo | Mbogo | Bukoro | Karindi |  |  |  | 120 | 510 | 31 | 16.4516 | 40 | 80 | 33.33% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2007 |  | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 180 | 9600 | 48 | 1 | 1 | 1 | 2007 | 1 | 1000 | 1 | 1 | 1997 | 2 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2007 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-04-2017 21:51:14 CEST | Rwanda | Rulindo | Burega | Taba | Gasango |  |  | Rwamugaza network | 79 | 14106 | 35 | 403.0286 | 79 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 1458.2278 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 3 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 23-03-2017 06:28:16 CET | Rwanda | Rulindo | Buyoga | Gitumba | Gitaba |  |  | Kiruruma | 169 | 8295 | 25 | 331.8 | 160 | 9 | 94.67% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 720 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 15 | 2014 | 1 | 1 | 5 | Distribution Chamber | 2014 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2014 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 15-04-2017 23:50:31 CEST | Rwanda | Rulindo | Rusiga | Gako | Ntakara |  |  | Ntakara water point/Ntakara gravity system | 129 | 0 | 1 | 0 | 129 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2015 | Local Government In Partnership With Community | Spring | 1 | 1 | 0 |  |  |  |  | 50 | 34560 | 53.5814 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 08:03:41 CET | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 214 | 2456 | 10 | 245.6 | 200 | 14 | 93.46% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 15 | 115200 | 115.2 | 1 | 1 | 1 | 2016 | 1 | 7200 | 1 | 6 | 2016 | 1 | 0 |  |  |  |  | 1 | 1 | 2016 | 2 | 7200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | Yes | 6 | 7 | 0 | 42 | 0 | 2
2017 | 10-03-2017 04:23:19 CET | Rwanda | Rulindo | Ngoma | Mugote | Kigina |  |  | Shishi network | 84 | 0 | 4 | 0 | 84 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 28 | 61714.2857 | 146.9388 | 1 | 1 | 1 | 2014 | 1 | 700 | 1 | 2 | 2014 | 1 | 0 |  |  |  |  | 1 | 1 | 2014 | 1 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 13-03-2017 06:47:36 CET | Rwanda | Rulindo | Ngoma | Munyarwanda | Busizi |  |  | Kabarore-Ngoma-Nyabuko network | 100 | 8284 | 14 | 591.7143 | 39 | 61 | 39% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 1 | 4 | 432000 | 2215.3846 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 4 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 1 | Yes | 1 | 10 | 0 | 10 | 1 | 1
2017 | 16-04-2017 23:15:04 CEST | Rwanda | Rulindo | Tumba | Barari | Gashoro |  |  | Gashoro water point/Nyirambuga pumping | 161 | 30604 | 1 | 30604 | 161 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 536.646 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 3 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 10-03-2017 04:26:25 CET | Rwanda | Rulindo | Ngoma | Karambo | Butare |  |  | Shishi network | 122 | 0 | 4 | 0 | 38 | 84 | 31.15% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 28 | 61714.2857 | 324.812 | 1 | 1 | 1 | 2014 | 1 | 700 | 1 | 2 | 2014 | 1 | 0 |  |  |  |  | 1 | 1 | 2014 | 1 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 13-03-2017 22:24:03 CET | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Water point at centre kigamba/Rutumvo gravity | 172 | 0 | 1 | 0 | 172 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 50.2326 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 14-03-2017 22:07:15 CET | Rwanda | Rulindo | Rusiga | Kirenge | Kinini |  |  | Kinini water point/Ntaruka-Gahama gravity | 250 | 1567 | 1 | 1567 | 250 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2008 | Gor | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2006 | 1 | 40 | 43200 | 34.56 | 1 | 1 | 1 | 2006 | 1 | 100 | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2008 | 1 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 14-03-2017 22:16:33 CET | Rwanda | Rulindo | Rusiga | Kirenge | Kinini |  |  | Kinini 2 water point/Ntaruka-gahama gravity | 250 | 1567 | 1 | 1567 | 250 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2006 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 34.56 | 1 | 0 |  |  |  |  | 1 | 1 | 2006 | 2 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2006 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 24-03-2017 05:17:39 CET | Rwanda | Rulindo | Masoro | Kigarama | Rukurazo |  |  | Mutagata Gravity network | 247 | 26296 | 12 | 2191.3333 | 140 | 107 | 56.68% | 0 | 0 | 1 | Piped Network -- Gravity Only | 1987 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2004 | 2 | 8 | 216000 | 308.5714 | 1 | 1 | 1 | 2004 | 2 | 3500 | 1 | 6 | 2004 | 2 | 1 | 4 | Distribution Chamber¦Washout And Air Release | 2004 | 2 | 1 | 2 | 2004 | 2 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 12 | 2004 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 14-04-2017 20:35:01 CEST | Rwanda | Rulindo | Bushoki | Mukoto | Muko |  |  | Water point at Godoro/Rusave gravity system | 116 | 567 | 1 | 567 | 116 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 40 | 43200 | 74.4828 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 18-04-2017 06:42:21 CEST | Rwanda | Rulindo | Tumba | Barari | Kigarama |  |  | Water point nearby APEKI Tumba Technical School/Nyirambuga pumping | 154 | 30604 | 1 | 30604 | 154 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 448.8312 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 15:30:27 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Nyakabanga |  |  | 0 | 780 | 6572 | 15 | 438.1333 |  | 780 |  | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2009 | 1 | 4.5 | 384000 |  | 0 | 1 | 2 | 2014 | 3 | 3000 | 1 | 2 | 2014 | 3 | 1 | 8 |  | 2014 | 3 | 1 | 2 | 2014 | 3 | 3000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 3 | Yes | 365 | 0 | 0 | 0 | 0 | 3
2017 | 22-03-2017 18:48:00 CET | Rwanda | Rulindo | Kinihira | Butunzi | Gisekuru |  |  | Nyamagana-Kinihira | 143 | 0 | 15 | 0 | 80 | 63 | 55.94% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 864 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse ,Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 07:09:28 CET | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 325 | 26296 | 49 | 536.6531 | 69 | 256 | 21.23% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1001.7391 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2015 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 11:55:37 CET | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at Buyoga sector/Nyirambuga pumping | 177 | 30604 | 1 | 30604 | 177 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 488.1356 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 04-06-2017 13:21:35 CEST | Rwanda | Rulindo | Kisaro | Kamushenyi | Gatete |  |  | gahama | 163 | 10234 | 11 | 930.3636 | 130 | 33 | 79.75% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2012 | Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 65 | 26584.6154 | 40.8994 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 | Pressure Break Tank¦Distribution Chamber¦Washout,Air Release | 2012 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 10:08:22 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Rusana |  |  | Rwamugaza network | 276 | 14106 | 35 | 403.0286 | 276 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 417.3913 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-03-2017 18:30:09 CET | Rwanda | Rulindo | Kinihira | Butunzi | Kiniihira |  |  | Nyamagana-Kinihira | 118 | 0 | 15 | 0 | 60 | 58 | 50.85% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1152 | 1 | 1 | 1 | 2015 | 1 | 6000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 17:25:07 CET | Rwanda | Rulindo | Bushoki | Kayenzi | Rwanzu |  |  | Matonyanga source catchment | 154 | 0 | 1 | 0 | 154 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2017 | 1 | 40 | 43200 | 56.1039 | 1 | 1 | 1 | 2017 | 1 | 100 | 1 | 1 | 2017 | 1 | 0 |  |  |  |  | 1 | 2 | 2017 | 1 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 04-06-2017 15:33:12 CEST | Rwanda | Rulindo | Mbogo | Bukoro | Ruhanya |  |  | musenge | 25 | 6074 | 2 | 3037 | 25 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2014 | Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.8 | 360000 | 2880 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber¦Washout And Air Release | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 02-06-2017 09:40:52 CEST | Rwanda | Rulindo | Cyinzuzi | Migendezo | Gitabage |  |  | Kararama | 70 | 6572 | 4 | 1643 | 60 | 10 | 85.71% | 0 | 0 | 1 | Piped Network With Pump | 2009 | Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2009 | 1 | 4.5 | 384000 | 1280 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 7 | 2009 | 1 | 1 | 14 | Pressure Break Tank¦Distribution Chamber | 2009 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 1 | 2012 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 14-03-2017 23:03:30 CET | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Kingazi water point chez Rwigema/Nyakabizi gravity | 157 | 1259 | 1 | 1259 | 157 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 20 | 86400 | 110.0637 | 1 | 0 |  |  |  |  | 1 | 1 | 2013 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 05-04-2017 21:57:36 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Tare |  |  | Nyakariba-Tare gravity system | 109 | 9577 | 1 | 9577 | 109 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Loal Government In Ubudehe Program | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 79.2661 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 19:38:14 CET | Rwanda | Rulindo | Bushoki | Kayenzi | Rwanzu |  |  | Rwanzu2 wpt/Nyirambuga pumping | 154 | 30604 | 1 | 30604 | 154 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Gor | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 561.039 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 08-03-2017 19:08:20 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Gisiza |  |  | kinywamagana pumping network | 212 | 6436 | 26 | 247.5385 | 112 | 100 | 52.83% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 308.5714 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 03-01-2015 01:59:24 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Murambi2 water point/Nyirambuga pumping | 174 | 30604 | 1 | 30604 | 174 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 496.5517 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  | 2012 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 23-03-2017 11:45:11 CET | Rwanda | Rulindo | Masoro | Shengampuri | Amataba |  |  | Mutagata Gravity Network | 178 | 26296 | 12 | 2191.3333 | 126 | 52 | 70.79% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2004 | 2 | 8 | 216000 | 342.8571 | 1 | 1 | 1 | 2004 | 2 | 3500 | 1 | 6 | 2004 | 2 | 1 | 4 | Distribution Chamber¦Washout And Air Release Chamber | 2004 | 2 | 1 | 2 | 2004 | 2 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 12 | 2004 | 2 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 23-03-2017 18:41:52 CET | Rwanda | Rulindo | Murambi | Mugambazi | Nyarurembo |  |  | Mutagata motorised network | 144 | 26296 | 49 | 536.6531 | 56 | 88 | 38.89% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1234.2857 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 10:22:04 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyakambu |  |  | Rwamugaza network | 186 | 14106 | 35 | 403.0286 | 186 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 619.3548 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 16-03-2017 08:08:50 CET | Rwanda | Rulindo | Burega | Butangampundu | Gashinge |  |  | Rwamugaza | 435 | 14106 | 38 | 371.2105 | 435 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 2 | 2003 | 1 | 3.5 | 493714.2857 | 226.9951 | 1 | 1 | 1 | 2003 | 1 | 8000 | 1 | 10 | 2014 | 1 | 1 | 8 |  | 2014 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 16-03-2017 07:47:23 CET | Rwanda | Rulindo | Burega | Butangampundu | Kibiraro |  |  | Rwamugaza | 500 | 14106 | 38 | 371.2105 | 500 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 2 | 2003 | 1 | 3.5 | 493714.2857 | 197.4857 | 1 | 1 | 1 | 2014 | 1 | 8000 | 1 | 20 | 2003 | 1 | 1 | 16 |  | 2014 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 3 | Yes | 5 | 25 | 0 | 125 | 0 | 3
2017 | 06-03-2017 10:16:53 CET | Rwanda | Rulindo | Murambi | Mugambazi | Amahoro |  |  |  | 120 | 26296 | 31 | 848.2581 | 120 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring¦Null | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 1 | 3.2 | 540000 | 900 | 1 | 1 | 2 | 2016 | 1 | 5300 | 1 | 24 | 2016 | 1 | 1 | 2 | Distribution Chamber | 2016 | 1 | 1 | 2 | 2016 | 1 | 17200 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 32 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 11:30:37 CET | Rwanda | Rulindo | Masoro | Shengampuri | Umubuga |  |  | Mutagata Gravity Network | 175 | 26296 | 12 | 2191.3333 | 54 | 121 | 30.86% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2004 | 2 | 8 | 216000 | 800 | 1 | 1 | 1 | 2004 | 2 | 3500 | 1 | 6 | 2004 | 2 | 1 | 4 | Distribution Chamber¦Washout And Air Release Chamber | 2004 | 2 | 1 | 2 | 2004 | 2 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 12 | 2004 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 16-03-2017 06:46:04 CET | Rwanda | Rulindo | Burega | Taba | Mwenene |  |  | Rwamugaza | 445 | 14106 | 38 | 371.2105 | 445 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 172.5843 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 3 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 09-03-2017 19:13:39 CET | Rwanda | Rulindo | Shyorongi | Rubona | Nyabitare |  |  | Gisoro-Nyundo network | 130 | 2297 | 2 | 1148.5 | 52 | 78 | 40% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 13 | 132923.0769 | 511.2426 | 1 | 1 | 1 | 2013 | 1 | 30 | 1 | 6 | 2013 | 2 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 7000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 14:57:10 CEST | Rwanda | Rulindo | Ngoma | Karambo | Nyakagezi |  |  | Sehuta | 99 | 0 | 2 | 0 | 39 | 60 | 39.39% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 30 | 57600 | 295.3846 | 1 | 1 | 1 | 2014 | 1 | 1500 | 1 | 1 | 2014 | 1 | 0 |  |  |  |  | 1 | 1 | 2014 | 1 | 200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 10:06:57 CET | Rwanda | Rulindo | Murambi | Bubangu | Gashubi |  |  | Mutagata Motorised Network | 140 | 26296 | 49 | 536.6531 | 29 | 111 | 20.71% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 2383.4483 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 14:10:45 CET | Rwanda | Rulindo | Rukozo | Mbuye | Musare |  |  | Kabonanyoni | 80 | 7894 | 30 | 263.1333 | 70 | 10 | 87.5% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 329.1429 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 2015 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 15:50:02 CET | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | Nyagahera | 151 | 0 | 4 | 0 | 140 | 11 | 92.72% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 16 | 108000 | 154.2857 | 1 | 1 | 1 | 2014 | 1 | 6800 | 1 | 3 | 20114 | 2 | 1 | 3 | Distribution Chamber | 2014 | 1 | 1 | 1 | 2014 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 16-04-2017 22:16:32 CEST | Rwanda | Rulindo | Base | Gitare | Rugerero |  |  | Water point at Mbarusha/Nyirambuga pumping system | 143 | 30604 | 1 | 30604 | 143 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 604.1958 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 12:43:37 CET | Rwanda | Rulindo | Buyoga | Busoro | Karambo |  |  | Water point2 at Gakoma/Nyirambuga pumping | 138 | 30604 | 1 | 30604 | 138 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 626.087 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 07:52:31 CET | Rwanda | Rulindo | Burega | Butangampundu | Karambi |  |  | Rwamugaza | 365 | 14106 | 38 | 371.2105 | 365 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 2 | 2003 | 1 | 3.5 | 493714.2857 | 270.5284 | 1 | 1 | 1 | 2014 | 1 | 8000 | 1 | 10 | 2003 | 2 | 1 | 8 |  | 2003 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 09-03-2017 17:18:46 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Nyamirembe |  |  | kirikumuryango network | 256 | 0 | 26 | 0 | 120 | 136 | 46.88% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 261.8182 | 1 | 1 | 500 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 10000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 06:05:23 CET | Rwanda | Rulindo | Base | Rwamahwa | Kabahama |  |  | Migogo | 178 | 558 | 10 | 55.8 | 150 | 28 | 84.27% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2009 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2009 | 1 | 50 | 34560 | 46.08 | 1 | 1 | 1 | 2009 | 2 | 6800 | 1 | 3 | 2009 | 2 | 0 |  |  |  |  | 1 | 1 | 2009 | 2 | 6800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2009 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 24-03-2017 11:32:42 CET | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo |  |  |  | 203 | 0 | 31 | 0 | 203 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 85.1232 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 1 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 12:41:45 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Kagunda |  |  | Muvumu-Taba | 94 | 0 | 2 | 0 | 30 | 64 | 31.91% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 25 | 69120 | 460.8 | 1 | 1 | 1 | 2013 | 1 | 800 | 1 | 3 | 2013 | 2 | 1 | 9 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 7500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | Yes | 1 | 3 | 0 | 3 | 1 | 2
2017 | 16-03-2017 08:27:29 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kamatongo |  |  | 0 | 1125 | 6572 | 15 | 438.1333 | 1125 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 1 | 2016 | 1 | 3 | 576000 | 102.4 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 3 | 2016 | 1 | 1 | 6 |  | 2016 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 3 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 03-01-2015 01:42:15 CET | Rwanda | Rulindo | Tumba | Barari | Rukore |  |  | Water point at Rukore center/Nyirambuga pumping | 157 | 30604 | 1 | 30604 | 157 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 550.3185 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 1 | 2 | 2015 | 1 | 2000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 13:58:10 CET | Rwanda | Rulindo | Rukozo | Buraro | Nyenyeri |  |  | Kabonanyoni | 45 | 7894 | 30 | 263.1333 | 40 | 5 | 88.89% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 576 | 1 | 1 | 1 | 2015 | 2 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 06:26:25 CET | Rwanda | Rulindo | Kisaro | Sayo | Cyasuli |  |  | Kiruruma | 129 | 8295 | 25 | 331.8 | 122 | 7 | 94.57% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2014 | 1 | 3 | 576000 | 944.2623 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 15 | 2014 | 1 | 1 | 4 | Sedimentation Tank | 2014 | 1 | 1 | 3 | 2014 | 1 | 4000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 09:31:09 CEST | Rwanda | Rulindo | Kisaro | Kamushenyi | Gakenke |  |  | Gahama Kisaro network | 173 | 10234 | 14 | 731 | 173 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 |  | 1 | 2012 | 1 | 3 | 576000 | 665.896 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 |  | 2012 | 2 | 1 | 1 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 2 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 13-03-2017 22:10:27 CET | Rwanda | Rulindo | Bushoki | Giko | Kivomo |  |  | Kivomo2 water point/Buramira gravity | 127 | 1255 | 1 | 1255 | 127 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 30 | 57600 | 90.7087 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 01-01-2015 19:47:40 CET | Rwanda | Rulindo | Cyungo | Rwili | Nturo |  |  | Sakara | 570 | 0 | 4 | 0 | 520 | 50 | 91.23% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 132.9231 | 1 | 1 | 1 | 2015 | 1 | 1200 | 1 | 2 | 2015 | 1 | 1 | 5 | Distribution Chamber | 2015 | 1 | 1 | 1 | 2016 | 1 | 2300 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 13:51:44 CET | Rwanda | Rulindo | Rukozo | Buraro | Rukingu |  |  | Kabonanyoni | 30 | 7894 | 30 | 263.1333 | 25 | 5 | 83.33% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 921.6 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 02:13:44 CET | Rwanda | Rulindo | Tumba | Barari | Karambi |  |  | Karambi water point/Nyirambuga pumping | 170 | 30604 | 1 | 30604 | 170 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 508.2353 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 06:57:04 CET | Rwanda | Rulindo | Burega | Karengeli | Rwamiko |  |  | Rwamugaza | 440 | 14106 | 38 | 371.2105 | 440 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 174.5455 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 23-04-2017 14:44:25 CEST | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | kiduha | 151 | 0 | 7 | 0 | 105 | 46 | 69.54% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 1097.1429 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 11 | 2014 | 1 | 0 |  |  |  |  | 1 | 32 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 14-03-2017 22:38:40 CET | Rwanda | Rulindo | Rusiga | Kirenge | Rebero |  |  | Kigarama source/AEP Kigarama | 243 | 2621 | 1 | 2621 | 243 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Gor | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 40 | 43200 | 35.5556 | 1 | 1 | 1 | 2015 | 1 | 100 | 1 | 1 | 2015 | 1 | 1 | 1 | Distribution Chamber | 2015 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 20:07:16 CET | Rwanda | Rulindo | Bushoki | Kayenzi | Gitaba |  |  | Gitaba water point/Nyirambuga pumping | 118 | 30604 | 1 | 30604 | 118 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Gor | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 732.2034 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 17:00:51 CET | Rwanda | Rulindo | Kinihira | Rebero | Kirwa |  |  | Miyove-Kinihira | 187 | 10452 | 19 | 550.1053 | 95 | 92 | 50.8% | 0 | 0 | 1 | Piped Network -- Gravity Only | 1989 | Kgww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 727.5789 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 20:57:53 CET | Rwanda | Rulindo | Mbogo | Bukoro | Gihonga |  |  | Kibuye | 110 | 1232 | 3 | 410.6667 | 50 | 60 | 45.45% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | Start And Collection Chamber | 2 | 2016 | 1 | 45 | 38400 | 153.6 | 1 | 1 | 1 | 2016 | 1 | 1500 | 0 |  |  |  | 1 | 1 | Washout Chamber | 2016 | 1 | 1 | 1 | 2016 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 11-03-2017 10:02:18 CET | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 200 | 20456 | 36 | 568.2222 | 180 | 20 | 90% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 384 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 2 | Yes | 12 | 25 | 0 | 300 | 0 | 2
2017 | 14-03-2017 22:54:41 CET | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Nyakabizi1 source/Nyakabizi1 gravity-Gakenke | 200 | 1259 | 1 | 1259 | 200 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Gor | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 20 | 86400 | 86.4 | 1 | 1 | 1 | 2015 | 1 | 100 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 21:09:19 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 165 | 6436 | 26 | 247.5385 | 20 | 145 | 12.12% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 1728 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 12-03-2017 13:28:10 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Muvumu |  |  | Muvumu- Taba | 132 | 0 | 10 | 0 | 45 | 87 | 34.09% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 25 | 69120 | 307.2 | 1 | 1 | 1 | 2013 | 1 | 800 | 1 | 3 | 2013 | 2 | 1 | 9 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 7500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | Yes | 1 | 3 | 0 | 3 | 1 | 2
2017 | 12-03-2017 13:05:44 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Kiviri |  |  | Muvumu- Taba | 135 | 0 | 10 | 0 | 60 | 75 | 44.44% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 25 | 69120 | 230.4 | 1 | 1 | 1 | 2013 | 1 | 800 | 1 | 3 | 2013 | 2 | 1 | 9 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 7500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | Yes | 1 | 3 | 0 | 3 | 1 | 2
2017 | 23-04-2017 12:42:28 CEST | Rwanda | Rulindo | Base | Gitare | Bushyiga |  |  | Gihanga | 170 | 2456 | 10 | 245.6 | 150 | 20 | 88.24% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 0 |  |  |  |  | 75 | 23040 | 30.72 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1978 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 21-03-2017 13:47:47 CET | Rwanda | Gicumbi | Miyove | Mubuga | Gatare |  |  | Kabonanyoni | 30 | 7894 | 30 | 263.1333 | 20 | 10 | 66.67% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 1152 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-04-2017 14:44:09 CEST | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | kiduha | 151 | 0 | 7 | 0 | 100 | 51 | 66.23% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 1152 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 11 | 2014 | 1 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 05-04-2017 20:10:01 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Terambere |  |  | Rutare-Nyirangarama gravity system/Water point at Terambere | 118 | 726 | 1 | 726 | 118 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 1960 | Government | Spring | 1 | 1 | 0 |  |  |  |  | 20 | 86400 | 146.4407 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1960 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 21-03-2017 13:53:00 CET | Rwanda | Rulindo | Rukozo | Buraro | Kabingo |  |  | Kabonanyoni | 40 | 7894 | 30 | 263.1333 | 35 | 5 | 87.5% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 658.2857 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-03-2017 20:22:48 CET | Rwanda | Rulindo | Murambi | Mvuzo | Rurama |  |  | Mutagata Motorised Network | 155 | 26296 | 49 | 536.6531 | 43 | 112 | 27.74% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 1607.4419 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout ,Air Release And Chlorination Chambre | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2016 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-03-2017 14:22:31 CET | Rwanda | Rulindo | Rusiga | Taba | Karambi |  |  | Water point at GS Gitanda/Nyakabizi gravity | 109 | 1259 | 1 | 1259 | 109 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 40 | 43200 | 79.2661 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 16-03-2017 08:54:52 CET | Rwanda | Rulindo | Mbogo | Bukro | Buhira |  |  | Musenge Network | 52 | 6074 | 29 | 209.4483 | 52 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1496.8815 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 3 | Yes | 8 | 30 | 0 | 240 | 0 | 3
2017 | 18-04-2017 07:01:46 CEST | Rwanda | Rulindo | Tumba | Gahabwa | Mafene |  |  | Water point chez Mukamponga/Nyirambuga pumping system | 172 | 30604 | 1 | 30604 | 172 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 401.8605 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 21:16:00 CET | Rwanda | Rulindo | Bushoki | Giko | Cyili |  |  | Cyili water point/Rutomvu gravity | 169 | 3015 | 1 | 3015 | 169 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 51.1243 | 1 | 0 |  |  |  |  | 1 | 1 | 2013 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 22:44:04 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Nyabisindu |  |  | kirikumuryango network | 149 | 0 | 26 | 0 | 38 | 111 | 25.5% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 826.7943 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 25-03-2017 10:50:31 CET | Rwanda | Rulindo | Masoro | Shengampuri | Rusine |  |  | Mutagata Gravity network | 220 | 26296 | 12 | 2191.3333 | 220 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2004 | 2 | 8 | 216000 | 196.3636 | 1 | 1 | 1 | 2004 | 2 | 3500 | 1 | 6 | 2004 | 2 | 1 | 4 | Distribution Chamber¦Washout And Air Release | 2004 | 2 | 1 | 2 | 2004 | 2 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 12 | 2004 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 14-03-2017 22:12:19 CET | Rwanda | Rulindo | Mbogo | Bukoro | Kinini/Mbogo |  |  | Kinini-Mbogo water point/Ntaruka-Gahama gravity | 188 | 1567 | 1 | 1567 | 188 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2006 | Gor | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2006 | 1 | 40 | 43200 | 45.9574 | 1 | 1 | 1 | 2006 | 1 | 100 | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2006 | 2 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 23-04-2017 14:42:02 CEST | Rwanda | Rulindo | Buyoga | Mwumba | Nyarubuye |  |  | kiruruma | 173 | 8295 | 25 | 331.8 | 120 | 53 | 69.36% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 30 | 57600 | 96 | 1 | 1 | 1 | 2014 | 1 | 6700 | 1 | 5 | 2014 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 04-06-2017 13:25:29 CEST | Rwanda | Rulindo | Kisaro | Murama | Mugomero |  |  | gahama | 129 | 10234 | 11 | 930.3636 | 100 | 29 | 77.52% | 0 | 0 | 1 | Piped Network With Pump | 2012 | Waterforpeople | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 20 | 86400 | 172.8 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 | Pressure Break Tank¦Distribution Chamber¦Washout,Air Release | 2012 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 14:05:23 CET | Rwanda | Rulindo | Rukozo | Buraro | Kabgayi |  |  | Kabonanyoni | 60 | 7894 | 30 | 263.1333 | 55 | 5 | 91.67% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 418.9091 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 17-03-2017 05:24:57 CET | Rwanda | Rulindo | Mbogo | Rurenge | Gakoma |  |  | Musenge network | 146 | 6074 | 29 | 209.4483 | 46 | 100 | 31.51% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1692.1269 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Washout And Air Release Chamber | 2014 | 1 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 17:41:51 CEST | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | Nkanga center water point/Kivomo-Ntakara gravity | 129 | 0 | 1 | 0 | 129 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 50 | 34560 | 53.5814 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 12-03-2017 13:32:54 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Nyabubare |  |  | Muvumu- Taba | 97 | 0 | 10 | 0 | 40 | 57 | 41.24% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 25 | 69120 | 345.6 | 1 | 1 | 1 | 2013 | 1 | 800 | 1 | 3 | 2013 | 2 | 1 | 9 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 7500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | Yes | 1 | 3 | 0 | 3 | 1 | 2
2017 | 21-03-2017 14:19:30 CET | Rwanda | Rulindo | Kinihira | Karegamazi | Mutoyi |  |  | Miyove-Kinihira | 119 | 10452 | 19 | 550.1053 | 60 | 59 | 50.42% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 1152 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 27-03-2017 07:17:48 CEST | Rwanda | Rulindo | Buyoga | Ndarage | Gahondo |  |  | Ndarage | 105 | 0 | 9 | 0 | 100 | 5 | 95.24% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2014 | 1 | 30 | 57600 | 115.2 | 1 | 1 | 1 | 2014 | 1 | 6300 | 1 | 5 | 2014 | 1 | 1 | 8 | Distribution Chamber | 2014 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 14:45:32 CEST | Rwanda | Rulindo | Mbogo | Mushali | Gitaba |  |  | Gitabage Network | 118 | 0 | 3 | 0 | 68 | 50 | 57.63% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2008 | Catholic Church | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2008 | 1 | 40 | 43200 | 127.0588 | 1 | 1 | 1 | 2008 | 1 | 700 | 1 | 2 | 2008 | 1 | 0 |  |  |  |  | 1 | 1 | 2008 | 1 | 500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2008 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 02:15:31 CET | Rwanda | Rulindo | Tumba | Barari | Karambi |  |  | Karambi2 water point/Nyirambuga pumping | 170 | 30604 | 1 | 30604 | 170 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 508.2353 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 20:20:11 CET | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | kinywamagana pumping network | 281 | 6436 | 26 | 247.5385 | 50 | 231 | 17.79% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 691.2 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 16-04-2017 21:07:26 CEST | Rwanda | Rulindo | Bushoki | Mukoto | Mukoto |  |  | Mukoto water point/Nyagahondo gravity system | 119 | 844 | 1 | 844 | 119 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2010 | Caritas | Spring | 1 | 1 | 0 |  |  |  |  | 30 | 57600 | 96.8067 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2010 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 22-03-2017 19:12:31 CET | Rwanda | Rulindo | Kinihira | Butunzi | Ndorandi |  |  | Nyamagana-Kinihira | 139 | 0 | 15 | 0 | 50 | 89 | 35.97% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1382.4 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse,Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:38:05 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kigarama |  |  | charity water 203.031 | 1165 | 6572 | 1 | 6572 | 1165 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2016 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 1 | 2016 | 1 | 3 | 576000 | 98.8841 | 1 | 1 | 1 | 2016 | 1 | 35000 | 1 | 10 | 2016 | 1 | 1 | 8 |  | 2016 | 1 | 1 | 1 | 2016 | 1 | 1000 | 1 | 3 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 12:26:42 CET | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point for People near Buyoga secondary school/Nyirambuga pumping | 177 | 30604 | 1 | 30604 | 177 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 488.1356 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 02-01-2015 13:12:45 CET | Rwanda | Rulindo | Buyoga | Karama | Cyasenga |  |  | Water point at grouped area of Cyasenga/Nyirambuga | 165 | 30604 | 1 | 30604 | 165 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 523.6364 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-03-2017 14:30:06 CET | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point[Charity:Water203.148]/AEP Kigarama gravity | 243 | 2621 | 1 | 2621 | 243 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 35.5556 | 1 | 0 |  |  |  |  | 1 | 1 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 14-03-2017 22:20:08 CET | Rwanda | Rulindo | Rusiga | Kirenge | Ntaruka |  |  | Ntaruka source/Ntaruka-Gahama gravity | 176 | 1567 | 1 | 1567 | 176 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2006 | Gor | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2006 | 1 | 40 | 43200 | 49.0909 | 1 | 1 | 1 | 2006 | 1 | 100 | 1 | 1 | 2006 | 1 | 0 |  |  |  |  | 1 | 1 | 2006 | 1 | 1000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2006 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 14-04-2017 22:27:58 CEST | Rwanda | Rulindo | Bushoki | Gasiza | Budaha |  |  | Budaha water point/Nkombe gravity system | 205 | 0 | 1 | 0 | 205 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2002 | Coforwa | Spring | 1 | 1 | 0 |  |  |  |  | 18 | 96000 | 93.6585 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2002 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 16-04-2017 22:31:15 CEST | Rwanda | Rulindo | Bushoki | Giko | Gashiru |  |  | Water point at Marembo center/Nyirambuga pumping system | 120 | 30604 | 1 | 30604 | 120 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 720 | 1 | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 01:36:41 CET | Rwanda | Rulindo | Base | Gitare | Nyamugali |  |  | Rutembe | 121 | 1012 | 7 | 144.5714 | 65 | 56 | 53.72% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 265.8462 | 1 | 1 | 1 | 2016 | 1 | 2500 | 1 | 1 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | Yes | 7 | 7 | 0 | 49 | 0 | 2
2017 | 10-03-2017 10:19:09 CET | Rwanda | Rulindo | Ngoma | Karambo | Karambi |  |  | Kabarore-Ngoma-Nyabuko network | 117 | 8284 | 14 | 591.7143 | 30 | 87 | 25.64% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 2 | 4 | 432000 | 2880 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-03-2017 18:56:58 CET | Rwanda | Rulindo | Kinihira | Butunzi | Kiniihira |  |  | Nyamagana-Kinihira | 118 | 0 | 15 | 0 | 60 | 58 | 50.85% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1152 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 08:31:03 CEST | Rwanda | Rulindo | Ntarabana | Mahaza | Karera |  |  | Rwamugaza network | 182 | 14106 | 35 | 403.0286 | 182 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 632.967 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-04-2017 23:51:27 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyarurama |  |  | Rwamugaza network | 168 | 14106 | 35 | 403.0286 | 168 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 685.7143 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 14 |  | 2003 | 1 | 1 | 1 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-04-2017 15:41:31 CEST | Rwanda | Rulindo | Base | Cyohoha | Gitwa |  |  | Gihanga | 104 | 2456 | 10 | 245.6 | 80 | 24 | 76.92% | 0 | 1 | 1 | Piped Network -- Gravity Only | 1980 | Governement (District, Wasac) And Water For People | Spring | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 1985 | 1 | 60 | 28800 | 72 | 1 | 1 | 1 | 2014 | 1 | 5000 | 1 | 2 | 2014 | 2 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 1 | Yes | 2 | 2 | 0 | 4 | 0 | 2
2017 | 23-04-2017 14:41:22 CEST | Rwanda | Rulindo | Buyoga | Mwumba | Murambo |  |  | Kiruruma | 136 | 8295 | 25 | 331.8 | 100 | 36 | 73.53% | 0 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 1152 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 11 | 2014 | 1 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 9000 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 07-03-2017 09:51:30 CET | Rwanda | Rulindo | Cyungo | Marembo | Rusayo |  |  | Nyabirarama | 150 | 0 | 2 | 0 | 100 | 50 | 66.67% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 150 | 11520 | 23.04 | 1 | 1 | 1 | 2015 | 1 | 1200 | 1 | 1 | 2015 | 1 | 1 | 1 | Distribution Chamber | 2015 | 1 | 1 | 1 | 2015 | 1 | 1200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 25-04-2017 17:05:28 CEST | Rwanda | Rulindo | Cyinzuzi | Rudogo | Gaseke |  |  | Nyamateke network | 127 | 0 | 2 | 0 | 127 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 0 | 1 |  | 1 | 2003 | 1 | 20 | 86400 | 136.063 | 1 | 1 | 2 | 2011 | 1 | 30000 | 1 | 5 | 2003 | 2 | 1 | 6 |  | 2003 | 3 | 1 | 1 | 2011 | 1 | 30000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 08-03-2017 18:41:59 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Kiziranyenzi |  |  | kinywamagana pumping network | 140 | 6436 | 26 | 247.5385 | 40 | 100 | 28.57% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 864 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 05-04-2017 20:56:20 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Terambere |  |  | Rutare-Nyirangarama gravity system/Terambere water point | 118 | 726 | 1 | 726 | 118 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 1960 | Government | Spring | 1 | 1 | 0 |  |  |  |  | 20 | 86400 | 146.4407 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  | 1960 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 03-01-2015 00:33:43 CET | Rwanda | Rulindo | Tumba | Taba | Nyirataba |  |  | Water point at EP Ruvumba/Nyirambuga pumping | 169 | 30604 | 1 | 30604 | 169 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 511.2426 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 6 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 14:01:43 CET | Rwanda | Rulindo | Rukozo | Buraro | Kabgayi |  |  | Kabonanyoni | 40 | 7894 | 30 | 263.1333 | 35 | 5 | 87.5% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 658.2857 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 15-04-2017 23:20:29 CEST | Rwanda | Rulindo | Rusiga | Gako | Kabunigu |  |  | Water point at Kabunigu/Tare-Rusiga pumping system | 219 | 9577 | 1 | 9577 | 219 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 39.4521 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 07:30:48 CET | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutembe | 229 | 1012 | 7 | 144.5714 | 229 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2009 | Padiri | Groundwater (Well, Etc.) | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 45 | 38400 | 33.5371 | 1 | 1 | 1 | 2016 | 1 | 2500 | 1 | 2 | 2009 | 2 | 0 |  |  |  |  | 1 | 2 | 2009 | 2 | 3000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 21-03-2017 15:33:40 CET | Rwanda | Rulindo | Kinihira | Rebero | Ndusu |  |  | Miyove-Kinihira | 146 | 10452 | 19 | 550.1053 | 120 | 26 | 82.19% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 576 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 20-04-2017 14:59:11 CEST | Rwanda | Rulindo | Ngoma | Karambo | Nyakagezi |  |  | Sehuta | 99 | 0 | 2 | 0 | 50 | 49 | 50.51% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 30 | 57600 | 230.4 | 1 | 1 | 1 | 2014 | 1 | 1500 | 1 | 1 | 2014 | 1 | 0 |  |  |  |  | 1 | 1 | 2014 | 1 | 200 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 21:31:04 CET | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Bitete-Rwahi network | 188 | 1316 | 15 | 87.7333 | 20 | 168 | 10.64% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 1440 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 08:32:28 CEST | Rwanda | Rulindo | Tumba | Nyirabirori | Rusura |  |  | Water point near Rusura center/Nyirambuga pumping | 157 | 30604 | 1 | 30604 | 157 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 |  | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 440.2548 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 1 | 100 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 11:38:28 CET | Rwanda | Rulindo | Masoro | Kigarama | Nyakibungo |  |  |  | 229 | 0 | 31 | 0 | 229 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 75.4585 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 09:08:58 CET | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 1789 | 14 | 127.7857 | 100 | 92 | 52.08% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2017 | Padiri | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2017 | 1 | 120 | 14400 | 28.8 | 1 | 0 |  | 2016 | 1 | 6450 | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 18-04-2017 20:14:38 CEST | Rwanda | Rulindo | Tumba | Taba | Ruvumba |  |  | Water point chez Fari/Nyirambuga pumping | 109 | 30604 | 1 | 30604 | 109 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 634.1284 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 13:50:44 CET | Rwanda | Rulindo | Rukozo | Buraro | Rukingu |  |  | Kabonanyoni | 70 | 7894 | 30 | 263.1333 | 65 | 5 | 92.86% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 354.4615 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 02:04:20 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point1 at ADEPR PEPO Tumba/Nyirambuga pumping | 169 | 30604 | 1 | 30604 | 169 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 511.2426 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:55:39 CET | Rwanda | Rulindo | Mbogo | Bukoro | Kibamba |  |  | Musenge Network | 76 | 6074 | 29 | 209.4483 | 76 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 2014 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1024.1821 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 3 | Yes | 8 | 30 | 0 | 240 | 0 | 3
2017 | 11-03-2017 10:27:01 CET | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 70 | 20456 | 36 | 568.2222 | 30 | 40 | 42.86% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 2304 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 10 | 25 | 0 | 250 | 0 | 2
2017 | 09-03-2017 19:26:48 CET | Rwanda | Rulindo | Shyorongi | Rubona | Nyarusange |  |  | Gisoro- Nyundo network | 97 | 2297 | 10 | 229.7 | 45 | 52 | 46.39% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 13 | 132923.0769 | 590.7692 | 1 | 1 | 1 | 2013 | 1 | 30 | 1 | 6 | 2013 | 2 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 7000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-06-2017 09:24:25 CEST | Rwanda | Rulindo | Cyinzuzi | Migendezo | Rusagara |  |  | Kararama | 98 | 6572 | 4 | 1643 | 90 | 8 | 91.84% | 0 | 0 | 1 | Piped Network With Pump | 2009 | Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2012 | 1 | 4.5 | 384000 | 853.3333 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 7 | 2009 | 1 | 1 | 14 | Pressure Break Tank¦Distribution Chamber | 2009 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 1 | 2012 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-04-2017 14:42:09 CEST | Rwanda | Rulindo | Buyoga | Ndarage | Kagozi |  |  | ndarage | 155 | 0 | 9 | 0 | 130 | 25 | 83.87% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 30 | 57600 | 88.6154 | 1 | 1 | 1 | 2014 | 1 | 6700 | 1 | 5 | 2014 | 1 | 0 |  |  |  |  | 1 | 1 | 2014 | 1 | 6700 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-04-2017 22:55:03 CEST | Rwanda | Rulindo | Buyoga | Karama | Kajeneni |  |  | Kajeneni water point/Nyirambuga pumping system | 175 | 30604 | 1 | 30604 | 175 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 493.7143 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 08-03-2017 22:31:24 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Bugarura |  |  | kirikumuryango network | 119 | 0 | 26 | 0 | 35 | 84 | 29.41% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 897.6623 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 00:46:04 CET | Rwanda | Rulindo | Tumba | Taba | Nyirataba |  |  | Nyirataba2 water point/Nyirambuga pumping | 169 | 30604 | 1 | 30604 | 169 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 511.2426 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 05:58:17 CET | Rwanda | Rulindo | Cyungo | Burehe | Nyagatovu |  |  | Nyamagana | 50 | 20456 | 36 | 568.2222 | 45 | 5 | 90% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1536 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 10 | 30 | 0 | 300 | 1 | 2
2017 | 21-03-2017 14:03:49 CET | Rwanda | Rulindo | Rukozo | Buraro | Kamiyove |  |  | Kabonanyoni | 70 | 7894 | 30 | 263.1333 | 65 | 5 | 92.86% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 354.4615 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 3 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 07-03-2017 13:21:14 CET | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 1789 | 14 | 127.7857 | 100 | 92 | 52.08% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2012 | Padiri | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 40 | 43200 | 86.4 | 1 | 1 | 2 | 2012 | 1 | 6450 | 1 | 3 | 2012 | 1 | 1 | 3 | Distribution Chamber | 2012 | 1 | 1 | 2 | 2012 | 2 | 6800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 3 | Yes | 365 | 0 | 0 | 0 | 0 | 2
2017 | 03-01-2015 02:20:59 CET | Rwanda | Rulindo | Tumba | Barari | Gaseke |  |  | Water point at Gashora/Nyirambuga pumping | 149 | 30604 | 1 | 30604 | 149 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 579.8658 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 05:50:24 CET | Rwanda | Rulindo | Base | Cyohoha | Gihemba |  |  | Nyamagana | 100 | 20456 | 36 | 568.2222 | 90 | 10 | 90% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 768 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 7 | 30 | 0 | 210 | 1 | 2
2017 | 20-04-2017 07:53:42 CEST | Rwanda | Rulindo | Tumba | Misezero | Taba |  |  | Water point at Taba/Nyirambuga pumping | 100 | 30604 | 1 | 30604 | 100 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 691.2 | 1 | 0 |  |  |  |  | 0 |  |  |  | 1 | 1 | Distribution Chamber | 2012 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:49:45 CET | Rwanda | Rulindo | Mbogo | Bukoro | Kalindi |  |  | Musenge Network | 55 | 6074 | 29 | 209.4483 | 55 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 2014 | Wfp | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1415.2334 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber¦Washout And Air Release | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 3 | Yes | 8 | 30 | 0 | 240 | 0 | 3
2017 | 16-03-2017 08:54:10 CET | Rwanda | Rulindo | Mbogo | Rurenge | Gicumbi |  |  | Musenge Network | 141 | 6074 | 29 | 209.4483 | 35 | 106 | 24.82% | 0 | 1 | 1 | Piped Network With Pump | 2014 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 2223.9382 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber¦Washout And Air Release | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 3 | Yes | 8 | 30 | 0 | 240 | 0 | 3
2017 | 13-03-2017 21:04:55 CET | Rwanda | Rulindo | Base | Gitare | Gihora |  |  | Gihora2 Water point/Rutomvu gravity | 101 | 3015 | 2 | 1507.5 | 101 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Gor | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 85.5446 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-04-2017 23:17:19 CEST | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | Water point at GS Rusiga/Tare-Rusiga pumping | 281 | 9577 | 1 | 9577 | 281 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 30.7473 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 06:59:33 CET | Rwanda | Rulindo | Kinihira | Marembo | Gatare |  |  | Nyamagana- Kinihira | 160 | 0 | 4 | 0 | 80 | 80 | 50% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 864 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 7 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 20:14:35 CET | Rwanda | Rulindo | Masoro | Kivugiza | Gasenga |  |  | Mutagata motorised network | 284 | 26296 | 49 | 536.6531 | 146 | 138 | 51.41% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 473.4247 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 22-03-2017 14:19:00 CET | Rwanda | Rulindo | Rusiga | Taba | Karambi |  |  | Karambi water point/Nyakabizi gravity | 109 | 1259 | 1 | 1259 | 109 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 40 | 43200 | 79.2661 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 25-04-2017 16:36:28 CEST | Rwanda | Rulindo | Cyinzuzi | Rudogo | Munoga |  |  |  | 98 | 0 | 31 | 0 | 98 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 1 | 1 | 1 |  | 1 | 2011 | 2 | 50 | 34560 | 70.5306 | 1 | 1 | 2 | 2011 | 1 | 30000 | 1 | 5 | 2011 | 1 | 1 | 6 |  | 2011 | 1 | 1 | 1 | 2011 | 1 | 30000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 17-03-2017 05:22:03 CET | Rwanda | Rulindo | Mbogo | Rurenge | Ruhondo |  |  | Musenge network | 184 | 6074 | 29 | 209.4483 | 39 | 145 | 21.2% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1995.842 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Washout And Air Release Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 22:26:59 CET | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Bitete-Rwahi network | 188 | 1316 | 15 | 87.7333 | 30 | 158 | 15.96% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 960 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 21:17:15 CET | Rwanda | Rulindo | Base | Cyohoha | Bukangano |  |  | Migogo | 129 | 558 | 10 | 55.8 | 120 | 9 | 93.02% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2009 | Italians(Lake Angels) | Groundwater (Well, Etc.)¦Lake/Reservoir | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2009 | 1 | 20 | 86400 | 144 | 1 | 1 | 2 | 2009 | 2 | 3000 | 1 | 3 | 2009 | 2 | 0 |  |  |  |  | 1 | 2 | 2009 | 2 | 3000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2009 | 2 | Yes | 4 | 2 | 0 | 8 | 1 | 2
2017 | 23-04-2017 14:41:05 CEST | Rwanda | Rulindo | Buyoga | Gahororo | Gatare |  |  | kiruruma | 169 | 8295 | 25 | 331.8 | 120 | 49 | 71.01% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 960 | 1 | 1 | 2 | 2014 | 1 | 4200 | 1 | 11 | 2014 | 1 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 4200 | 1 | 2 | 2014 | 1 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 25-04-2017 16:43:25 CEST | Rwanda | Rulindo | Cyinzuzi | Rudogo | Kirambo |  |  | Nyamateke source | 137 | 0 | 1 | 0 | 137 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 1 | 1 | 1 |  | 1 | 2003 | 1 | 50 | 34560 | 50.4526 | 1 | 1 | 2 | 2003 | 1 | 30000 | 1 | 5 | 2003 | 1 | 1 | 6 |  | 2003 | 1 | 1 | 1 | 2003 | 1 | 30000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 21-03-2017 14:15:26 CET | Rwanda | Rulindo | Rukozo | Mbuye | Mujebe |  |  | Kabonanyoni | 90 | 7894 | 30 | 263.1333 | 80 | 10 | 88.89% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 288 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 25-04-2017 17:04:44 CEST | Rwanda | Rulindo | Cyinzuzi | Rudogo | Kirambo |  |  | Nyamateke network | 137 | 0 | 2 | 0 | 137 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 120 | 14400 | 21.0219 | 1 | 1 | 2 | 2003 | 1 | 30000 | 1 | 5 | 2003 | 2 | 1 | 14 |  | 2003 | 1 | 1 | 1 | 2003 | 1 | 30000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 23-03-2017 07:58:32 CET | Rwanda | Rulindo | Murambi | Mugambazi | Buliza |  |  | Mutagata Motorised Network | 221 | 26296 | 49 | 536.6531 | 100 | 121 | 45.25% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 691.2 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release Chamber | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 12:35:52 CET | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Tare-Rusiga water pumping system/Nyakabingo1 water spring source | 228 | 9577 | 1 | 9577 | 228 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 20 | 86400 | 75.7895 | 1 | 1 | 1 | 2015 | 1 | 400 | 1 | 2 | 2015 | 1 | 1 | 1 | Distribution Chamber | 2015 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 28-03-2017 08:14:03 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Kiyanza I |  |  | Rwamugaza network | 1025 | 14106 | 35 | 403.0286 | 1025 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 112.3902 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 21:57:31 CET | Rwanda | Rulindo | Bushoki | Giko | Ngarama |  |  | Ngarama2 water point/Nkore gravity | 110 | 0 | 1 | 0 | 110 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Private People Joined Hands Together To Get Water | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 78.5455 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 13-03-2017 07:06:01 CET | Rwanda | Rulindo | Ngoma | Munyarwanda | Busizi |  |  | Kabarore-Ngoma-Nyabuko network | 100 | 8284 | 14 | 591.7143 | 31 | 69 | 31% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 0 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 1 | 4 | 432000 | 2787.0968 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 4 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 2 | Yes | 1 | 10 | 0 | 10 | 1 | 1
2017 | 05-04-2017 21:51:28 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Tare |  |  | Nyabishengeshi gravity system | 109 | 893 | 2 | 446.5 | 109 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 50 | 34560 | 63.4128 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-04-2017 22:08:01 CEST | Rwanda | Rulindo | Bushoki | Giko | Rugote |  |  | Water point chez Jean de Dieu/Nyirambuga pumping system | 120 | 30604 | 1 | 30604 | 120 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 720 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 25-04-2017 00:03:40 CEST | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyagasozi |  |  | Rwamugaza network | 197 | 14106 | 35 | 403.0286 | 197 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 584.7716 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 14 |  | 2003 | 1 | 1 | 1 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 06:51:57 CET | Rwanda | Rulindo | Burega | Taba | Lyinzovu |  |  | Rwamugaza | 505 | 14106 | 38 | 371.2105 | 505 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 152.0792 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 22-03-2017 20:24:37 CET | Rwanda | Rulindo | Murambi | Mvuzo | Ntyaba |  |  | Mutagata Motorised Network | 136 | 26296 | 49 | 536.6531 | 136 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 508.2353 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 12:22:38 CET | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at Buyoga Banque Populaire/Nyirambuga pumping | 177 | 30604 | 1 | 30604 | 177 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 488.1356 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 6 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-04-2017 22:59:13 CEST | Rwanda | Rulindo | Buyoga | Karama | Kigarama |  |  | Kigarama water point/Nyirambuga pumping | 121 | 30604 | 1 | 30604 | 121 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 714.0496 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 3 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 15-04-2017 22:36:53 CEST | Rwanda | Rulindo | Bushoki | Gasiza | Buhande |  |  | Buhande water point/Tare-Rusiga pumping system | 129 | 9577 | 1 | 9577 | 129 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 10 | 1 | 0 |  |  |  |  | 40 | 43200 | 66.9767 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 05-04-2017 21:55:12 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Tare |  |  | Nyakariba-Tare small gravity system | 109 | 9577 | 1 | 9577 | 109 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Local Government In Ubudehe Program | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 40 | 43200 | 79.2661 | 1 | 1 | 1 | 2015 | 1 | 5 | 1 | 1 | 2015 | 1 | 1 | 1 | Distribution Chamber | 2015 | 1 | 1 | 1 | 2015 | 1 | 500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 04-06-2017 13:20:10 CEST | Rwanda | Rulindo | Kisaro | Kamushenyi | Gatete |  |  | gahama | 163 | 10234 | 11 | 930.3636 | 140 | 23 | 85.89% | 0 | 0 | 1 | Piped Network With Pump | 2012 | Waterforpeople | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 65 | 26584.6154 | 37.978 | 1 | 1 | 2 | 2012 | 1 | 12000 | 1 | 7 | 2012 | 1 | 1 | 14 | Pressure Break Tank¦Distribution Chamber¦Washout,Air Release | 2012 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 10:52:41 CET | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Remera water point from Rutare gravity on Tare pumping | 228 | 9577 | 1 | 9577 | 228 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 8 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2017 | 1 | 40 | 43200 | 37.8947 | 1 | 1 | 1 | 2015 | 1 | 2000 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 2000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 01-01-2015 20:20:32 CET | Rwanda | Rulindo | Cyungo | Rwili | Nyabisasa |  |  | Sakara | 570 | 0 | 4 | 0 | 520 | 50 | 91.23% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 132.9231 | 1 | 1 | 2 | 2015 | 1 | 1200 | 1 | 2 | 2015 | 1 | 1 | 5 | Distribution Chamber | 2015 | 1 | 1 | 1 | 2016 | 1 | 2300 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 22:07:57 CET | Rwanda | Rulindo | Shyorongi | Rubona | Nyarunyinya |  |  | Bitete-Rwahi network | 132 | 1316 | 15 | 87.7333 | 50 | 82 | 37.88% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 12 | 144000 | 576 | 1 | 1 | 1 | 2013 | 1 | 600 | 1 | 6 | 2013 | 2 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 6500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 06:45:59 CET | Rwanda | Rulindo | Ngoma | Munyarwanda | Busizi |  |  | Kabarore-Ngoma-Nyabuko network | 100 | 8284 | 14 | 591.7143 | 30 | 70 | 30% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 0 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 1 | 4 | 432000 | 2880 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 4 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 1 | Yes | 1 | 10 | 0 | 10 | 1 | 1
2017 | 17-03-2017 05:22:39 CET | Rwanda | Rulindo | Mbogo | Rurenge | Gakoma |  |  | Musenge network | 146 | 6074 | 29 | 209.4483 | 52 | 94 | 35.62% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1496.8815 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Washout And Air Release Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 12-03-2017 18:40:05 CET | Rwanda | Rulindo | Base | Gitare | Kirwa |  |  | Rwicanyoni | 136 | 698 | 7 | 99.7143 | 101 | 35 | 74.26% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 1 | 10 | 172800 | 342.1782 | 1 | 1 | 1 | 2016 | 1 | 8600 | 1 | 3 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 06-03-2017 10:30:33 CET | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  |  | 30 | 510 | 31 | 16.4516 | 30 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2015 | Wfp | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 20 | 86400 | 576 | 1 | 1 | 1 | 2015 | 1 | 1500 | 1 | 1 | 2015 | 1 | 1 | 3 | Valve Chamber | 2015 | 1 | 1 | 2 | 2015 | 1 | 500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2015 | 1 | Yes | 1 | 1 | 1 | 1 | 1 | 1
2017 | 20-04-2017 07:09:10 CEST | Rwanda | Rulindo | Tumba | Misezero | Kavumu |  |  | Water point chez Habarugira/Nyirambuga pumping | 139 | 30604 | 1 | 30604 | 139 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 497.2662 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 05-04-2017 21:23:59 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Ngarama |  |  | Nyabishengeshi gravity system/Water point at Nyirangarama | 89 | 893 | 1 | 893 | 89 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 50 | 34560 | 77.6629 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 00:16:44 CET | Rwanda | Rulindo | Tumba | Taba | Mwili |  |  | Mwili2 water point/Nyirambuga pumping | 141 | 30604 | 1 | 30604 | 141 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 612.766 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 07-03-2017 10:24:58 CET | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 1789 | 14 | 127.7857 | 100 | 92 | 52.08% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2012 | Padiri | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 60 | 28800 | 57.6 | 1 | 1 | 2 | 2012 | 1 | 6450 | 0 |  |  |  | 0 |  |  |  |  | 1 | 1 | 2012 | 1 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 16:13:36 CET | Rwanda | Rulindo | Kinihira | Rebero | Kirwa |  |  | Miyove-Kinihira | 187 | 10452 | 19 | 550.1053 | 60 | 127 | 32.09% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 1152 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1989 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 15-03-2017 06:05:53 CET | Rwanda | Rulindo | Base | Rwamahwa | Kabahama |  |  | Migogo | 178 | 558 | 10 | 55.8 | 150 | 28 | 84.27% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2009 | Padiri(Lake Angels). | Groundwater (Well, Etc.) | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2009 | 1 | 50 | 34560 | 46.08 | 1 | 1 | 2 | 2009 | 2 | 6200 | 1 | 1 | 2009 | 2 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2009 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 02-01-2015 05:49:39 CET | Rwanda | Rulindo | Cyungo | Rwili | Kabanda |  |  | Nyamagana | 50 | 20456 | 36 | 568.2222 | 26 | 24 | 52% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 2658.4615 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 2 | Yes | 7 | 30 | 0 | 210 | 0 | 2
2017 | 23-03-2017 10:37:38 CET | Rwanda | Rulindo | Murambi | Bubangu | Rebero |  |  | Mutagata Motorised Network | 148 | 26296 | 49 | 536.6531 | 78 | 70 | 52.7% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 886.1538 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release Chamber | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 10:26:01 CET | Rwanda | Rulindo | Murambi | Bubangu | Gashubi |  |  | Mutagata Motorised Network | 140 | 26296 | 49 | 536.6531 | 32 | 108 | 22.86% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 2160 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release Chamber | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 02:11:23 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | WATER POINT AT VTC TUMBA/Nyirambuga pumping | 169 | 30604 | 1 | 30604 | 169 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 511.2426 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 04:55:32 CET | Rwanda | Rulindo | Masoro | Kivugiza | Rebero |  |  | Mutagata motorised network | 376 | 26296 | 49 | 536.6531 | 115 | 261 | 30.59% | 0 | 0 | 1 | Piped Network With Pump | 1987 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2007 | 1 | 5 | 345600 | 601.0435 | 1 | 1 | 1 | 2016 | 1 | 1900 | 1 | 39 | 2016 | 1 | 1 | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air Release | 2016 | 1 | 1 | 6 | 2016 | 1 | 40000 | 1 | 5 | 2017 | 1 | 1 | 2016 | 1 | 1 | Disinfection/Chlorination | 2017 | 1 | 0 |  |  | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 64 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 04:51:31 CET | Rwanda | Rulindo | Rukozo | Buraro | Shyondwe |  |  | Kabonanyoni | 125 | 7894 | 30 | 263.1333 | 120 | 5 | 96% | 1 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 10 | 2015 | 1 | 15 | 115200 | 192 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 17:25:37 CET | Rwanda | Rulindo | Buyoga | Ndarage | Karambi |  |  | Ndarage | 112 | 0 | 9 | 0 | 100 | 12 | 89.29% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 30 | 57600 | 115.2 | 1 | 1 | 1 | 2014 | 1 | 6700 | 1 | 5 | 2014 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 22:23:35 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Mwagiro |  |  | Kirikumuryango network | 139 | 0 | 26 | 0 | 37 | 102 | 26.62% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 849.14 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 11-03-2017 08:57:18 CET | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 780 | 20456 | 36 | 568.2222 | 780 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 88.6154 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | Yes | 15 | 20 | 0 | 300 | 1 | 2
2017 | 15-03-2017 14:46:35 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kavumu |  |  | 0 | 850 | 6572 | 15 | 438.1333 | 850 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 90.3529 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 2 | 2014 | 3 | 1 | 8 | Pressure Break Tank | 2014 | 3 | 1 | 2 | 2014 | 3 | 3000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 3 | Yes | 365 | 0 | 0 | 0 | 0 | 3
2017 | 10-03-2017 12:18:57 CET | Rwanda | Rulindo | Bushoki | Mukoto | Marembo |  |  | Water point at GS Bushoki/Tare-Rusiga pumping system | 90 | 9577 | 1 | 9577 | 90 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 10 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 8 | 2015 | 1 | 40 | 43200 | 96 | 1 | 1 | 1 | 2015 | 1 | 4000 | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 8000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 11:03:35 CET | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 192 | 1789 | 14 | 127.7857 | 180 | 12 | 93.75% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2012 | Padiri | Spring¦Groundwater (Well, Etc.) | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 1 | 45 | 38400 | 42.6667 | 1 | 1 | 2 | 2016 | 1 | 6450 | 1 | 3 | 2016 | 1 | 1 | 1 | Distribution Chamber | 2016 | 1 | 1 | 2 | 2016 | 1 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 02:07:06 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point at ADEPR Tumba/Nyirambuga pumping | 169 | 30604 | 1 | 30604 | 169 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 511.2426 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-04-2017 23:55:56 CEST | Rwanda | Rulindo | Ntarabana | Mahaza | Karera |  |  | Rwamugaza network | 182 | 14106 | 35 | 403.0286 | 182 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 632.967 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 14 |  | 2003 | 1 | 1 | 1 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 04-06-2017 15:32:54 CEST | Rwanda | Rulindo | Mbogo | Bukoro | Ruhanya |  |  | musenge | 40 | 6074 | 2 | 3037 | 40 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2014 | Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.8 | 360000 | 1800 | 1 | 1 | 1 | 2014 | 2 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber¦Washout And Air Release Chamber | 2014 | 1 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 2 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 3 | Yes | 6 | 30 | 0 | 180 | 0 | 3
2017 | 15-03-2017 08:01:01 CET | Rwanda | Rulindo | Base | Cyohoha | Rubanda |  |  | Gihanga | 214 | 2456 | 10 | 245.6 | 200 | 14 | 93.46% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 15 | 115200 | 115.2 | 1 | 1 | 1 | 2016 | 2 | 7200 | 1 | 6 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 15-04-2017 22:17:25 CEST | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Water point at EP Gasiza/Nyagahondo gravity system | 228 | 844 | 1 | 844 | 228 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2010 | Caritas | Spring | 1 | 1 | 0 |  |  |  |  | 30 | 57600 | 50.5263 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2010 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 17:23:38 CET | Rwanda | Rulindo | Kinihira | Rebero | Karambi |  |  | Miyove-Kinihira | 144 | 10452 | 19 | 550.1053 | 60 | 84 | 41.67% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 1152 | 1 | 1 | 1 | 1989 | 2 | 8000 | 1 | 4 | 1989 | 1 | 1 | 18 | Distribution Chamber¦Ventouse ,Washout | 1989 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1989 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 28-03-2017 11:46:22 CEST | Rwanda | Rulindo | Ngoma | Mugote | Rukoma |  |  | Kararama pumping network | 92 | 6572 | 3 | 2190.6667 | 45 | 47 | 48.91% | 0 | 0 | 1 | Piped Network With Pump | 2007 | Government | Spring¦Collection Chamber | 4 | 0 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 3 | 2007 | 1 | 6 | 288000 | 1280 | 1 | 1 | 1 | 2007 | 1 | 1500 | 1 | 25 | 2007 | 1 | 1 | 20 | Distribution Chamber¦Washout And Air Release Chamber | 2007 | 1 | 1 | 4 | 2007 | 2 | 30000 | 1 | 2 | 2007 | 2 | 1 | 2007 | 2 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 47 | 2007 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 10-03-2017 10:18:00 CET | Rwanda | Rulindo | Ngoma | Kabuga | Kagarama |  |  | Kabarore- Ngoma- Nyabuko network | 57 | 8284 | 3 | 2761.3333 | 57 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 2 | 4 | 432000 | 1515.7895 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-04-2017 14:43:06 CEST | Rwanda | Rulindo | Buyoga | Gahororo | Gipfundo |  |  | rugarama | 162 | 0 | 1 | 0 | 120 | 42 | 74.07% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2012 | G. Thierry | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2012 | 1 | 30 | 57600 | 96 | 1 | 1 | 1 | 2012 | 1 | 4500 | 1 | 4 | 2012 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 05:51:13 CET | Rwanda | Rulindo | Cyungo | Burehe | Sove |  |  | Nyamagana | 75 | 20456 | 36 | 568.2222 | 35 | 40 | 46.67% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2011 | 1 | 5 | 345600 | 1974.8571 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 1 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 1 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 23-04-2017 14:43:38 CEST | Rwanda | Rulindo | Buyoga | Gahororo | Gatenderi |  |  | kiruruma | 141 | 8295 | 25 | 331.8 | 100 | 41 | 70.92% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2017 | 1 | 3 | 576000 | 1152 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 11 | 2014 | 1 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 9000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 08:08:33 CET | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutembe | 229 | 1012 | 7 | 144.5714 | 229 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2017 | 1 | 45 | 38400 | 33.5371 | 1 | 1 | 1 | 2017 | 1 | 2500 | 1 | 1 | 2016 | 1 | 1 | 3 | Distribution Chamber | 2016 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 16:54:52 CET | Rwanda | Rulindo | Rusiga | Gako | Kabuye |  |  | Kabuye water point[RW.WFP.Q3.14.166.066]/Tare-Rusiga pumping | 169 | 9577 | 1 | 9577 | 169 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 10 | 1 | 0 |  |  |  |  | 40 | 43200 | 51.1243 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 11:12:55 CET | Rwanda | Rulindo | Shyorongi | Muvumu | Nyabubare |  |  | Bitete-Muvumu | 97 | 1316 | 7 | 188 | 35 | 62 | 36.08% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 897.6623 | 1 | 1 | 1 | 2013 | 2 | 11 | 1 | 1 | 2013 | 1 | 1 | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 2 | 1 | 1 | 2013 | 1 | 4000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-06-2017 09:36:41 CEST | Rwanda | Rulindo | Cyinzuzi | Rudogo | Gasiza |  |  | Rwagitare | 45 | 0 | 2 | 0 | 40 | 5 | 88.89% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2009 | Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2009 | 1 | 1.2 | 1440000 | 7200 | 1 | 1 | 1 | 2009 | 1 | 1200 | 1 | 1 | 2009 | 1 | 1 | 2 | Pressure Break Tank¦Distribution Chamber | 2009 | 1 | 1 | 1 | 2009 | 1 | 900 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2009 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 11-03-2017 09:32:34 CET | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 1200 | 20456 | 36 | 568.2222 | 1200 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2011 | Government And African Development Bank | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 57.6 | 1 | 1 | 2 | 2015 | 1 | 2100 | 1 | 11 | 2011 | 1 | 1 | 15 | Pressure Break Tank¦Distribution Chamber | 2011 | 1 | 1 | 3 | 2011 | 2 | 37000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 29 | 2011 | 2 | Yes | 10 | 22 | 0 | 220 | 1 | 2
2017 | 22-03-2017 19:38:46 CET | Rwanda | Rulindo | Kinihira | Marembo | Cyogo |  |  | Nyamagana-Kinihira | 184 | 0 | 15 | 0 | 60 | 124 | 32.61% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1152 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 09:00:36 CET | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 19 | 911 | 5 | 182.2 | 19 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 1997 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | Start Chamber And Collection Chamber | 2 | 2016 | 1 | 30 | 57600 | 606.3158 | 1 | 1 | 1 | 2016 | 1 | 700 | 1 | 1 | 2016 | 1 | 1 | 2 | Washout Chamber, And Air Release Chamber | 2016 | 1 | 1 | 2 | 2016 | 1 | 800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 1997 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 06:27:06 CET | Rwanda | Rulindo | Buyoga | Gitumba | Munini |  |  | Kiruruma | 158 | 8295 | 25 | 331.8 | 152 | 6 | 96.2% | 1 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 3 | 576000 | 757.8947 | 1 | 1 | 3 | 2014 | 1 | 9000 | 1 | 15 | 2014 | 1 | 0 |  |  |  |  | 1 | 3 | 2014 | 1 | 9000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-06-2017 07:05:19 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyakambu |  |  | rwamugaza | 186 | 14106 | 38 | 371.2105 | 30 | 156 | 16.13% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2003 | 1 | 3 | 576000 | 3840 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 | Sedimentation Tank¦Pressure Break Tank¦Distribution Chamber | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2003 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 03-01-2015 01:55:03 CET | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Murambi water point/Nyirambuga pumping | 174 | 30604 | 1 | 30604 | 174 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 496.5517 | 1 | 0 |  |  |  |  | 1 | 1 | 2015 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:51:38 CET | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  |  | 186 | 510 | 31 | 16.4516 | 52 | 134 | 27.96% | 0 | 1 | 1 | Piped Network With Pump | 2014 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1496.8815 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 3 | Yes | 8 | 30 | 0 | 240 | 0 | 3
2017 | 24-03-2017 12:13:00 CET | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  |  | 214 | 0 | 31 | 0 | 214 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 1998 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 80.7477 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 12:30:04 CET | Rwanda | Rulindo | Rusiga | Taba | Bitare |  |  | Muvumu- Taba | 113 | 0 | 10 | 0 | 35 | 78 | 30.97% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2017 | 3 | 25 | 69120 | 394.9714 | 1 | 1 | 1 | 2013 | 1 | 800 | 1 | 3 | 2013 | 2 | 1 | 9 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 1 | 2013 | 1 | 7500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 3 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 28-03-2017 08:24:11 CEST | Rwanda | Rulindo | Ntarabana | Mahaza | Kayenzi |  |  | Rwamugaza network | 200 | 14106 | 35 | 403.0286 | 200 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 576 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 20-04-2017 07:05:00 CEST | Rwanda | Rulindo | Tumba | Misezero | Kavumu |  |  | Water point at Tumba Public RS/Nyirambuga pumping | 139 | 30604 | 1 | 30604 | 139 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 497.2662 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 21-03-2017 14:19:45 CET | Rwanda | Rulindo | Rukozo | Buraro | Kamiyove |  |  | Kabonanyoni | 70 | 7894 | 30 | 263.1333 | 65 | 5 | 92.86% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 5 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 5 | 2015 | 1 | 15 | 115200 | 354.4615 | 1 | 1 | 1 | 2015 | 1 | 720 | 1 | 19 | 2015 | 1 | 1 | 10 | Pressure Break Tank¦Distribution Chamber¦Null | 2015 | 1 | 1 | 3 | 2015 | 1 | 19000 | 1 | 2 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 31 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-04-2017 21:52:15 CEST | Rwanda | Rulindo | Kisaro | Kigarama | Runyinya |  |  | Gahama Kisaro network | 148 | 10234 | 14 | 731 | 148 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 |  | 1 | 2012 | 1 | 3 | 576000 | 778.3784 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 |  | 2012 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 03-01-2015 01:46:32 CET | Rwanda | Rulindo | Tumba | Barari | Rukore |  |  | Water point at Tumba Health Center/Nyirambuga pumping | 157 | 30604 | 1 | 30604 | 157 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 550.3185 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 08-03-2017 19:56:24 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Kigarama |  |  | kinywamagana pumping network | 233 | 6436 | 26 | 247.5385 | 120 | 113 | 51.5% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 288 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:55:14 CET | Rwanda | Rulindo | Mbogo | Bukoro | Kinini Ya Mbogo |  |  | Musenge Network | 100 | 6074 | 29 | 209.4483 | 100 |  | 100% | 1 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 778.3784 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber¦Washout And Air Release | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 04-06-2017 15:52:52 CEST | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 135 | 6074 | 29 | 209.4483 | 25 | 110 | 18.52% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Water For People, Wasac And Rulindo District. | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 3113.5135 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Washout, Air Release Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 12:00:26 CET | Rwanda | Rulindo | Mbogo | Mushali | Buraro |  |  | Matyazo network | 155 | 0 | 4 | 0 | 47 | 108 | 30.32% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2016 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 4 | 2016 | 1 | 17 | 101647.0588 | 432.5407 | 1 | 1 | 1 | 2016 | 1 | 4300 | 1 | 1 | 2016 | 1 | 1 | 2 | Air Release Chamber, Washout Chamber | 2016 | 1 | 1 | 1 | 2016 | 1 | 1800 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-04-2017 22:11:59 CEST | Rwanda | Rulindo | Bushoki | Giko | Cyili |  |  | Water point at GS Mugenda/ Nyirambuga pumping system | 165 | 30604 | 1 | 30604 | 165 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 4 | 432000 | 523.6364 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 10-03-2017 10:19:28 CET | Rwanda | Rulindo | Ngoma | Kabuga | Nyabuko |  |  | Kabarore-Ngoma-Nyabuko network | 122 | 8284 | 14 | 591.7143 | 32 | 90 | 26.23% | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 4 | 1 | 1 | "Springbox" --Intake Structure At A Spring¦Collection Chamber | 5 | 2014 | 2 | 4 | 432000 | 2700 | 1 | 1 | 2 | 2014 | 1 | 8000 | 1 | 13 | 2014 | 1 | 0 |  |  |  |  | 1 | 2 | 2014 | 1 | 7000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 17 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 04-06-2017 15:53:01 CEST | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 135 | 6074 | 29 | 209.4483 | 28 | 107 | 20.74% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Water For People, Wasac And Rulindo District | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 2779.9228 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Washout, Air Release Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-03-2017 11:18:54 CET | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 203 | 5544 | 14 | 396 | 203 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 1998 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 20 | 86400 | 85.1232 | 1 | 1 | 2 | 2016 | 1 | 5000 | 1 | 15 | 2016 | 1 | 0 |  |  |  |  | 1 | 2 | 2016 | 1 | 5000 | 1 | 1 | 2016 | 1 | 1 | 2016 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 18-04-2017 06:59:40 CEST | Rwanda | Rulindo | Tumba | Gahabwa | Munyinya |  |  | Munyinya water point chez Rugigana/Nyirambuga pumping system | 142 | 30604 | 1 | 30604 | 142 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 0 |  |  |  |  | 5 | 345600 | 486.7606 | 1 | 1 | 1 | 2017 | 1 | 500 | 1 | 1 | 2017 | 1 | 0 |  |  |  |  | 1 | 1 | 2017 | 1 | 500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2017 | 3 | No | 0 | 0 | 1 | 0 | 0 | 3
2017 | 15-03-2017 16:39:16 CET | Rwanda | Rulindo | Burega | Butangampundu | Kigarama |  |  | Rwamugaza | 380 | 14106 | 38 | 371.2105 |  | 380 |  | 0 | 0 | 1 | Piped Network With Pump | 2009 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 |  | 0 | 1 | 2 | 2009 | 1 | 3000 | 1 | 3 | 2014 | 3 | 1 | 8 |  | 2014 | 3 | 1 | 2 | 2014 | 3 | 3000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 3 | Yes | 365 | 0 | 0 | 0 | 0 | 3
2017 | 22-03-2017 19:28:32 CET | Rwanda | Rulindo | Kinihira | Butunzi | Ndorandi |  |  | Nyamagana-Kinihira | 139 | 0 | 15 | 0 | 50 | 89 | 35.97% | 0 | 1 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1382.4 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 15:55:42 CET | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kamatongo |  |  | 0 | 1125 | 6572 | 15 | 438.1333 |  | 1125 |  | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 |  | 0 | 1 | 2 | 2009 | 1 | 3000 | 1 | 3 | 2014 | 3 | 1 | 8 |  | 2014 | 3 | 1 | 2 | 2014 | 3 | 3000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 3 | Yes | 365 | 0 | 0 | 0 | 0 | 3
2017 | 17-03-2017 05:22:22 CET | Rwanda | Rulindo | Mbogo | Rurenge | Gakoma |  |  | Musenge network | 146 | 6074 | 29 | 209.4483 | 48 | 98 | 32.88% | 0 | 1 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 1621.6216 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Washout And Air Release Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 1 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 06:54:01 CET | Rwanda | Rulindo | Kinihira | Marembo | Kigali |  |  | Nyamagana- Kinihira | 189 | 0 | 4 | 0 | 60 | 129 | 31.75% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 5 | 345600 | 1152 | 1 | 1 | 1 | 2015 | 1 | 1000 | 1 | 7 | 2015 | 1 | 1 | 8 | Distribution Chamber¦Ventouse, Washout | 2015 | 1 | 1 | 3 | 2015 | 1 | 6000 | 1 | 2 | 2015 | 1 | 1 | 2015 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 13-03-2017 21:52:37 CET | Rwanda | Rulindo | Bushoki | Giko | Ngarama |  |  | Ngarama water point/Nkore gravity system | 110 | 0 | 1 | 0 | 110 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Private Group Of People That Have Joined Hands To Get Clean Water | Spring | 1 | 1 | 0 |  |  |  |  | 40 | 43200 | 78.5455 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 16:28:30 CET | Rwanda | Rulindo | Burega | Butangampundu | Runyinya |  |  | Rwamugaza | 390 | 14106 | 38 | 371.2105 |  | 390 |  | 0 | 0 | 1 | Piped Network With Pump | 2014 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 |  | 0 | 1 | 2 | 2009 | 1 | 3000 | 1 | 3 | 2014 | 3 | 1 | 8 |  | 2014 | 3 | 1 | 2 | 2014 | 3 | 3000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 3 | Yes | 365 | 0 | 0 | 0 | 0 | 3
2017 | 03-01-2015 00:10:48 CET | Rwanda | Rulindo | Tumba | Taba | Mwili |  |  | Mwili water point/Nyirambuga pumping | 141 | 30604 | 1 | 30604 | 141 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 612.766 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 09-03-2017 04:57:18 CET | Rwanda | Rulindo | Shyorongi | Kijabagwe | Kabagabaga |  |  | kirikumuryango network | 181 | 0 | 26 | 0 | 106 | 75 | 58.56% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 296.3979 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 05:48:50 CET | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 229 | 1458 | 6 | 243 | 200 | 29 | 87.34% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Groundwater (Well, Etc.) | 2 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 75 | 23040 | 23.04 | 1 | 1 | 1 | 2016 | 2 | 4280 | 1 | 1 | 2012 | 1 | 1 | 1 | Pressure Break Tank | 2016 | 1 | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 0 | 2
2017 | 15-03-2017 14:37:39 CET | Rwanda | Rulindo | Cyinzuzi | Migendezo | Remera |  |  | 0 | 975 | 14106 | 15 | 940.4 | 975 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2009 | Umushinga Witwa Ema | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 78.7692 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 16 | 2009 | 1 | 1 | 23 |  | 2009 | 1 | 1 | 2 | 2009 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2009 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 04-06-2017 13:34:36 CEST | Rwanda | Rulindo | Kisaro | Mubuga | Nyakarekare |  |  | gahama | 150 | 10234 | 11 | 930.3636 | 100 | 50 | 66.67% | 0 | 0 | 1 | Piped Network With Pump | 2012 | Waterforpeople | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2012 | 1 | 65 | 26584.6154 | 53.1692 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 | Pressure Break Tank¦Distribution Chamber¦Washout,Air Release | 2012 | 1 | 1 | 2 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-06-2017 06:41:45 CEST | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza | 229 | 14106 | 38 | 371.2105 | 229 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2003 | 1 | 3 | 576000 | 503.0568 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 | Pressure Break Tank | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 3 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 05-04-2017 21:43:50 CEST | Rwanda | Rulindo | Bushoki | N.Ngarama | Byimana |  |  | Nyabishengeshi gravity system | 92 | 893 | 2 | 446.5 | 92 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 0 |  |  |  |  | 50 | 34560 | 75.1304 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 14-03-2017 22:51:31 CET | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Water point1 at Kingazi/Nyakabizi2 gravity | 157 | 1259 | 1 | 1259 | 157 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Gor | Spring | 2 | 1 | 0 |  |  |  |  | 20 | 86400 | 110.0637 | 1 | 0 |  |  |  |  | 1 | 1 | 2013 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-04-2017 23:27:56 CEST | Rwanda | Rulindo | Burega | Butangampundu | Mayaga |  |  | Rwamugaza network | 105 | 14106 | 35 | 403.0286 | 105 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 1097.1429 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 14 |  | 2003 | 1 | 1 | 1 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 12-03-2017 18:40:26 CET | Rwanda | Rulindo | Base | Gitare | Gatete |  |  | Rwicanyoni | 141 | 698 | 7 | 99.7143 | 135 | 6 | 95.74% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2017 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 2 | 2016 | 1 | 10 | 172800 | 256 | 1 | 1 | 1 | 2016 | 1 | 8600 | 1 | 3 | 2016 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2016 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 07:05:18 CET | Rwanda | Rulindo | Burega | Karengeli | Kiziba |  |  | Rwamugaza | 400 | 14106 | 38 | 371.2105 | 400 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 192 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 28-03-2017 08:27:30 CEST | Rwanda | Rulindo | Ntarabana | Mahaza | Kayenzi |  |  | Rwamugaza network | 200 | 14106 | 35 | 403.0286 | 200 |  | 100% | 1 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Government | Spring | 2 | 1 | 1 |  | 1 | 2003 | 1 | 3 | 576000 | 576 | 1 | 1 | 2 | 2003 | 1 | 35000 | 1 | 7 | 2003 | 1 | 1 | 12 |  | 2003 | 1 | 1 | 2 | 2003 | 1 | 35000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2003 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 25-03-2017 20:47:34 CET | Rwanda | Rulindo | Buyoga | Butare | Gasave |  |  | KIDUHA | 114 | 0 | 7 | 0 | 100 | 14 | 87.72% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2007 | Italians (Lake Angels) Expanded By Water For People | Groundwater (Well, Etc.) | 1 | 0 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 2 | 20 | 86400 | 172.8 | 1 | 1 | 1 | 2007 | 2 | 2200 | 1 | 3 | 2007 | 2 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 23-03-2017 17:26:27 CET | Rwanda | Rulindo | Buyoga | Ndarage | Gahondo |  |  | Ndarage | 105 | 0 | 9 | 0 | 100 | 5 | 95.24% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2014 | Governement (District, Wasac) And Water For People | Spring | 2 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 30 | 57600 | 115.2 | 1 | 1 | 1 | 2014 | 1 | 6700 | 1 | 5 | 2014 | 1 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2014 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 08:52:24 CET | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  | Musenge Network | 186 | 6074 | 29 | 209.4483 | 22 | 164 | 11.83% | 0 | 1 | 1 | Piped Network With Pump | 2014 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2014 | 1 | 4.44 | 389189.1892 | 3538.0835 | 1 | 1 | 1 | 2014 | 1 | 3000 | 1 | 16 | 2014 | 1 | 1 | 8 | Distribution Chamber | 2014 | 2 | 1 | 3 | 2014 | 2 | 20000 | 1 | 2 | 2014 | 2 | 1 | 2014 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 28 | 2014 | 3 | Yes | 8 | 30 | 0 | 240 | 0 | 3
2017 | 07-03-2017 12:43:55 CET | Rwanda | Rulindo | Cyungo | Marembo | Murambo |  |  | Mugomero Murambo | 161 | 3456 | 3 | 1152 | 150 | 11 | 93.17% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2015 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2015 | 1 | 120 | 14400 | 19.2 | 0 | 1 | 2 | 2015 | 1 | 10000 | 1 | 10 | 2015 | 1 | 1 | 3 | Distribution Chamber | 2015 | 1 | 1 | 2 | 2015 | 1 | 10000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 07-03-2017 16:07:56 CET | Rwanda | Rulindo | Mbogo | Mushali | Buraro |  |  | Kishwi network | 155 | 1309 | 4 | 327.25 | 53 | 102 | 34.19% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2003 | Goverment | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2016 | 1 | 25 | 69120 | 260.8302 | 1 | 1 | 2 | 2016 | 1 | 700 | 1 | 2 | 2003 | 1 | 0 |  |  |  |  | 1 | 2 | 2003 | 1 | 680 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 4 | 2003 | 2 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 12:38:00 CET | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water at Buyoga Market/Nyirambuga pumping | 177 | 30604 | 1 | 30604 | 177 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 |  | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 488.1356 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 24-04-2017 21:52:48 CEST | Rwanda | Rulindo | Kisaro | Murama | Akamanama |  |  | Gahama Kisaro network | 141 | 10234 | 14 | 731 | 141 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 |  | 1 | 2012 | 1 | 3 | 576000 | 817.0213 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 7 | 2012 | 1 | 1 | 14 |  | 2012 | 1 | 1 | 1 | 2012 | 1 | 30000 | 1 | 2 | 2012 | 1 | 1 | 2012 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 21-03-2017 13:39:51 CET | Rwanda | Rulindo | Kinihira | Karegamazi | Buhita |  |  | Miyove-Kinihira | 131 | 10452 | 19 | 550.1053 | 60 | 71 | 45.8% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2001 | Gkww | Spring | 6 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 1989 | 2 | 5 | 345600 | 1152 | 1 | 1 | 1 | 1985 | 2 | 8000 | 1 | 4 | 1985 | 1 | 1 | 18 | Distribution Chamber¦Ventouse, Washout | 2015 | 2 | 1 | 2 | 1989 | 2 | 15000 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 16-04-2017 00:29:17 CEST | Rwanda | Rulindo | Bushoki | Gasiza | Buhande |  |  | Water point at Pensez-y/Gasebeya gravity system | 129 | 0 | 1 | 0 | 1 | 128 | 0.7752% | 0 | 1 | 1 | Piped Network -- Gravity Only | 2004 | Pensez-Y Bar Restaurant | Spring | 1 | 1 | 0 |  |  |  |  | 60 | 28800 | 5760 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2004 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 15-03-2017 17:04:16 CET | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Water point nearby Giko cell/Nyirambuga pumping | 134 | 30604 | 1 | 30604 | 134 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Gor | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 644.7761 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 02-01-2015 13:23:55 CET | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point nearby Gisha/Nyirambuga pumping | 133 | 30604 | 1 | 30604 | 133 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2015 | Governement (District, Wasac) And Water For People | Spring | 11 | 1 | 0 |  |  |  |  | 4 | 432000 | 649.6241 | 1 | 0 |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 2015 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 16-03-2017 06:08:35 CET | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 495 | 14106 | 38 | 371.2105 | 495 |  | 100% | 1 | 0 | 1 | Piped Network With Pump | 2012 | Governement (District, Wasac) And Water For People | Spring | 3 | 1 | 1 |  | 3 | 2009 | 1 | 4.5 | 384000 | 155.1515 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 16 | 2012 | 1 | 1 | 8 |  | 2012 | 1 | 1 | 2 | 2012 | 1 | 5000 | 1 | 1 | 2009 | 1 | 1 | 2009 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2012 | 1 | No | 0 | 0 | 1 | 0 | 0 | 1
2017 | 09-03-2017 04:45:50 CET | Rwanda | Rulindo | Shyorongi | Rutonde | Rutonde |  |  | kirikumuryango network | 160 | 0 | 26 | 0 | 160 |  | 100% | 1 | 1 | 1 | Piped Network -- Gravity Only | 2013 | Governement (District, Wasac) And Water For People | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2013 | 1 | 11 | 157090.9091 | 196.3636 | 1 | 1 | 1 | 2013 | 1 | 500 | 1 | 17 | 2013 | 1 | 1 | 6 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 2 | 2013 | 1 | 3500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 1
2017 | 25-03-2017 11:40:09 CET | Rwanda | Rulindo | Masoro | Shengampuri | Amataba |  |  | Mutagata Gravity network | 220 | 26296 | 12 | 2191.3333 | 54 | 166 | 24.55% | 0 | 0 | 1 | Piped Network -- Gravity Only | 2004 |  | Spring | 1 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 1 | 2004 | 2 | 8 | 216000 | 800 | 1 | 1 | 1 | 2004 | 2 | 3500 | 1 | 6 | 2004 | 2 | 1 | 4 | Distribution Chamber¦Washout And Air Release | 2004 | 2 | 1 | 2 | 2004 | 2 | 4500 | 0 | [6 empty] | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 12 | 2004 | 2 | No | 0 | 0 | 1 | 0 | 1 | 2
2017 | 08-03-2017 20:55:31 CET | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 165 | 6436 | 26 | 247.5385 | 35 | 130 | 21.21% | 0 | 1 | 1 | Piped Network With Pump | 2013 | Governement (District, Wasac) And Water For People | Spring | 7 | 1 | 1 | "Springbox" --Intake Structure At A Spring | 3 | 2013 | 1 | 10 | 172800 | 987.4286 | 1 | 1 | 1 | 2013 | 1 | 1500 | 1 | 20 | 2013 | 1 | 1 | 25 | Distribution Chamber¦Ventouse, Washout | 2013 | 1 | 1 | 4 | 2013 | 1 | 11000 | 1 | 2 | 2013 | 2 | 1 | 2013 | 1 | 0 | [6 empty] | 0 | 0 | Not Present | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2013 | 1 | No | 0 | 0 | 1 | 0 | 1 | 2

## Raw Data
Identifier | Repeat no. | Display Name | Device identifier | Instance | Submission Date | Submitter | Duration | 996770226¦Year | Geo_1 | Geo_2 | Geo_3 | Geo_4 | Geo_5 | Geo_6 | Geo_7 | 995840254¦Water Point/System Unique ID | Population using system | Users/System | 995840255¦Total Number of Families Living in the Community | 995830254¦Total Number Of Families In The Community With Access To An Improved Water Point/System | 999390233¦Total Number Of Families In The Community Without Access To An Improved Water Point/System | 995830255¦Is This An Improved Water Point/System? | 996780265¦What Type Of Water Point/System Is This? | 996780266¦What Type Of Unimproved Water Source Is This? | 991360249¦What Year Was The Water Point/System First Constructed? | 998450243¦Does This Water Point/System Serve More Than 1 Community? | 997720247¦List The Names Of The Other Communities It Serves | 993220252¦Who Funded The Construction Of This Water Point/System? | 998460242¦Comments Or Notes (Optional) | 990250711¦How Many Sources Does This System Have? | 997720248¦What Is The Source Of Water Point/System? | 996760258¦Latitude | --GEOLON--¦Longitude | --GEOELE--¦Elevation | --GEOCODE--¦Geo Code | 993970241¦Photo Of Source | 992050246¦Is The Source Protected? | 995820230¦How Many Seconds Does It Take To Fill A 20 Liter Container? | 997730247¦Does The Water Point/System Have An Intake Structure? | 990330242¦How Many Intake Structures Does This Water Point/System Have? | 997730249¦Photo Of Intake Structure | 995840259¦What Is The Type Of Intake Structure(s)? | 997720253¦Year Intake Structure Was Constructed or Last Rehabilitated | 994820245¦Physical State Of The Intake Structure | 995840261¦How Many Seconds Does It Take To Fill A 20 Liter Container? | 990330246¦Does The Water Point/System Include A Conduction Line (Include Accessories)? | 995830264¦How Many Conduction Lines Does The Water Point/System Have? | 994830255¦Photo Of Conduction Line | 997730253¦Year Conduction Line Was Constructed or Last Rehabilitated (Including Accessories) | 998460249¦Physical State Of Conduction Line (Including Accessories) | 997540310¦Approximately How Many Meters Long Is the Conduction Line(s) | 994830259¦Does This Water Point/System Include A Storage Tank? | 996770239¦How Many Storage Tanks Does This Water Point/System Have? | 998450248¦Latitude | --GEOLON--¦Longitude | --GEOELE--¦Elevation | --GEOCODE--¦Geo Code | 999390244¦Photo Of Storage Tank | 991360262¦Year Storage Tank Was Constructed or Last Rehabilitated | 998450250¦Physical State Of Storage Tank | 991370236¦Does The Water Point/System Have Any Other Concrete Structures (Sedimentation Tank, Pressure Break Tank, Distribution Chamber etc.)? | 997540312¦How Many Other Concrete Structures Does The Water Point/System Have? | 991350246¦What Type Are The Concrete Structures? | 997540313¦Photo Of Other Concrete Structure | 995840272¦Year Other Concrete Structures Were Constructed Or Last Reconstructed | 995710727¦Physical State Of The Other Concrete Structures | 999380264¦Does The Water Point/System Have A Distribution Network (Include Accessories)? | 995840277¦How Many Distributions Networks Does This Water Point/System Have? | 991370243¦Photo Of Distribution Network | 991360270¦Year Distribution Network Was Constructed Or Last Reconstructed | 995820239¦Physical State Of The Distribution Network (Including Accessories) | 997710255¦Approximately How Many Meters Long Is The Distribution Network(s)? | 995710730¦Does The Water Point/System Have A Pump (Include Pump Related Electrical Equipment? | 994820262¦How Many Pumps Does This Water Point/System Have? | 997540319¦Photo Of Pump | 996780294¦Year The Pump Was Installed Or Last Replaced? | 997720273¦Physical State Of The Pump (Including Pump Related Electrical Equipment) | 990330262¦Does The Water Point/System Have A Pump House/Station? | 990250732¦Photo Of Pump House/Station | 991350253¦Year Pump House/Station Was Constructed Or Last Reconstructed | 991370249¦Physical State Of Pump House/Station | 998450257¦Does The Water Point/System Have Treatment Equipment? | 998460267¦Photo Of Treatment Equipment | 993970263¦Type Of Water Treatment | 996760288¦Year Treatment Equipment Was Constructed Or Last Reconstructed | 997540328¦Physical State Of Water Treatment Equipment | 994830272¦Does The Treatment Equipment Have A Housing Structure? | 995850266¦Photo Of Treatment Housing | 991370256¦Year Treatment Housing Structure Was Constructed Or Last Rehabilitated | 990330272¦Physical State Of Treatment Housing | 992060291¦Was Water Quality Testing Done Today Or In The Last 12 Months? | 998450263¦Was E. coli Tested For? | 990250742¦What Was The Result for E. coli (CFU/100ml)? | 992060295¦Was Residual Chlorine Tested For? | 999390260¦What Was the Result for Residual Chlorine (mg/L)? | 994830279¦Was Bacterial Contamination Tested For? | 997720285¦What Was The Result for Bacterial Contamination? | 990330279¦Was Turbidity Tested For? | 997540334¦What Was The Result for Turbidity (NTU)? | 995810271¦Is There A Kiosk Or Public Tap Stand? | 997540340¦Latitude | --GEOLON--¦Longitude | --GEOELE--¦Elevation | --GEOCODE--¦Geo Code | 993220279¦How Many Kiosks or Tap Stands Are There? | 999390265¦Photo Of Kiosk Or Public Tap Stand | 995850275¦Year Kiosk or Public Tap Stand Was Constructed Or Last Rehabilitated | 992070282¦Physical State Of Kiosk Or Public Tap Stand | 997720294¦In The Last Year Was The Water Point Or System Ever Broken Or Out Of Service For More Than One Day? | 992050285¦How Many Times Was It Broken Or Out Of Service In The Last Year? | 995710751¦On Average, Each Time It Was Out Of Service, How Many Days Was It Out For? | 992070283¦Why Was The Water Point/System Broken Or Out Of Service? | 998450275¦Is Water Available From The Water Point/System Today? | 995820257¦Why Isn't Water Available? | 992070285¦Overall State Of The Water Point/System (Consider Shortfalls, Physical, Design, Etc.) | 995840302¦Comments Or Notes (Optional)
jf8y-wfvh-hdg6 | 1 |  | J7 Rw24 | 1246240100 | 27-03-2017 08:35:32 CEST | Kabalisa Manzi Christella | 00:08:36 | 2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Gakenke |  |  | Gahama Kisaro network | 10234 |  | 865 | 865 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6671501074688961 | 30.041830412153367 | 1945.4 | 24l5zh36 |  | Yes | 3 | Yes | 1 |  |  | 2012 | Poor | 3 | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 |  |  | 2012 | Normal | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Poor | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6224809494425454 | 30.044099033437085 | 2076.7 | 22jag5ug | 1 | https://waterforpeople.s3.amazonaws.com/images/c456cd51-d953-455a-a281-a90a38b825f5.jpg | 2012 | Normal | No |  |  |  | No | System closed | Poor |  | 71b0f46a4641f3d986c5a5ca3079e1d3
pm6u-7j7k-jhbg | 1 |  | J7 Rw23 | 1212340746 | 15-03-2017 06:11:16 CET | Rugirangoga Augustin | 00:17:59 | 2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Gihanga II |  |  | 151 | 151 | 0 | Yes | Piped Network -- Gravity Only |  | 2017 | Yes | gatiba gatwa | Governement (District, WASAC) and Water For People |  | 1 | Groundwater (well, etc.) | -1.6358367374763643 | 29.91135277934778 | 1996.9 | 235d9tex |  | Yes | 15 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 15 | Yes | 1 |  | 2016 | Normal | 7000 | Yes | 3 | -1.6498521069502532 | 29.917613599705728 | 1996.9 | 23sjzjl4 |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.650315674844109 | 29.92708884931781 | 1700 | 23tbdhhi | 2 | https://waterforpeople.s3.amazonaws.com/images/a15230a8-38a7-4263-a7f5-6ff1864d35fb.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 9bc3e4b7024e026055f1c55b27415b
qtn5-dp58-y79n | 1 |  | J7 Rw26 | 1196560784 | 02-01-2015 05:48:51 CET | Byukusenge Elie | 00:20:34 | 2017 | Rwanda | Rulindo | Cyungo | Rwili | Karambi |  |  | Nyamagana | 20456 |  | 60 | 10 | 50 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6086270818225763 | 29.931225291293163 | 1901.8 | 21wd9cj4 | 29 | https://waterforpeople.s3.amazonaws.com/images/b6c61ae2-4c82-4daf-be73-37e9dbe917a1.jpg | 2011 | Normal | Yes | 7 | 35 | Poor tee junctions connection and not well located of main distribution reservoir | No | The distribution reservoir does not supply water in this transmission line because of bad connection of tee junctions towards Gatovu | Poor | This water tap doesn't have water caused by the problem in the types of pipeline . | 13a8de6ad976fd434ab6ebe882d95619
1s5t-9rvf-qh0w | 1 |  | J7 Rw24 | 1250740269 | 28-03-2017 09:37:35 CEST | Kabalisa Manzi Christella | 00:09:51 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyagasozi |  |  | Kararama network | 6572 |  | 197 | 197 | 0 | Yes | Piped Network with Pump |  | 2009 | No |  | Governement (District, WASAC) and Water For People |  | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 5 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 14 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7575773007512252 | 30.06109219679338 | 1851 | 28qpcx36 | 1 | https://waterforpeople.s3.amazonaws.com/images/061978a5-624d-41a2-9979-362c5e32e647.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal |  | 88e02382243e7ebd7b8c5806515f682
fydc-3agr-6cy3 | 1 |  | J7 Rw10 | 1277940061 | 05-04-2017 21:15:59 CEST | Tuyisenge Vianney | 00:05:12 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Ngarama |  |  | Rutare-Nyirangarama gravity/Nyirangarama water point | 726 |  | 89 | 89 | 0 | Yes | Piped Network -- Gravity Only |  | 1960 | No |  | Government of Rwanda | Rutare-Nyirangarama gravity/Nyirangarama water point does nolonger deliver water to people due to the tap that got removed and not replaced | 1 | Spring | -1.6705676828047722 | 29.878696276428556 | 2067 | 24qt0942 |  | Yes | 20 | No | [5 empty] | 20 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6656042031479839 | 29.88633237658635 | 1798.5 | 24ilp94f | 1 | https://waterforpeople.s3.amazonaws.com/images/e55a71c3-a750-4559-bcfe-4d648a78ba4a.jpg | 1960 | Poor | No |  |  |  | Yes |  | Poor | Rutare-Nyirangarama gravity/Nyirangarama water point does nolonger deliver water to people due to the tap that got removed and not replaced | a5cc4378be9541c3b98a1d453c74957
52bk-p09e-c0da | 1 |  | J7 Rw15 | 1201310337 | 09-03-2017 20:28:53 CET | Mukakarangwa Assoumpta | 00:07:06 | 2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Gaseke |  |  | Gisoro- Nyundo network | 2297 |  | 176 | 65 | 111 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.840451151026817 | 29.948165560771624 | 1795.9 | 2cjrthy1 |  | Yes | 13 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 13 | Yes | 1 |  | 2013 | Normal | 30 | Yes | 6 | 1.8406374522240199 | 29.94836287627501 | 1783.7 | 2ck2jau3 |  | 2013 | Poor | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 7000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8768554216984343 | 29.948671253209664 | 1472.5 | 2e7yzbxa | 1 | https://waterforpeople.s3.amazonaws.com/images/83f1273d-201d-4ec4-bbc4-af9e7e800298.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 98fdfffbaf44d31da5c299bbaa98
kv9t-6du3-b2rs | 1 |  | J7 Rw24 | 1246240102 | 27-03-2017 15:41:31 CEST | Kabalisa Manzi Christella | 00:12:48 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Kararama and Rwamugaza pumping | 6572 |  | 965 | 965 | 0 | Yes | Piped Network -- Gravity Only¦Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Here is at a school people use two systems but mostly Rwamugaza system | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3.5 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2003 | Normal | 3.5 | Yes | 1 |  | 2003 | Normal | 8000 | Yes | 7 | -1.7374173333138418 | 30.06563288387298 | 1723.9 | 27td31kg |  | 2003 | Normal | Yes | 14 |  |  | 2003 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7598500570325084 | 30.065784156813418 | 1809.2 | 28uh3r1t | 1 | https://waterforpeople.s3.amazonaws.com/images/492b8a07-8a84-48ba-8aa7-131fd35e7103.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal |  | 31ed3b8edd13288c63fcc1fbf3c02a90
w54r-rk8k-fga5 | 1 |  | J7 Rw15 | 1243470294 | 21-03-2017 18:25:38 CET | Mukakarangwa Assoumpta | 00:08:07 | 2017 | Rwanda | Rulindo | Kinihira | Butunzi | Gisekuru |  |  | Miyove- Kinihira | 10452 |  | 143 | 80 | 63 | Yes | Piped Network -- Gravity Only |  | 2001 | Yes | Kamiyove | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.671721884645144 | 29.953733739672447 | 1910.9 | 24sq2jv5 | 1 | https://waterforpeople.s3.amazonaws.com/images/ebe6ae2f-bcd5-4395-bbc1-e0339ee3f22c.jpg | 1989 | Poor | No |  |  |  | Yes |  | Poor |  | be4881f57eda19ed2ad11277a39b0
v9ek-2kbn-9ax1 | 1 |  | J7 Rw8 | 1441760193 | 04-06-2017 15:38:02 CEST | Amani Desire | 00:10:19 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gihonga |  |  |  | 510 |  | 20 | 20 | 0 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | water for People |  | 2 | Spring | -1.7319103236390618 | 29.9285227727732 | 1850.6 | 27k9mlsl |  | Yes | 180 | Yes | 180 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 180 | Yes | 1 |  | 2016 | Normal | 900 | No | [8 empty] | No | [5 empty] | Yes | 1 |  | 2016 | Normal | 700 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7283045408667743 | 29.935055674252915 | 1759.9 | 27eap4gm | 2 | https://waterforpeople.s3.amazonaws.com/images/40065bd0-8d88-4e9a-b49f-ad1fcf6bc9fb.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | c39bbce5328dc6238a91e1dbc435
k870-q1nf-u9jc | 1 |  | J7 Rw7 | 1451550050 | 06-06-2017 21:36:49 CEST | Rugirangoga Augustin | 00:13:24 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Cyondo | [5 empty] | 173 | 150 | 23 | Yes | Piped Network with Pump |  | 2012 | No |  | waterforpeople | umuhanda waciye amatuyaux | 2 | Spring | -1.66099723036262 | 30.02129350219593 | 1753.6 | 24az8gac |  | Yes | 65 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 75 | No | [5 empty] | No | [8 empty] | Yes | 14 | Pressure Break Tank¦Distribution Chamber¦washout,air release |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 30000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 1 | Yes | 1 | Yes | Not Present | Yes | 0 | Yes | -1.6307369107925318 | 30.03297291739131 | 2207.3 | 22wxmru1 | 1 | https://waterforpeople.s3.amazonaws.com/images/e9c4eb9f-2463-4d5f-ac30-dce47bd6235d.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | umuyoboro ufite ikibazo cy'umuhanda wawusenye | 5b3fe690f728b4dab7873003cdb5934
j6qt-xy28-q0dg | 1 |  | J7 Rw8 | 1217540235 | 10-03-2017 10:49:23 CET | Amani Desire | 00:31:15 | 2017 | Rwanda | Rulindo | Ngoma | Kabuga | Kirambo |  |  | Nganzo-Kabarore |  |  | 131 | 40 | 91 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | nkanga,kagwa | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8123160408683467 | 29.96796382144226 | 1787.1 | 2b98fpsv | https://waterforpeople.s3.amazonaws.com/images/b0ff64ad-5362-4c97-b3c9-c797a3bf90ca.jpg | Yes | 20 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/49ee1b1d-25c8-4a30-92be-db9ac632758c.jpg | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 20 | Yes | 1 |  | 2014 | Poor | 400 | Yes | 3 | -1.8123911178819008 | 29.967599969457293 | 1761.4 | 2b9d76mz | https://waterforpeople.s3.amazonaws.com/images/c58843db-8d80-4eb6-bbd4-16b99cfe2a8c.jpg | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Does Not Function | 800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8122932864846988 | 29.967787534922856 | 1765.6 | 2b978ul9 | 4 | https://waterforpeople.s3.amazonaws.com/images/24495fc9-6a83-4e4d-aed8-41aab2b474c0.jpg | 2014 | Poor | No |  |  |  | Yes |  | Poor | -the water point at the source is damaged but it is functioning -The pipeline is damaged ; all distribution pipes are broken - There are no water at all water points served by gravity by Nganzo source | 39bacf30d569d16cb375643278ca
k02d-2qbu-wye9 | 1 |  | J7 Rw19 | 1203681054 | 07-03-2017 15:15:03 CET | Kayinamura Innocent | 00:48:03 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Ruhondo |  |  | Kishwi network | 1309 |  | 184 | 46 | 138 | Yes | Piped Network -- Gravity Only |  | 2003 | Yes | Buraro and Ruhondo | Goverment | One Part of the system was Rehabilitated By the Government (District, WASAC) and Water For People | 1 | Spring | -1.7722077069769515 | 29.962926865497884 | 1849 | 29ewe2ct | https://waterforpeople.s3.amazonaws.com/images/d41982e0-cc59-4990-8880-371b0e6210f8.jpg | Yes | 25 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/8a249a09-24eb-4ac6-9bdd-3f4d47c589ba.jpg | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 25 | Yes | 2 |  | 2016 | Normal | 700 | Yes | 2 | -1.7714946380440713 | 29.963728274178695 | 1845.6 | 29dq4aet | https://waterforpeople.s3.amazonaws.com/images/c5e1d0ce-9d53-4bd5-bc3d-51c5a452d410.jpg | 2003 | Normal | No | [5 empty] | Yes | 2 |  | 2003 | Normal | 680 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7729085951992256 | 29.965603322273203 | 1821.7 | 29g22eq0 | 4 | https://waterforpeople.s3.amazonaws.com/images/30149245-1028-4e64-98c8-529764da5db7.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | Water gets dirty in the rainy season and part of the system was rehabilitated in 2016 only one point is not well functioning | 50fbecea1e542371a4e8ab4d481d52
en1f-vynp-h1jn | 1 |  | J7 Rw10 | 1220090120 | 15-03-2017 19:32:37 CET | Tuyisenge Vianney | 00:05:05 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Murambi 2 wpt/Nyirambuga pumping | 30604 |  | 174 | 174 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | GoR | Murambi water point/Nyirambuga pumping operates well though tap valves are not fixed | 1 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.6866972283180823 | 29.927574511012644 | 2074.4 | 25hhcg97 | https://waterforpeople.s3.amazonaws.com/images/0cc9687f-e816-4c80-8734-df6a0d6dcf27.jpg | 2012 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6864371793414927 | 29.92777301165432 | 2056.7 | 25h1v6j1 | 1 | https://waterforpeople.s3.amazonaws.com/images/d447c5a2-fa62-4d05-a4d8-7a78a1151d31.jpg | 2012 | Poor | No |  |  |  | Yes |  | Normal | Murambi central catholic church water point/Nyirambuga pumping operates well though tap valves are not fixed | 8416c831d5c895d5e479d8dce5797e
kdvr-k3uw-r1f9 | 1 |  | J7 Rw26 | 1194190308 | 06-03-2017 10:23:00 CET | Byukusenge Elie | 00:25:41 | 2017 | Rwanda | Rulindo | Cyungo | Marembo | Murambo | [5 empty] | 586 | 541 | 45 | Yes | Piped Network -- Gravity Only |  | 2012 | Yes | Ruhango,Kanyinya | Governement (District, WASAC) and Water For People | This network needs partial rehabilitation | 5 | Spring | -1.9864383712449805 | 30.10282582537071 | 1513.5 | 2j973c10 |  | Yes | 2 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 2 | No | [5 empty] | Yes | 5 | -1.986437369714554 | 30.102816562148135 | 1514 | 2j973c10 |  | 2012 | Normal | No | [5 empty] | Yes | 1 |  | 2012 | Normal | 1234 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.9864331473684775 | 30.102833254788674 | 1506.5 | 2j973c10 | 10 |  | 2012 | Normal | No |  |  |  | Yes |  | Normal |  | 7df85a4282d359fd4d9046da99bca1b2
yxca-c0c0-ntnb | 1 |  | J7 Rw10 | 1313150327 | 20-04-2017 06:55:45 CEST | Tuyisenge Vianney | 00:10:21 | 2017 | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point at Refectory APEKI Tumba/Nyirambuga pumping | 30604 |  | 115 | 115 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | Yes | 1 | -1.7084116423935287 | 29.952243644651396 | 2213.6 | 26hehyde | https://waterforpeople.s3.amazonaws.com/images/7e08d56f-5769-4936-9722-95379daeed27.jpg | 2012 | Normal | No | [5 empty] | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/39d77973-b971-4e01-974a-8fa3a936d4b5.jpg | 2012 | Normal | 100 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7085865226893084 | 29.950910538228126 | 2202.4 | 26hombn9 | 6 | https://waterforpeople.s3.amazonaws.com/images/645993f2-758b-408e-8285-7be4a446a6f0.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Operational | 976c7167ebdd5f3545e5e81a866ca91
k16m-nau9-wmba | 1 |  | J7 Rw8 | 1241510548 | 23-03-2017 07:51:59 CET | Amani Desire | 00:13:59 | 2017 | Rwanda | Rulindo | Murambi | Gatwa | Akarambi |  |  | Mutagata Motorised Network | 26296 |  | 206 | 100 | 106 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 4 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8254644855301652 | 30.040324002347656 | 1704.6 | 2buzcqur | 64 | https://waterforpeople.s3.amazonaws.com/images/99261f0b-9b3a-418e-876f-21bbee1b0283.jpg | 2016 | Normal | Yes | 3 | 30 | water closed by management | No | the network management opted to close this water point | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | d44b7ee55fd331f66a98a2d5e60b376
rh0j-9wb9-d91g | 1 |  | J7 Rw19 | 1239200050 | 23-03-2017 18:57:48 CET | Kayinamura Innocent | 00:15:50 | 2017 | Rwanda | Rulindo | Masoro | Kabuga | Rubaya |  |  | Mutagata motorised network | 26296 |  | 167 | 167 | 0 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout And Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 1900 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7939824979986811 | 30.059417592188236 | 1673.8 | 2aex46nm | 64 | https://waterforpeople.s3.amazonaws.com/images/6206a981-ff47-4825-9f33-f581fcdd6c55.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 76fbd4de20c5b412131d7a2ed164882a
grx7-mqn7-3ban | 1 |  | J7 Rw19 | 1219360340 | 17-03-2017 05:26:28 CET | Kayinamura Innocent | 01:14:35 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gitaba |  |  | Musenge network | 6074 |  | 195 | 95 | 100 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma, Karehe, Rutonde, Gitaba, Kiruri, Buhira, Ruhanya, Kibamba and karindi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Washout and Air release |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7884692900894037 | 29.948019813859613 | 1958.7 | 2a5sgvvc | 28 | https://waterforpeople.s3.amazonaws.com/images/7293056a-4d5f-406c-81be-681789bc844d.jpg | 2016 | Poor | No |  |  |  | Yes |  | Normal | 1. The system has two Pumps but one is damaged and is not working, only one pump is used to pump water 2. Eleven (11) water points served by the distribution reservoir R 50m3 located at Kibamba village do not have water today because water don't reach this reservoir, there is not water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 6. the interconnection to Ngoma network is under construction with one water points and resevoir being under construcyion | 84a8e9601554d5bb571e64aeb1d824a0
ph2u-y4yg-9x0b | 1 |  | J7 Rw19 | 1215120139 | 09-03-2017 18:11:30 CET | Kayinamura Innocent | 00:13:28 | 2017 | Rwanda | Rulindo | Ngoma | Karambo | Jyambere |  |  | Gahama network |  |  | 117 | 65 | 52 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | Jyambere | Governement (District, WASAC) and Water For People | two water point had been damaged | 1 | Spring | -1.824762618736981 | 29.979015616308 | 1718 | 2bttoe1a |  | No | 15 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 15 | Yes | 1 |  | 2014 | Normal | 1800 | Yes | 2 | -1.8248055237148662 | 29.983823341228508 | 1657.7 | 2btw24hq |  | 2014 | Normal | Yes | 1 | Distribution Chamber |  | 2014 | Normal | Yes | 1 |  | 2014 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8306308125755528 | 29.986590542680425 | 1607.9 | 2c3j5u6x | 5 | https://waterforpeople.s3.amazonaws.com/images/6a56421d-e923-4c1a-97bb-b7cb31d71037.jpg | 2014 | Normal | No |  |  |  | Yes |  | Poor | Two water points have broken parts and source stayed | 92f1e0e8bc9bd93fc34fd37ae861f1a5
snf8-n6jd-15as | 1 |  | J7 Rw19 | 1226650142 | 17-03-2017 05:21:09 CET | Kayinamura Innocent | 00:21:31 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 6074 |  | 135 | 68 | 67 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma, Karehe, Rutonde, Gitaba, Kiruri, Buhera, Ruhanya, Kibamba and Karindi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Washout and Air release chamber |  | 2014 | Normal | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7775428786739629 | 29.951365039825014 | 2133.8 | 29nqbjax | 28 | https://waterforpeople.s3.amazonaws.com/images/bed37cea-174b-4c18-b7bf-6ad308bba326.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | 1. the system has two Pumps but one is damaged and is not working only one pump is used to pump water 2. Eleven (11) water points served by the distribution reservoir R 50m3 located at Kibamba village do not have water today because water don't reach this reservoir, there is not water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5. one water point doesn't Function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | e1cdf7f1df19627c462dd02f195c4074
h0nr-uf1n-nq1h | 1 |  | J7 Rw10 | 1308460113 | 18-04-2017 20:12:24 CEST | Tuyisenge Vianney | 00:06:50 | 2017 | Rwanda | Rulindo | Tumba | Taba | Kamuragi |  |  | Water point chez Safari/Nyirambuga pumping system | 30604 |  | 154 | 154 | 0 | Yes | Piped Network with Pump |  | 2012 | Yes | Kamuragi,Ruvumba and Nyirambuga | Governement (District, WASAC) and Water For People | The water point is operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.735350271251818 | 29.95102593729578 | 2004 | 27pyfq2e | 2 | https://waterforpeople.s3.amazonaws.com/images/21d75454-862a-4d58-aa8f-1557e7ba1287.jpg | 2012 | Normal | No |  |  |  | Yes |  | Poor | The water point is operational | 9abd62f2653f79ce8cdcd4a69e776f
9dqp-pdst-3par | 1 |  | J7 Rw15 | 1201020526 | 12-03-2017 10:59:20 CET | Mukakarangwa Assoumpta | 00:07:30 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Karama |  |  | Bitete-Muvumu | 1316 |  | 121 | 35 | 86 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 3 | Spring | 1.8337482672601935 | 29.943433443706404 | 1749 | 2c8obmzu |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Poor | 1000 | Yes | 4 | 1.8368127107947887 | 29.93457412501046 | 1635 | 2cdr3pn5 |  | 2013 | Normal | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Poor | Yes | 1 |  | 2013 | Normal | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8510133025167776 | 29.923607149192982 | 1539.7 | 2d18j8kk | 1 | https://waterforpeople.s3.amazonaws.com/images/e551096e-0623-40f2-9ec0-ebb5dfe5a55f.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 154c1e10a1a0e8358e6a515efdaa3ad
7103-k7ad-qeka | 1 |  | J7 Rw23 | 1327430084 | 23-04-2017 14:40:46 CEST | Rugirangoga Augustin | 00:16:47 | 2017 | Rwanda | Gicumbi | Mutete | Nyarubuye | Rugarama |  |  | rukondo |  |  | 162 | 140 | 22 | Yes | Piped Network -- Gravity Only |  | 2012 | No |  | G. thierry | rukondo. uyu muyoboro uturuka mu karere ka Gicumbi | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 30 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 30 | Yes | 1 |  | 2012 | Normal | 4500 | Yes | 4 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2012 | Normal | No | [5 empty] | Yes | 1 |  | 2012 | Normal | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.716078778206044 | 30.08050337428137 | 1530.5 | 26u2k0qt | 2 | https://waterforpeople.s3.amazonaws.com/images/c03e1e6f-7581-4b33-92df-d3c66662e23c.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | System originates in Gicumbi and was funded by G.thierry. | 87e66ae8cb1e155768daef66903041
djga-rs33-qh15 | 1 |  | J7 Rw15 | 1205071011 | 09-03-2017 16:59:14 CET | Mukakarangwa Assoumpta | 00:13:58 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Rweya |  |  | kirikumuryango network |  |  | 212 | 110 | 102 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.903078547250875 | 29.967586612588885 | 1356.3 | 2ffc1w7v | 1 | https://waterforpeople.s3.amazonaws.com/images/0b76f7ce-667d-49a1-ac36-ceba0f65ddba.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | ea516ba6925cd70f45993b6089a580
dvrt-9rqf-nnjf | 1 |  | J7 Rw7 | 1235621063 | 24-03-2017 12:07:50 CET | Safari Bosco | 00:12:29 | 2017 | Rwanda | Rulindo | Masoro | Shengampuri | Mutagata |  |  |  | 6740 |  | 124 | 124 | 0 | Yes | Piped Network with Pump |  | 1998 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 15 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8119613986408982 | 30.05796600961691 | 1799.8 | 2b8nlkbn | 2 | https://waterforpeople.s3.amazonaws.com/images/8db93d9b-1f34-4f1f-a9cf-441f828fcf73.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | System is okay but there is a problem in the dry season | 6485a61cd66bddc0e4b9bb8f85eb973
13q2-p5hy-gjxe | 1 |  | J7 Rw23 | 1236600605 | 23-03-2017 17:26:20 CET | Rugirangoga Augustin | 00:19:22 | 2017 | Rwanda | Rulindo | Buyoga | Gahororo | Bunyana |  |  | Ndarage |  |  | 108 | 100 | 8 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | karambi gahondo Bunyana Rugarama Gasave | Governement (District, WASAC) and Water For People |  | 2 | Spring¦Groundwater (well, etc.) | -1.6829614865475908 | 30.031434012077444 | 1962 | 25bb9sey |  | Yes | 30 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 30 | Yes | 1 |  | 2014 | Normal | 6700 | Yes | 5 | -1.6902852583901373 | 30.03414816539013 | 1811.8 | 25nf3391 |  | 2014 | Normal | No | [5 empty] | Yes | 1 |  | 2014 | Normal | 6700 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7092239730775034 | 30.05176631057654 | 1571.9 | 26iqq351 | 2 | https://waterforpeople.s3.amazonaws.com/images/75a8aa50-3bf2-44ba-993e-94616ab27742.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | there is no problem with this network | 3736df144e7374f6aa33e35df6fc986
u3qy-puey-96xp | 1 |  | J7 Rw10 | 1226780407 | 16-03-2017 17:37:34 CET | Tuyisenge Vianney | 00:12:34 | 2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Rebero |  |  | Water point at Rebero/Matonyanga gravity |  |  | 175 | 175 | 0 | Yes | Piped Network -- Gravity Only |  | 2017 | No |  | Governement (District, WASAC) and Water For People | As Matonyanga gravity has been recently captured and this Rebero water point is part of it;the water point hasn't yet started benefiting people with water services | 1 | Spring | -1.69919116767908 | 29.937233740854015 | 1848.2 | 2625kai4 |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7130690562629904 | 29.92948072399655 | 1777.2 | 26p3cihq | 1 | https://waterforpeople.s3.amazonaws.com/images/cd3a9f2a-d3b7-44bd-95b8-af825efab7e3.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | Water point has water though it hasn't yet delivered water services to the people. | 74f77ca0e231c0d532afd6f6080f8cf
qvs4-e6a4-xe3h | 1 |  | J7 Rw24 | 1224820178 | 16-03-2017 06:34:10 CET | Kabalisa Manzi Christella | 00:06:28 | 2017 | Rwanda | Rulindo | Burega | Taba | Nyagisozi |  |  | Rwamugaza | 14106 |  | 520 | 520 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | no problem | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.0028444827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7411346073289555 | 30.007967136299975 | 2037.6 | 27zika5r | 1 | https://waterforpeople.s3.amazonaws.com/images/d7a7b4ee-5324-41c3-9fc9-eaf468b8ddae.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | no problem | fa37e0b6de4a293aa365dc0f9db8cbf
s8jk-qn2j-4532 | 1 |  | J7 Rw24 | 1222090784 | 16-03-2017 09:06:09 CET | Kabalisa Manzi Christella | 00:07:04 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kanyoni |  |  | charity water 203.032 | 6572 |  | 640 | 640 | 0 | Yes | Piped Network with Pump |  | 2016 | Yes | Gatagara, Kanyoni | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8024532750946713 | 30.042616473975034 | 1748.3 | 2asxebwq |  | Yes | 3 | Yes | 1 |  |  | 2016 | Normal | 3 | Yes | 1 |  | 2016 | Normal | 2000 | Yes | 2 | -1.7575350016834248 | 30.02449548695202 | 1874.2 | 28qmz6dw |  | 2016 | Normal | Yes | 2 |  |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 500 | Yes | 3 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7782173643226062 | 30.03082150935542 | 1965.5 | 29ou7lg4 | 1 | https://waterforpeople.s3.amazonaws.com/images/209785d6-6bf4-49c7-8ecf-c6f567f06c01.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | a8d084bd5b118fdf632484a0157156
ax90-shrp-r1r9 | 1 |  | J7 Rw10 | 1218210204 | 15-03-2017 19:52:15 CET | Tuyisenge Vianney | 00:07:23 | 2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Rwanzu |  |  | Rwanzu wpt behind TCT/Nyirambuga pumping | 30604 |  | 154 | 154 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | GoR | BF behind TCT does no longer deliver water to the people | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.695966904039419 | 29.92121234277251 | 2125.8 | 25wt99zg | 1 | https://waterforpeople.s3.amazonaws.com/images/70b75409-b507-42e4-b8ca-4c6dfca1dd2e.jpg | 2012 | Does Not Function | No |  |  |  | Yes |  | Does Not Function | The Water point behind TCT does no longer operate | c89cf3db638ca23bf1964892fd5d50ad
4k85-fvm9-5ypr | 1 |  | J7 Rw10 | 1214290739 | 14-03-2017 22:30:53 CET | Tuyisenge Vianney | 00:06:53 | 2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kinini |  |  | BF at GS Rukingu/Gashinge gravity |  |  | 250 | 250 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | The water point at school operates well.And it benefits both the school and Kirenge cell office | 1 | Spring | -1.778040825436737 | 29.92360289445436 | 2013.8 | 29ok37c4 |  | Yes | 60 | No | [5 empty] | 60 | No | [5 empty] | Yes | 1 | -1.775790563569434 | 29.927050890820947 | 1881.6 | 29ku4o92 | https://waterforpeople.s3.amazonaws.com/images/7d99bea4-7a4b-4458-9dd3-8acf2fdc1f08.jpg | 2013 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7728107232288708 | 29.932516004663057 | 1802.9 | 29fwpi0t | 1 | https://waterforpeople.s3.amazonaws.com/images/466461c8-22b6-4918-a810-320ddff748b1.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | The water point functions well | 1d9afc9416346a77d491d365aa9b3ae
6kvw-6t90-eg9h | 1 |  | J7 Rw15 | 1212380184 | 08-03-2017 21:03:33 CET | Mukakarangwa Assoumpta | 00:08:43 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 6436 |  | 165 | 80 | 85 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Poor | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8635767134052266 | 29.980292034932003 | 1971 | 2dm0bot6 | 1 | https://waterforpeople.s3.amazonaws.com/images/f6e1a926-6a69-4356-aa7d-d7c3d7d27a93.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | 8aa4d81b089a62bfe591ce236899696
31r8-uxxt-phe8 | 1 |  | J7 Rw15 | 1436540069 | 02-06-2017 06:57:43 CEST | Mukakarangwa Assoumpta | 00:09:37 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Bikamba |  |  | Rwamugaza | 14106 |  | 205 | 20 | 185 | Yes | Piped Network -- Gravity Only |  | 2003 | Yes | all villages of Ntarabana | goverment |  | 2 | Spring | 1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | 1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 | Sedimentation Tank¦Pressure Break Tank¦Distribution Chamber |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.800192686860599 | 30.127577029012727 | 1470.6 | 2ap6uduj | 1 | https://waterforpeople.s3.amazonaws.com/images/aacab254-516a-4001-99f4-167814145a46.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | a475822b8e6921c9cb515783842c644
8y17-t9un-6ek7 | 1 |  | J7 Rw10 | 1215430239 | 10-03-2017 15:24:12 CET | Tuyisenge Vianney | 00:06:53 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Karambi |  |  | Karambi water point/Tare-Rusiga pumping | 9577 |  | 164 | 164 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Karambi water point is the 4th and last water point on Tare-Rusiga /Rusiga1 water network | 10 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 4000 | Yes | 1 | -1.7520229529077493 | 29.912761599884877 | 2174.1 | 28hixb7b | https://waterforpeople.s3.amazonaws.com/images/24cbbdfd-ef84-4e38-ae8d-586af7115fdc.jpg | 2015 | Normal | No | [5 empty] | Yes | 3 |  | 2015 | Normal | 8000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7516679156573711 | 29.913099504616316 | 2164.3 | 28gxhpfe | 1 | https://waterforpeople.s3.amazonaws.com/images/26e6e8a1-fad0-461f-846a-899a7c8c65b2.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Karambi water point is the 4th and last on Tare-Rusiga pumping/Rusiga distribution1 | 988b42233299e064fbdbad1d6618296
9qp2-d2s7-gq74 | 1 |  | J7 Rw15 | 1229190628 | 22-03-2017 19:03:50 CET | Mukakarangwa Assoumpta | 00:07:30 | 2017 | Rwanda | Rulindo | Kinihira | Butunzi | Akamiyove |  |  | Nyamagana-Kinihira |  |  | 132 | 60 | 72 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.9632014862039 | 1985.8 | 24rtx59s |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.673649818548059 | 29.95599502384405 | 1854.9 | 24vwds13 | 2 | https://waterforpeople.s3.amazonaws.com/images/a437afd6-1165-4b73-aa33-336d8b77271f.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | fb1c646bc83807faae79f36c57ce4
a9sa-u2u6-d2kr | 1 |  | J7 Rw8 | 1232810382 | 23-03-2017 07:47:23 CET | Amani Desire | 00:18:54 | 2017 | Rwanda | Rulindo | Murambi | Gatwa | Akarambi |  |  | Mutagata Motorised Network | 26296 |  | 206 | 106 | 100 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8209025305126023 | 30.038763139282636 | 1764.6 | 2bnfv2zn | 64 | https://waterforpeople.s3.amazonaws.com/images/dd652e6b-dbd0-4367-b6e9-98071e269154.jpg | 2016 | Does Not Function | Yes | 3 | 30 | water do not reach the water point it is closed because pipes are distroyed due to high pressure and there no storage reservoir | No | pipes that connect water to this water point is broken due to high pressure | Does Not Function | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | 9e22bbfc13d755cd3bc2d3e3f8bed6
4akq-4xx4-4y2w | 1 |  | J7 Rw24 | 1248050167 | 27-03-2017 15:27:54 CEST | Kabalisa Manzi Christella | 00:09:14 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Kararama network | 6572 |  | 965 | 965 | 0 | Yes | Piped Network with Pump |  | 2009 | No |  | Government |  | 3 | Spring | -1.7503785350192076 | 29.98212109950618 | 1826.3 | 28esosx9 |  | Yes | 4.5 | Yes | 1 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 14 | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | 2009 | Normal | Yes | 23 |  |  | 2009 | Normal | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7592862908351976 | 30.063929459836476 | 1829.8 | 28tj61jz | 1 | https://waterforpeople.s3.amazonaws.com/images/81eab247-793d-4cb6-83f1-2a35376583b0.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | This system gives not enough water but it is being rehabilitated | aa65cfa62ce0c3eb98f79f5e556397b0
4ej6-g8ct-xu8g | 1 |  | J7 Rw24 | 1248070242 | 28-03-2017 10:29:09 CEST | Kabalisa Manzi Christella | 00:05:10 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza network | 14106 |  | 229 | 229 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695880900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8067315434084603 | 30.123725561684097 | 1476.7 | 2b007vg5 | 1 | https://waterforpeople.s3.amazonaws.com/images/49a197f6-7ac2-4d06-8be0-95cbc6da953d.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | a25b6e4dfd4bdce9c55c3a8eac64a7cb
80tw-hyqm-rjtx | 1 |  | J7 Rw23 | 1325690054 | 23-04-2017 14:42:23 CEST | Rugirangoga Augustin | 00:14:24 | 2017 | Rwanda | Rulindo | Buyoga | Mwumba | Nyamwiza |  |  | kiruruma | 8295 |  | 149 | 120 | 29 | Yes | Piped Network with Pump |  | 2017 | Yes | nyamwiza nyarubuye gatenderi gatare shagasha | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 11 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2014 | Normal | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 9000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6795550908732244 | 30.01230695977452 | 2033 | 255o8yzf | 2 | https://waterforpeople.s3.amazonaws.com/images/a329c6ab-7cb5-442b-8d74-3716b78105de.jpg | 2017 | Normal | No |  |  |  | No | Water point under construction | Normal | This Water Point/system functions well | 9c738a3b3a739f8af785734f355d9cb
rsgt-fn49-fcjy | 1 |  | J7 Rw24 | 1220210290 | 15-03-2017 14:28:53 CET | Kabalisa Manzi Christella | 00:16:36 | 2017 | Rwanda | Rulindo | Cyinzuzi | Migendezo | Marembo |  |  | 0 | 14106 |  | 735 | 735 | 0 | Yes | Piped Network with Pump |  | 2009 | No |  | umushinga witwa ema | No Problem with the Water Point | 3 | Spring | 1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2009 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 16 | -1.7543004341479447 | 29.99197561543003 | 2178 | 28lao5qn |  | 2009 | Normal | Yes | 23 |  |  | 2009 | Normal | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7794687617826475 | 30.00016101849992 | 2138 | 29qwmrtt | 1 | https://waterforpeople.s3.amazonaws.com/images/5d842f78-4e23-4673-9ecd-29311aec9724.jpg | 2009 | Normal | No |  |  |  | Yes |  | Normal | harakora ariko havomwaho nabantu benshi cyane | 54e48f65edfba53e1b309c1a2cd56dc
296f-ysk4-hd6d | 1 |  | J7 Rw23 | 1204230251 | 09-03-2017 07:35:42 CET | Rugirangoga Augustin | 00:32:54 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 1458 |  | 229 | 200 | 29 | Yes | Piped Network -- Gravity Only |  | 2005 | No |  | Governement (District, WASAC) and Water For People | this system works well except some defects of the pipe. | 1 | Spring | -1.6426625760859115 | 29.882931577022582 |  | 23gnwvd9 |  | Yes | 75 | Yes | 1 |  | start chamber | 2005 | Normal | 75 | Yes | 1 |  | 2016 | Normal | 2000 | Yes | 1 | -1.6503480343855401 | 29.882910347806035 | 1718 | 23td5ryl |  | 2005 | Normal | Yes | 2 | break pressure |  | 2016 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6515396305945012 | 29.881153191553434 | 1730.3 | 23vc0cxn | 2 |  | 2016 | Normal | No |  |  |  | Yes |  | Normal | System works but there are some pipes that were destroyed | 1ede28acec24743a1373be541ff91a
34vg-yxvc-44be | 1 |  | J7 Rw24 | 1330410426 | 24-04-2017 23:11:06 CEST | Kabalisa Manzi Christella | 00:28:04 | 2017 | Rwanda | Rulindo | Burega | Karengeli | Bugoboka |  |  | Rwamugaza network | 14106 |  | 80 | 80 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 1 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7374173333138418 | 30.06563288387298 | 1723.9 | 27td31kg |  | 2003 | Normal | Yes | 14 |  |  | 2003 | Normal | Yes | 1 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7195529585349403 | 30.052250887948166 | 1602.7 | 26ztqv1m | 1 | https://waterforpeople.s3.amazonaws.com/images/688a5900-ca4c-4eaf-864b-89b407f40fb4.jpg | 2013 | Poor | No |  |  |  | Yes |  | Normal |  | 8e832089e4c2a3398af1428caa1375b
pgex-gxp4-h0a2 | 1 |  | J7 Rw23 | 1213280166 | 11-03-2017 20:03:44 CET | Rugirangoga Augustin | 00:17:11 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Cyondo |  |  | Ruramba | 1564 |  | 173 | 150 | 23 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | this network has been destroyed by the road Base-Gicumbi which is in construction | 1 | Spring | -1.612504606727932 | 29.86882944818841 | 1922.4 | 222s9irk |  | Yes | 60 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 60 | Yes | 1 |  | 2016 | Does Not Function | 4500 | Yes | 2 | -1.6213170406640873 | 29.869799421143036 | 1873.1 | 22hcseq1 |  | 2016 | Normal | Yes | 2 | Pressure Break Tank |  | 2016 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.615412382017564 | 29.867567497895134 | 682.8 | 227linsj | 1 | https://waterforpeople.s3.amazonaws.com/images/74fc8b4c-9ba8-4b62-9b4d-3617aad7d418.jpg | 2016 | Normal | No |  |  |  | Yes |  | Poor | This Water Point/system functions well | c4c688c76c012fc1aa603ea240407c
td1x-yjrx-kf89 | 1 |  | J7 Rw7 | 1239290080 | 24-03-2017 11:50:03 CET | Safari Bosco | 00:10:41 | 2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Kabuga |  |  |  | 5544 |  | 119 | 119 | 0 | Yes | Piped Network with Pump |  | 1998 | Yes | kabunga,kingomwo | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 35.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8173224622489657 | 30.050001367196714 | 1837.8 | 2bhipwic | 2 | https://waterforpeople.s3.amazonaws.com/images/e412b4d8-3b5b-4e4c-a47e-07812784058e.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 50b0f3367d90f86286d643ceae417c37
fgbq-1r3m-atbw | 1 |  | J7 Rw19 | 1244610329 | 23-03-2017 04:57:00 CET | Kayinamura Innocent | 00:14:42 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Nyarurembo |  |  | Mutagata motorised network | 26296 |  | 144 | 48 | 96 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.5 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7946230613999719 | 30.041303543245995 | 1934.2 | 2afz7x8d | 64 | https://waterforpeople.s3.amazonaws.com/images/14b8b1c2-51b2-45eb-a747-e76ce813fb7c.jpg | 2016 | Poor | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 271196796a5a2fe2317001d359d5953
d6v8-2kue-px5u | 1 |  | J7 Rw24 | 1226541097 | 15-03-2017 16:59:08 CET | Kabalisa Manzi Christella | 00:18:29 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Gacyamo |  |  | Rwamugaza | 14106 |  | 550 | 550 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | No Problem with the Water Point | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 23 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7498236137603536 | 30.053069331787793 | 1875.5 | 28dvxz76 | 1 | https://waterforpeople.s3.amazonaws.com/images/5942d987-d715-4d97-900e-33f5457d2688.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | 7411bc2242eed9b6134c6bbd14c91d86
4bg9-hqtm-6tb1 | 1 |  | J7 Rw24 | 1247160141 | 28-03-2017 09:26:51 CEST | Kabalisa Manzi Christella | 00:10:41 | 2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Karambi |  |  | Gahama Kisaro network | 10234 |  | 184 | 184 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6671501074688961 | 30.041830412153367 | 1945.4 | 24l5zh36 |  | Yes | 3 | Yes | 1 |  |  | 2012 | Normal | 3 | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 |  |  | 2012 | Normal | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Poor | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6305414114893337 | 30.051507988666785 | 2033.6 | 22wmbjhf | 1 | https://waterforpeople.s3.amazonaws.com/images/cb2071f8-6667-4798-90f4-5d7678c84cac.jpg | 2012 | Poor | No |  |  |  | No | Pipes Broken | Poor | This system has rehabilitation | a09e538a632a6514116fd71dd772eb48
x1tg-shxm-y8ww | 1 |  | J7 Rw10 | 1228190563 | 02-01-2015 12:56:53 CET | Tuyisenge Vianney | 00:05:27 | 2017 | Rwanda | Rulindo | Buyoga | Karama | Cyasenga |  |  | Water point near GS Kadendegere/Nyirambuga pumping | 30604 |  | 165 | 165 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point near GS Kadendegere.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water. | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.7147904088084454 | 29.982877052474294 | 2116.2 | 26rycik4 | https://waterforpeople.s3.amazonaws.com/images/e8c5c84e-8fcb-4f97-ae96-8d835914c4b1.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7150014857198 | 29.982856515620824 | 2123.6 | 26saum9g | 2 | https://waterforpeople.s3.amazonaws.com/images/66380744-a677-4368-bdf1-ff8f2685bc4c.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point near GS Kadendegere.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water.Several valve chambers are nolonger having covers. | 9318b91b1e4e61c874c56738ca280b1
scjp-vm0d-60bg | 1 |  | J7 Rw15 | 1209680458 | 09-03-2017 21:13:37 CET | Mukakarangwa Assoumpta | 00:12:46 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Gishyita |  |  | Bitete-Rwahi network | 1316 |  | 205 | 60 | 145 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.8336417737979869 | 29.94346668826428 | 1815.5 | 2c8iday2 |  | Yes | 12 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 |  | 2013 | Normal | 600 | Yes | 6 | 1.8427360326225883 | 29.938932546871705 | 1676.5 | 2cnjkbst |  | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8661493441761918 | 29.93641903907126 | 1434.4 | 2dq9c2xw | 1 | https://waterforpeople.s3.amazonaws.com/images/714341aa-e26c-49eb-be1a-cd45d19687fe.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 15f920ba597bb89bbb193afdc3a73a82
8a1e-jtxm-h5cw | 1 |  | J7 Rw15 | 1430230085 | 02-06-2017 06:47:34 CEST | Mukakarangwa Assoumpta | 00:16:14 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza | 14106 |  | 229 | 10 | 219 | Yes | Piped Network -- Gravity Only |  | 2003 | Yes | all villages of Ntarabana | Goverment |  | 2 | Spring | 1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 12 | 1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 | Distribution Chamber |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8076551471925206 | 30.117101264526102 | 1615 | 2b1izr1v | 3 | https://waterforpeople.s3.amazonaws.com/images/1fb45ed0-5c62-404d-8bd0-0a5b5b3217e7.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | 906da6cc431acc8b04f1986d7b7e9f
dmhn-mj9n-1kha | 1 |  | J7 Rw10 | 1300330148 | 16-04-2017 22:38:22 CEST | Tuyisenge Vianney | 00:08:10 | 2017 | Rwanda | Rulindo | Buyoga | Busoro | Rugarama |  |  | Water point at EP Busoro/Nyirambuga pumping system | 30604 |  | 189 | 189 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | In use,operational water point | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.7073858286988044 | 29.997679068927205 | 2098.8 | 26fp6bew | https://waterforpeople.s3.amazonaws.com/images/41eb8d34-e4a0-4b36-af16-e8f6092369c5.jpg | 2012 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7071950612311753 | 29.998289373222647 | 2082.5 | 26fdv2xa | 4 | https://waterforpeople.s3.amazonaws.com/images/e6eae2a5-b6db-4c89-82a4-52dd847d12a6.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | In use,operational water point | 7ee6bfb793944365730d412fcfbdf49
13c6-t99h-g090 | 1 |  | J7 Rw10 | 1226780410 | 16-03-2017 17:17:56 CET | Tuyisenge Vianney | 00:13:44 | 2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Muduha |  |  | Muduha water point/Matonyanga gravity |  |  | 160 | 160 | 0 | Yes | Piped Network -- Gravity Only |  | 2017 | No |  | Governement (District, WASAC) and Water For People | This is a water point located at Muduha and supplied by Matonyanga gravity system.Its construction has been completed recently | 1 | Spring | -1.69919116767908 | 29.937233740854015 | 1848.2 | 2625kai4 |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | Yes | 1 | -1.7067925055000475 | 29.928944153057586 | 1758.4 | 26eq1q6x | https://waterforpeople.s3.amazonaws.com/images/18356c5a-e5dc-448f-866a-f3da0e23aebb.jpg | 2017 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.70732581142553 | 29.928939057715475 | 1746.3 | 26fllp95 | 1 | https://waterforpeople.s3.amazonaws.com/images/fa1f877b-36f1-412c-8c10-b85791a261cd.jpg | 2017 | Normal | No |  |  |  | No | It has been completed very soon but not yet delivering water to the people | Normal | Constructed very soon and has been tested today to see if the water reaches however it hasn't yet delivered water to the people.They fetch on water spring | 9adebdd8acbe9711e165861a8e05a8f
45vr-sqc6-wjyx | 1 |  | J7 Rw15 | 1207080249 | 08-03-2017 21:14:49 CET | Mukakarangwa Assoumpta | 00:06:12 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 6436 |  | 165 | 32 | 133 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8579701155074921 | 29.971834085984334 | 1986.4 | 2dcqwxza | 1 | https://waterforpeople.s3.amazonaws.com/images/aecf1ff2-d3b9-4b22-9bbb-0ae692a8d403.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | e1ea54497893967c2e715fcc47db917
wmu6-s0m3-49a7 | 1 |  | J7 Rw10 | 1304420096 | 14-04-2017 22:14:15 CEST | Tuyisenge Vianney | 00:05:21 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Gitwa |  |  | Gitwa water point/Nkombe gravity system |  |  | 134 | 134 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | COFORWA | This is a water point connected to Nkombe gravity system located in Gitwa village nearby Rulindo catholic parish.It operates well | 1 | Spring | -1.726263209282846 | 29.90351686333194 | 2121.4 | 27ax8ot7 |  | Yes | 1.02 | No | [5 empty] | 1.02 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7248422184021135 | 29.922009288402315 | 1866.6 | 278kp51w | 1 | https://waterforpeople.s3.amazonaws.com/images/e5627a09-7dcc-4a5e-8f3d-a3cf814718c0.jpg | 2002 | Normal | No |  |  |  | Yes |  | Normal | This is a water point connected to Nkombe gravity system located in Gitwa village nearby Rulindo catholic parish.It operates well | e0588fd992d7fe3459a72279575cfc
kvmp-dvuk-d2ej | 1 |  | J7 Rw8 | 1193280316 | 07-03-2017 15:18:26 CET | Amani Desire | 00:16:58 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kibaya |  |  | Mutungo | 510 |  | 133 | 73 | 60 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | kibaya ,Ruhanya |  |  | 1 | Spring | -1.76948858676096 | 29.9450760030861 | 1922.1 | 29aeg5oa |  | No | 24 | No | [5 empty] | 24 | Yes | 1 |  | 2004 | Poor | 500 | Yes | 2 | -1.7685825306926122 | 29.944785701134276 | 1910.6 | 298wv587 |  | 2004 | Poor | No | [5 empty] | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/ff80917c-1ee5-493c-bb80-3629c776d1d1.jpg | 2004 | Poor | 2000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7433973625715677 | 29.94460199884638 | 1767.6 | 283948dy | 1 | https://waterforpeople.s3.amazonaws.com/images/62424f88-48f7-4eeb-bd63-4d4ef9d34877.jpg | 2004 | Poor | No |  |  |  | Yes |  | Poor | the water point structure is damaged there is no water tap water is flowing every day | dac173a23afd4741d588da084845ff2
yb7g-ttkx-ef08 | 1 |  | J7 Rw24 | 1328920059 | 25-04-2017 17:01:39 CEST | Kabalisa Manzi Christella | 00:07:09 | 2017 | Rwanda | Rulindo | Kisaro | Murama | Kibingwe | [5 empty] | 122 | 122 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 1 | Spring | -1.6200005552162142 | 30.02248352098647 | 2050.5 | 22f6snnk |  | Yes | 120 | Yes | 1 |  |  | 2003 | Normal | 120 | Yes | 2 |  | 2003 | Normal | 30000 | Yes | 7 | -1.6225195031496076 | 30.023722788318132 | 2089 | 22jc8gi5 | https://waterforpeople.s3.amazonaws.com/images/cdafb73f-6593-4d27-97b3-250136a75df4.jpg | 2003 | Normal | Yes | 14 |  |  | 2003 | Normal | Yes | 1 |  | 2003 | Normal | 30000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6225447493889298 | 30.023726690033268 | 2055.8 | 22je0rbh | 1 | https://waterforpeople.s3.amazonaws.com/images/cb93a58e-1e91-4821-8936-8615f93cac34.jpg | 2003 | Does Not Function | No |  |  |  | No | Broken parts | Poor |  | f615dec363bf3c9c383f16c6f3e3e3
83uk-h4ua-vx4j | 1 |  | J7 Rw7 | 1243630319 | 20-03-2017 11:01:49 CET | Safari Bosco | 00:29:07 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 5544 |  | 27 | 27 | 0 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | Water points is functioning well | 2 | Spring | -1.8173580437936339 | 30.0498914272377 | 1873 | 2bhki7bm |  | Yes | 43 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 45 | Yes | 1 |  | 2016 | Normal | 500 | Yes | 2 | -1.8203078904726735 | 30.052799088587552 | 1897.1 | 2bmg52sv |  | 2016 | Normal | Yes | 0 | Distribution Chamber |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 500 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8173534680869354 | 30.050040961084957 | 1851 | 2bhki7bo | 0 |  | 2016 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | b274fa345961715d6cde8c88438aee
9pgv-uj7y-5pt6 | 1 |  | J7 Rw19 | 1241930254 | 23-03-2017 05:35:51 CET | Kayinamura Innocent | 00:12:49 | 2017 | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 26296 |  | 325 | 63 | 262 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.801550488976415 | 30.055981410053793 | 1705.7 | 2arftbkf | 64 | https://waterforpeople.s3.amazonaws.com/images/ab37bbb5-bd39-4d9a-a33e-f367530cf63b.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 7e5256b2f3662327c124b71aa3aafe26
1bgr-eudk-ur8 | 1 |  | J7 Rw10 | 1208712114 | 10-03-2017 10:12:55 CET | Tuyisenge Vianney | 00:08:05 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Byimana |  |  | Byimana water point/Tare-Rusiga pumping | 9577 |  | 92 | 92 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This is Byimana water point.It has water but the people haven't yet chosen a tap manager.They are fetching water in nearby water point located in Sina College | 10 | Spring | -1.737938326200818 | 29.906994158112184 | 2017.8 | 27u81jst |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 4000 | No | [8 empty] | No | [5 empty] | No | [5 empty] | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6804385409532798 | 29.88784980482459 | 2099.3 | 2574n39a | 2 | https://waterforpeople.s3.amazonaws.com/images/8381983f-02ba-4d54-8fde-8995f51837ae.jpg | 2015 | Normal | No |  |  |  | No | The water is closed due to lack of tap manager | Normal | This water tap needs to get a tap manager in order to deliver satisfactory services to the people | 6aa7b667bdef1ba172eab19a4a6ad65
he4u-49py-94jn | 1 |  | J7 Rw7 | 1233820600 | 24-03-2017 12:18:04 CET | Safari Bosco | 00:07:28 | 2017 | Rwanda | Rulindo | Masoro | Shengampuri | Agasharu |  |  |  | 6740 |  | 130 | 130 | 0 | Yes | Piped Network with Pump |  | 1998 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8153520544793162 | 30.06043364802043 | 1855.5 | 2be9fif0 | 1 | https://waterforpeople.s3.amazonaws.com/images/268e6202-82bb-4584-bc10-7930d931b29f.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | ede59b43c88f8d2c4682bfe3f3d2efe
6y1d-p6gy-vv5c | 1 |  | J7 Rw10 | 1273250120 | 05-04-2017 22:00:55 CEST | Tuyisenge Vianney | 00:15:03 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Ngarama |  |  | Water point at Nyirangarama cell/Rutare-Nyirangarama gravity | 726 |  | 109 | 109 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Local government in Ubudehe program | Water point at Nyirangarama cell/Rutare-Nyirangarama gravity is operational and functional | 1 | Spring | -1.67056768280477222 | 29.878696276428556 | 2067 | 24qt0942 |  | Yes | 20 | No | [5 empty] | 20 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6668679021136406 | 29.89089442233963 | 1759 | 24kopvdo | 1 | https://waterforpeople.s3.amazonaws.com/images/f5166c02-e3c8-4902-949e-958736647e79.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | Water point at Nyirangarama cell/Rutare-Nyirangarama gravity is operational and functional | 4a29e8ab1d95bb2a4cd10dd7fe32cb6
csmy-4192-003k | 1 |  | J7 Rw8 | 1218941389 | 16-03-2017 08:50:37 CET | Amani Desire | 00:11:14 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Ruhanya |  |  | Musenge Network | 6074 |  | 102 | 52 | 50 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi | WFP |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber¦washout and Air release |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7510960822062243 | 29.93535369036495 | 2119.2 | 28fzk049 | 28 | https://waterforpeople.s3.amazonaws.com/images/4a4405fa-3118-4f4a-9fd9-03c64d11f821.jpg | 2014 | Does Not Function | Yes | 8 | 30 | water do not reach the distribution Reservoir R50m3 located at kibamba village that serves the water point | No | water doesnt reach the distribution located at kibamba and all water points served by this R50m3 doesnt have water | Does Not Function | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | 2835c12647964b5e97772b8204255b3
y7qp-vseb-8sgv | 1 |  | J7 Rw10 | 1222050248 | 15-03-2017 20:04:25 CET | Tuyisenge Vianney | 00:09:50 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Marembo center water point/Nyirambuga pumping | 30604 |  | 134 | 134 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | GoR | Marembo center water point operates well and normally | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.6866913809480875 | 29.91363828399236 | 2135.8 | 25hhcg5c | https://waterforpeople.s3.amazonaws.com/images/2a676cf3-bfda-449a-831d-b777e6ce6e9d.jpg | 2012 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.687063723761654 | 29.913872032111886 | 2100.3 | 25i3dhj6 | 1 | https://waterforpeople.s3.amazonaws.com/images/0b9f9fd7-6e86-4ba3-99ee-fce80ff8f464.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Marembo center water point operates well and normally | c4792faf9b5371ed6fd0528aa1dddb
9106-dqmk-ty6d | 1 |  | J7 Rw24 | 1220250195 | 15-03-2017 14:21:35 CET | Kabalisa Manzi Christella | 00:48:54 | 2017 | Rwanda | Rulindo | Cyinzuzi | Migendezo | Nyamugali |  |  |  | 14106 |  | 111 | 111 | 0 | Yes | Piped Network with Pump |  | 2009 | Yes | Budakiranya, Nyamugali | Umushinga witwa Ema | The system is functioning well | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye | https://waterforpeople.s3.amazonaws.com/images/b9274302-4be6-45cc-95cc-652e74ccfac2.jpg | Yes | 4.5 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/aa021452-a6ea-40f8-8e77-9864c7b1d7de.jpg | "Springbox" --Intake Structure at a Spring | 2009 | Poor | 4.5 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/45f90fee-8669-4523-a8cf-e40e77266ced.jpg | 2009 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc | https://waterforpeople.s3.amazonaws.com/images/bee03fa4-a5f4-4bc1-9878-f9c72bbbae70.jpg | 2009 | Normal | Yes | 23 | vantouse, vidange |  | 2009 | Normal | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/87cfe062-e19f-4043-84a2-b4ff92c34da4.jpg | 2009 | Normal | 5000 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/c3ee5ab4-264a-40ea-b9c8-026ebcc5d7cf.jpg | 2009 | Normal | Yes | https://waterforpeople.s3.amazonaws.com/images/2382386a-f809-4b6e-a63e-bf808af88c92.jpg | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7457223541423337 | 30.00372297540776 | 2114.6 | 2873u8sl | 1 | https://waterforpeople.s3.amazonaws.com/images/3845eee5-c108-4a77-b3b4-3da8854a1a66.jpg | 2009 | Normal | No |  |  |  | Yes |  | Normal | there is no problem | 4d1ec8d23a39c51d70445de05a3e8c2
j9by-56ua-26cq | 1 |  | J7 Rw15 | 1203320177 | 08-03-2017 19:29:38 CET | Mukakarangwa Assoumpta | 00:09:11 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gisiza |  |  | kinywamagana pumping network | 6436 |  | 212 | 105 | 107 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8561573562245208 | 29.98258987782091 | 1842.2 | 2d9qk1yp | 1 | https://waterforpeople.s3.amazonaws.com/images/560bf1aa-31b1-4f9d-bed0-4283fdbde257.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | a52e87b938bedb63104fe11d7872e8
a6q8-0qgj-a8b8 | 1 |  | J7 Rw10 | 1214120898 | 13-03-2017 08:55:01 CET | Tuyisenge Vianney | 00:09:33 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Terambere |  |  | Terambere water point/Nyabishengeshi water gravity system | 893 |  | 79 | 79 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | This is the 2water point for Nyabishengeshi gravity | 2 | Spring | -1.6778517470929726 | 29.880934967401814 | 2032.3 | 252v194p |  | Yes | 50 | No | [5 empty] | 50 | Yes | 1 |  | 2013 | Normal | 100 | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.67282643845523 | 29.88472335787712 | 1961.8 | 24ujk7vj | 1 | https://waterforpeople.s3.amazonaws.com/images/0cff6d9b-6d0c-4c77-b534-ea9eb1beff9e.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | This is the 2nd water point for Nyabishengeshi gravity | 05d78d12c9af9a627e70a746d747e
ema8-5tvu-3q0x | 1 |  | J7 Rw26 | 1211140135 | 11-03-2017 09:03:16 CET | Byukusenge Elie | 00:13:03 | 2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 20456 |  | 50 | 45 | 5 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank | This network serves four sectors Cyungo,Rukozo, Base,Base and Kinihira, It has some problems in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible because it serves many populations and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6235338105458779 | 29.94731108238126 | 1855 | 22l0ynm9 | 29 | https://waterforpeople.s3.amazonaws.com/images/3353f6d8-b8dc-40f5-a225-0fa368bf41dd.jpg | 2011 | Poor | Yes | 12 | 30 | Bad tee junctions connection and types of pipeline needs to be replaced | No | There is no Taps on the water tap | Poor | This water tap does not in service | ac47132b9edc94ae3266968f9294ab2
4nfk-6wdr-5a5r | 1 |  | J7 Rw7 | 1235310900 | 23-03-2017 18:05:37 CET | Safari Bosco | 01:34:02 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 5544 |  | 214 | 214 | 0 | Yes | Piped Network with Pump |  | 1986 | No |  | Governement (District, WASAC) and Water For People | This System was built in 1986 had a few problems in the Past but now working well | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy | https://waterforpeople.s3.amazonaws.com/images/66494d82-a5e6-4c65-afa0-c34972a7ac88.jpg | Yes | 20 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/30200462-881c-4fd8-b5ca-12b554d70960.jpg | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/3f2f3540-598c-410d-ae24-00ea103e5611.jpg | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.05522315814525 | 1892.4 | 2bqqcci0 | https://waterforpeople.s3.amazonaws.com/images/feed686c-8e56-42f2-9966-fcbdf8dc6acf.jpg | 2016 | Normal | No | [5 empty] | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/282196af-0db2-4243-a52f-435e38dae99e.jpg | 2016 | Normal | 5000 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/8ee42012-e0a0-43e5-99e3-5c68a9fa3736.jpg | 2016 | Normal | Yes | https://waterforpeople.s3.amazonaws.com/images/a561f8ba-a867-442d-a988-c5bb4c1c7002.jpg | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8284906124110314 | 30.064097137403223 | 1580.8 | 2bzzr3c0 | 1 | https://waterforpeople.s3.amazonaws.com/images/7fca4e1b-0091-43aa-890e-6e2b9d06deb7.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | In the dry season there is not enough water | 528de4a9a6c9b8fa74fdcb4ed1f432a
qrys-5e82-yxg1 | 1 |  | J7 Rw23 | 1213320086 | 11-03-2017 20:03:31 CET | Rugirangoga Augustin | 00:24:03 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Cyondo |  |  | Ruramba | 1564 |  | 173 | 150 | 23 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | This system was destroyed by the road construction of Base-Gicumbi. | 1 | Groundwater (well, etc.) | -1.612504606727932 | 29.86882944818841 | 1922.4 | 222s9irk |  | Yes | 60 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2017 | Normal | 60 | Yes | 1 |  | 2016 | Does Not Function | 4500 | Yes | 2 | -1.6213170406640873 | 29.869799421143036 | 1873.1 | 22hcseq1 | https://waterforpeople.s3.amazonaws.com/images/e5168819-ab0c-47aa-8eff-7f46d9412b92.jpg | 2016 | Normal | Yes | 2 | Sedimentation Tank | https://waterforpeople.s3.amazonaws.com/images/16cd190b-b6fa-4c36-995b-d2303eb40c62.jpg | 2016 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6213840773706165 | 29.86975359907686 | 1900 | 22hgyfyh | 2 | https://waterforpeople.s3.amazonaws.com/images/2c4a7193-5c75-4f16-be72-ca1684ed5afe.jpg | 2016 | Does Not Function | No |  |  |  | No | Pipes Destroyed by road construction | Does Not Function | Water is not Flowing because pipes were destroyed during road construction | 37a3d4b846e8aada7e39ecf61bbcc1f3
7cvn-vrnn-4j9x | 1 |  | J7 Rw15 | 1201250966 | 09-03-2017 22:32:54 CET | Mukakarangwa Assoumpta | 00:06:48 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Ngona |  |  | Bitete-Rwahi network | 1316 |  | 122 | 28 | 94 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.8336417737979869 | 29.94346668826428 | 1815.5 | 2c8iday2 |  | Yes | 12 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 |  | 2013 | Normal | 600 | Yes | 6 | 1.8427360326225883 | 29.938932546871705 | 1676.5 | 2cnjkbst |  | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8564441973996932 | 29.930573110361 | 1437.3 | 2da7tm3t | 1 | https://waterforpeople.s3.amazonaws.com/images/01a9075c-949a-46f1-a665-4e49b7a3b959.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | a97188d9508fdc2c1fae74914821c6a2
hsy5-waeh-ndaf | 1 |  | J7 Rw26 | 1202150113 | 02-01-2015 05:51:45 CET | Byukusenge Elie | 00:09:18 | 2017 | Rwanda | Rulindo | Cyungo | Burehe | Nyagatovu |  |  | Nyamagana | 20456 |  | 100 | 70 | 30 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2011 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6275333762731001 | 29.942125147644514 | 1828.8 | 22rn41jx | 29 | https://waterforpeople.s3.amazonaws.com/images/d4b31e48-0382-4251-a888-844520e40db3.jpg | 2011 | Normal | Yes | 10 | 28 | bad connection of tee junctions towards Burehe and the distribution reservoir does not supply water in this transmission line | No | The distribution reservoir does not supply water in this transmission line | Poor | water tap used by G.S Urumuli | a7dfb369377bd1a64ca4f67e43e91d
32m0-qpc7-w17d | 1 |  | J7 Rw23 | 1232050840 | 24-03-2017 15:50:15 CET | Rugirangoga Augustin | 00:27:38 | 2017 | Rwanda | Rulindo | Buyoga | Butare | Ryanyirakayobe |  |  | Nyagahera |  |  | 96 | 80 | 16 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | kankanga ryanyirakayobe karambi | Governement (District, WASAC) and Water For People | This system has a problem at the source in Giko and Gasave village have to draw water form Nyagahera source in the valley which is far | 1 | Spring | -1.69921094772796 | 30.01400249942007 | 1901.3 | 2626r6b0 | https://waterforpeople.s3.amazonaws.com/images/27e3162a-2b69-4614-8951-d87d35a2c939.jpg | Yes | 16 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Poor | 16 | Yes | 2 |  | 2014 | Poor | 6800 | Yes | 3 | -1.6902852583901373 | 30.034148165390133 | 1811.3 | 25nf3391 |  | 2014 | Normal | Yes | 3 | Distribution Chamber |  | 2014 | Normal | Yes | 1 |  | 2014 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6998524103692088 | 30.014700874912368 | 1813.1 | 2638ux0z | 1 | https://waterforpeople.s3.amazonaws.com/images/f3967639-84d7-418c-9177-020ea07a8191.jpg | 2014 | Poor | No |  |  |  | Yes |  | Poor | Water is not enough, People are not buying Water as it should be, pipes destroyed due to terracing in Shagasha area | 607142eae03085a18febdb99f17126f5
b084-wwra-gkyq | 1 |  | J7 Rw8 | 1242980130 | 23-03-2017 11:49:25 CET | Amani Desire | 00:06:53 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | Mutagata Gravity Network | 26296 |  | 214 | 52 | 162 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | Ruri,musenga,umubuga,amataba,rusine,marenge |  |  | 1 | Spring | -1.8023389079852206 | 30.042447389592418 | 1691.2 | 2asq94nc |  | Yes | 8 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2004 | Poor | 8 | Yes | 1 |  | 2004 | Poor | 3500 | Yes | 6 | -1.8078446763653504 | 30.066649761552014 | 1669.8 | 2b1uaz5m |  | 2004 | Poor | Yes | 4 | Distribution Chamber¦Washout and Air release chamber |  | 2004 | Poor | Yes | 2 |  | 2004 | Poor | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.822563608753177 | 30.07032375640766 | 1645.7 | 2bq6p1nj | 12 | https://waterforpeople.s3.amazonaws.com/images/97995876-87df-4fde-8b0a-f222330dd73f.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.the extension to nyabinyana village has 2 reservoirs and two water points which is under construction 2.this system have been constructed in 2004 3.it serves a part of Masoro sector and parts is located in Gasabo district 4. 2 water points and one reservoir have been constructed in 2016 5.in general this network has 27 water points in wich 12 are in Rulindo district and others are in Gasbo district | 98a995996dd47223b2b5cf70464e7085
qtqx-2yr7-kj7n | 1 |  | J7 Rw19 | 1239720977 | 23-03-2017 11:39:08 CET | Kayinamura Innocent | 00:20:59 | 2017 | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 26296 |  | 325 | 65 | 260 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7995001817360075 | 30.05233655031154 | 1754.5 | 2ao1rgiz | 64 | https://waterforpeople.s3.amazonaws.com/images/4d369fab-0a6e-444f-9254-2e6bd0346419.jpg | 2016 | Poor | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | fcf7d5836d1c33df6f2253dd9987e51f
h8p6-3phw-tcs0 | 1 |  | J7 Rw23 | 1216030759 | 15-03-2017 06:55:52 CET | Rugirangoga Augustin | 00:41:42 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Mutima |  |  | Rutare I | 345 |  | 229 | 200 | 29 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.6301134502114292 | 29.875285172506338 | 2066.9 | 22vwpv40 | https://waterforpeople.s3.amazonaws.com/images/a21f521c-c774-4b8b-9f00-970f03234911.jpg | Yes | 50 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/565b91f0-5118-4a4c-8ce5-bcc7c0191eae.jpg | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 75 | No | [5 empty] | Yes | 1 | -1.6508336759560134 | 29.884394940764913 | 1503.1 | 23u6c0m3 |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6299827121780204 | 29.875537886330296 | 1993.1 | 22voz88z | 2 | https://waterforpeople.s3.amazonaws.com/images/2fdc2f91-78d8-413b-9918-17dd0998ccf8.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | this network has no many problems. it has been rehabilitated by waterforpeople in 2016 | 1c14241824ff21b8e588b66f4e5
yrq1-0cuj-d75r | 1 |  | J7 Rw15 | 1208000204 | 08-03-2017 21:41:44 CET | Mukakarangwa Assoumpta | 00:06:59 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 6436 |  | 354 | 150 | 204 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8709772985000082 | 29.963718529847842 | 1873.1 | 2dy8wgc5 | 1 | https://waterforpeople.s3.amazonaws.com/images/a52d5fe4-92da-4fbd-b0e7-49a4022bdd8b.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 6d0cdbcd4289584caed8ecb14a22f9
bvp3-6r1c-y3h7 | 1 |  | J7 Rw24 | 1221260156 | 16-03-2017 07:00:53 CET | Kabalisa Manzi Christella | 00:06:52 | 2017 | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 14106 |  | 495 | 495 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | no problem | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  | https://waterforpeople.s3.amazonaws.com/images/16722023-31ec-470b-8303-2a6a2cb985d8.jpg | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2006 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7348297751697161 | 30.034002673540108 | 2018.7 | 27p2vrn8 | 1 | https://waterforpeople.s3.amazonaws.com/images/d108717d-3d76-48c1-bafc-4d2bbb41871b.jpg | 2012 | Normal | No |  |  |  | No | People use other taps around | Does Not Function | no problem | e81aa661f31ef8bfaf402077e6c8f38a
w2ea-dr1y-ru22 | 1 |  | J7 Rw23 | 1196240345 | 08-03-2017 18:53:06 CET | Rugirangoga Augustin | 00:32:57 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Mutima |  |  | Rutare I | 345 |  | 169 | 140 | 29 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | mutima base | Governement (District, WASAC) and Water For People | This system is new but was destroyed partly a road being constructed | 1 | Spring | -1.6301829505751766 | 29.875821766632345 | 1956.8 | 22w0vwcm |  | Yes | 20 | No | [5 empty] | 20 | Yes | 1 |  | 2016 | Normal | 3800 | Yes | 2 | -1.6421782827296525 | 29.877214231989047 | 1817 | 23fuqmok |  | 2016 | Normal | No | [5 empty] | Yes | 1 |  | 2016 | Normal | 3800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6337584808545729 | 29.874092577330256 | 1868.7 | 231xfnas | 2 |  | 2016 | Poor | Yes | 3 | 8 | ibikorwa byo kubaka umuhanda byarawangije | Yes |  | Poor | ntakindi kibazo umuyoboro ufite uretse amatuyaux umuhanda urikubakwa waciye | a0b2be7d2b79ab4b20a966f1f574447f
usp4-vpj6-xvdb | 1 |  | J7 Rw23 | 1215191564 | 15-03-2017 06:06:22 CET | Rugirangoga Augustin | 00:20:13 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Kiruli |  |  | Migogo | 558 |  | 223 | 200 | 23 | Yes | Piped Network -- Gravity Only |  | 2009 | Yes | kiruli rubanda bukangano kabahama | padiri(LAKE ANGELS). |  | 1 | Spring | -1.6327309674421784 | 29.901262305566668 |  | 2308pft0 |  | Yes | 50 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2009 | Poor | 50 | Yes | 1 |  | 2009 | Poor | 6800 | Yes | 3 | -1.6327309674421784 | 29.901262305566668 | 1900.3 | 2308pft0 |  | 2009 | Poor | No | [5 empty] | Yes | 1 |  | 2009 | Poor | 6800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6406523831972173 | 29.894596541227557 | 806.9 | 23dc8qv5 | 2 | https://waterforpeople.s3.amazonaws.com/images/90878733-e28f-42c0-9dec-d99e0c088816.jpg | 2009 | Normal | No |  |  |  | Yes |  | Poor | this network needs rehabilitation | c75671f668c238458ef895248f197b
hqkk-cu7d-rar0 | 1 |  | J7 Rw7 | 1236751333 | 24-03-2017 11:44:04 CET | Safari Bosco | 00:17:24 | 2017 | Rwanda | Rulindo | Masoro | Shengampuri | Mutagata |  |  |  | 6740 |  | 124 | 124 | 0 | Yes | Piped Network with Pump |  | 1998 | Yes | mutagata.agasharu |  |  | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8102342497475674 | 30.064355956270422 | 1722.8 | 2b5slkpv | 1 | https://waterforpeople.s3.amazonaws.com/images/1c2b656f-fa7a-4c1e-9355-701a39fc088b.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | f7e847c57b44a58a519c8c171dcd2abd
s9he-2rj2-6ub0 | 1 |  | J7 Rw8 | 1221110904 | 16-03-2017 08:51:01 CET | Amani Desire | 00:10:22 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Musenge Network | 6074 |  | 118 | 27 | 91 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi | WFP |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber¦washout and Air release |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7455494136189171 | 29.9324870682441 | 2048.9 | 286t4fcs | 28 | https://waterforpeople.s3.amazonaws.com/images/5276bb83-f0f6-403a-8b70-2c1c3e2c67b8.jpg | 2014 | Does Not Function | Yes | 8 | 30 | water doesnt reach the distribution Reservoir R50m3 located at kibamba village due to the lack of sufficient pressure | No | water doesnt reach R50m3 at kibamba village which serves this water points | Does Not Function | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | 4fc9797087435826f26f28d3ad9b6ffb
48fm-vmr8-8p8 | 1 |  | J7 Rw15 | 1202310449 | 09-03-2017 22:47:43 CET | Mukakarangwa Assoumpta | 00:07:52 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Rwahi |  |  | Bitete-Rwahi network | 1316 |  | 161 | 25 | 136 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.8336417737979869 | 29.9434666882628 | 1815.5 | 2c8iday2 |  | Yes | 12 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 |  | 2013 | Normal | 600 | Yes | 6 | 1.8427360326225883 | 29.938932546871705 | 1676.5 | 2cnjkbst |  | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8645074531473085 | 29.923081457361146 | 1369 | 2dnjozmm | 1 | https://waterforpeople.s3.amazonaws.com/images/d24bccfd-4a6b-48d0-a928-6039a3f46492.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | d473da88294dfd4ed14756cd55988b55
y5p9-ac59-ch8b | 1 |  | J7 Rw15 | 1240030103 | 21-03-2017 14:12:35 CET | Mukakarangwa Assoumpta | 00:11:42 | 2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Mutoyi |  |  | Miyove-Kinihira | 10452 |  | 119 | 65 | 54 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6532784414522004 | 29.977963049171773 | 1823.1 | 23y7lsxv | 2 | https://waterforpeople.s3.amazonaws.com/images/64860ed6-2703-41cd-8db2-ae209316d0c1.jpg | 2015 | Normal | No |  |  |  | Yes |  | Poor |  | 6a6d9cbc61fc25bac895a96bd864c
6n7h-tpxc-rscv | 1 |  | J7 Rw23 | 1243880094 | 23-03-2017 06:26:37 CET | Rugirangoga Augustin | 00:42:39 | 2017 | Rwanda | Rulindo | Buyoga | Gitumba | Remera |  |  | Kiruruma | 8295 |  | 130 | 125 | 5 | Yes | Piped Network with Pump |  | 2014 | Yes | rutabo gitaba remera rusongati nyarubuye remera rugarama cyasuli munini | Governement (District, WASAC) and Water For People | there is no problem with this water tap | 1 | Groundwater (well, etc.) | 1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 15 | -1.6684773741137722 | 30.047381335897573 | 1775.8 | 24nckozd |  | 2014 | Normal | Yes | 5 | Pressure Break Tank |  | 2014 | Normal | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6762149460982616 | 30.03741597250593 | 2140.1 | 2505e74m | 2 | https://waterforpeople.s3.amazonaws.com/images/f83d44f7-c03f-4603-961d-cb4f61d2f1a1.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal |  | 75c6febb65f2089a6c5fe3ba54cfa5b
a2s1-uchp-59dm | 1 |  | J7 Rw15 | 1202310445 | 09-03-2017 22:22:02 CET | Mukakarangwa Assoumpta | 00:07:55 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyarunyinya |  |  | Bitete-Rwahi network | 1316 |  | 132 | 40 | 92 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.8336417737979869 | 29.94346668826428 | 1815.5 | 2c8iday2 |  | Yes | 12 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 |  | 2013 | Normal | 600 | Yes | 6 | 1.8427360326225883 | 29.938932546871705 | 1676.5 | 2cnjkbst |  | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8492865146969149 | 29.93531704552334 | 1594.3 | 2cydj909 | 1 | https://waterforpeople.s3.amazonaws.com/images/bf50f0f4-51f5-4cfa-bb7d-c53b456cd0b1.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | a950c84bf1fb4af6f054523229dec
dn1c-sjsg-ax6d | 1 |  | J7 Rw10 | 1218860579 | 14-03-2017 22:00:37 CET | Tuyisenge Vianney | 00:15:34 | 2017 | Rwanda | Rulindo | Tumba | Taba | Nyirambuga |  |  | Nyirambuga pumping station2/Nyirambuga source | 30604 |  | 128 | 128 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | GoR | The pumping station operates well.However some sources have deviated | 8 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg | https://waterforpeople.s3.amazonaws.com/images/43be52fe-4586-4c17-abb8-867b86fca8aa.jpg | No | 4 | Yes | 5 | https://waterforpeople.s3.amazonaws.com/images/d51e8a35-294f-4ce5-8f4a-e7ff06805e05.jpg | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 4 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/95727c96-19c6-41e0-abfa-51d8c75cab6a.jpg | 2012 | Normal | 50 | Yes | 1 | -1.7265891210669213 | 29.956077547195537 | 1930.8 | 27bgakko | https://waterforpeople.s3.amazonaws.com/images/15a9a781-04d6-4ced-813c-5696af324145.jpg | 2012 | Normal | No | [5 empty] | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/25332e1b-2aad-4616-9511-74617a428cec.jpg | 2012 | Normal | 4000 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/d400fce4-a3a9-43d9-abe1-41152b381703.jpg | 2012 | Normal | Yes |  | 2012 | Normal | Yes | https://waterforpeople.s3.amazonaws.com/images/8dae331d-1319-47ac-a885-dae513896ce0.jpg | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7263303990629582 | 29.955960403627042 | 1939.3 | 27b1eqg7 | 1 | https://waterforpeople.s3.amazonaws.com/images/915c4afc-2124-4971-b0d4-1f3e3537887d.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | The pumping house has started to get demolished,where walls have separated from foundations. | ab4168bbfba498bcdf23c9966a432d17
qh34-yt8n-2vdg | 1 |  | J7 Rw24 | 1226660338 | 16-03-2017 07:27:19 CET | Kabalisa Manzi Christella | 00:08:08 | 2017 | Rwanda | Rulindo | Burega | Karengeli | Kanunga |  |  | Rwamugaza | 14106 |  | 275 | 275 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3.5 | Yes | 2 |  |  | 2003 | Normal | 3.5 | Yes | 1 |  | 2003 | Normal | 8000 | Yes | 20 | -1.7416188180333267 | 29.988511802248155 | 1861.3 | 280b531p |  | 2003 | Normal | Yes | 16 |  | https://waterforpeople.s3.amazonaws.com/images/250f39d8-ba92-4bd5-abae-323f5d7fb621.jpg | 2003 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.716219720262854 | 30.036241027114823 | 1794.4 | 26uaw2ve | 1 | https://waterforpeople.s3.amazonaws.com/images/bd03ecb9-8d1c-4791-91d6-b72f270e994a.jpg | 2003 | Poor | No |  |  |  | No | System under rehabilitation | Poor | System Under rehabilitation | 2bf3e581199b3b90baecc9463adc9c3
tsa5-yemd-bbb | 1 |  | J7 Rw7 | 1243000050 | 23-03-2017 16:48:28 CET | Safari Bosco | 00:50:04 | 2017 | Rwanda | Rulindo | Murambi | Bubangu | Karwa |  |  | rwiseke | 9536 |  | 215 | 215 | 0 | Yes | Piped Network -- Gravity Only |  | 2001 | Yes | gashubi,rebero,taba,karwa | Governement (District, WASAC) and Water For People | The Water point is on the border of villages and thus many village come to get water from here | 3 | Spring | -1.8081127252820783 | 30.019302406005654 | 1889.4 | 2b2ado4h |  | Yes | 14 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2001 | Normal | 14 | Yes | 1 |  | 2001 | Normal | 12000 | Yes | 7 | -1.8083188633668612 | 30.018599981640595 | 1825.6 | 2b2mac7t |  | 2001 | Normal | No | [5 empty] | Yes | 1 |  | 2001 | Normal | 12000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8439756750644187 | 30.030872380627045 | 1736.7 | 2cple3is | 1 | https://waterforpeople.s3.amazonaws.com/images/75f7e9ed-109b-4744-a86a-4daeb44af53f.jpg | 2001 | Normal | No |  |  |  | Yes |  | Normal | This System has 12,000 meters | 65fef24d1befc5568c43f0e8c145cb1
fg4d-w014-wahk | 1 |  | J7 Rw23 | 1324620058 | 23-04-2017 14:43:55 CEST | Rugirangoga Augustin | 00:27:03 | 2017 | Rwanda | Rulindo | Buyoga | Gahororo | Gatare |  |  | Kiruruma | 8295 |  | 175 | 100 | 75 | Yes | Piped Network with Pump |  | 2017 | Yes | gatare gatenderi shagasha rutabo kimagali sayo | Governement (District, WASAC) and Water For People | This is a new Water Point it has not yest started functioning | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 1 |  | 2014 | Does Not Function | 9000 | No | [8 empty] | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.726346051352908 | 30.07178602988422 | 1530.8 | 27b206y5 | 2 | https://waterforpeople.s3.amazonaws.com/images/17cb9a41-0f01-44d9-9700-cd101fbef01a.jpg | 2016 | Does Not Function | No |  |  |  | No | Water point is new | Does Not Function | Water point is new and under construction | 6a96ddbe31ab051ad2aa38ee2935dbd
u85e-p08y-gk1b | 1 |  | J7 Rw15 | 1200180404 | 09-03-2017 22:39:44 CET | Mukakarangwa Assoumpta | 00:07:15 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Rwahi |  |  | Bitete-Rwahi network | 1316 |  | 161 | 40 | 121 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.8336417737979869 | 29.94346668826428 | 1815.5 | 2c8iday2 |  | Yes | 12 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 |  | 2013 | Normal | 600 | Yes | 6 | 1.8427360326225883 | 29.938932546871705 | 1676.5 | 2cnjkbst |  | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8622505444193191 | 29.92220635387713 | 1396 | 2djtqgie | 1 | https://waterforpeople.s3.amazonaws.com/images/61a8809f-13f3-41f5-b544-999a9d7466c5.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 968a3da17e5e38dcaf5729de2e76a93
f5h8-rxkb-fyx7 | 1 |  | J7 Rw10 | 1226490423 | 13-03-2017 22:19:44 CET | Tuyisenge Vianney | 00:06:17 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Karambo |  |  | Karambo water point/Buramira gravity | 1255 |  | 104 | 104 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | GoR | The water point operates normally | 2 | Spring | -1.6776639816373493 | 29.911131429480132 | 2061.4 | 252jq0vb |  | Yes | 30 | No | [5 empty] | 30 | No | [5 empty] | Yes | 1 | -1.673163892190922 | 29.91974469213936 | 1872.4 | 24v3sypp | https://waterforpeople.s3.amazonaws.com/images/2549492e-fc80-4cbe-9bbf-9afd08725f71.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6728347231683887 | 29.920145766956722 | 1851.3 | 24uk5nr5 | 1 | https://waterforpeople.s3.amazonaws.com/images/10773036-0109-47eb-92df-abfb5feea626.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The water point operates well | 95931273222ed645247c31ed44f831a
102m-d007-13kd | 1 |  | J7 Rw24 | 1221260147 | 16-03-2017 06:23:31 CET | Kabalisa Manzi Christella | 00:06:22 | 2017 | Rwanda | Rulindo | Burega | Taba | Lyinzovu |  |  | Rwamugaza | 14106 |  | 505 | 505 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | no problem | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7320424482657897 | 30.01793589927449 | 2077.6 | 27khd9cj | 1 | https://waterforpeople.s3.amazonaws.com/images/58741014-be1c-4e3d-85dc-7d8a401ef060.jpg | 2012 | Normal | No |  |  |  | Yes |  | Poor | no problem | 301718feb850533180a6164c7bdff343
9fb7-dgyx-2m2f | 1 |  | J7 Rw23 | 1326420069 | 23-04-2017 14:41:30 CEST | Rugirangoga Augustin | 00:11:44 | 2017 | Rwanda | Rulindo | Buyoga | Mwumba | Nyarubuye |  |  | kiruruma | 8295 |  | 173 | 120 | 53 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | nyarubuye nyamwiza gatenderi gatare kimagari |  |  | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 1 |  | 2014 | Normal | 6700 | Yes | 11 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2014 | Normal | No | [5 empty] | Yes | 3 |  | 2016 | Normal | 6700 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6769201508765412 | 30.008591808403835 | 1935.4 | 251bnyut | 2 | https://waterforpeople.s3.amazonaws.com/images/8bfe540f-b007-4def-9984-a0abbc41818d.jpg | 2017 | Does Not Function | No |  |  |  | Yes |  | Poor |  | 2fe340b7a2cff26989467bbb0d7e2bd
ux26-cnd2-x6sn | 1 |  | J7 Rw15 | 1217800202 | 12-03-2017 12:52:28 CET | Mukakarangwa Assoumpta | 00:06:28 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Mukumba |  |  | Muvumu- Taba |  |  | 92 | 20 | 72 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.8242130164596562 | 29.931083430301516 | 1700.7 | 2bswxje6 |  | Yes | 25 | No | [5 empty] | 25 | Yes | 1 |  | 2013 | Normal | 800 | Yes | 3 | 1.828985219687556 | 29.926634523104315 |  | 2c0sxawy |  | 2013 | Poor | Yes | 9 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 7500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8356641053431544 | 29.930605353970286 | 1615.7 | 2cbumv1m | 1 | https://waterforpeople.s3.amazonaws.com/images/abaa3429-5d5c-4aa1-8c54-1859091b6c40.jpg | 2013 | Normal | Yes | 1 | 3 | Those rehabilitating Rushinya source had strayed it | Yes |  | Poor |  | 3148d96dbcab92e0f136d97747f6
f2rg-7w2r-c160 | 1 |  | J7 Rw7 | 1451470092 | 04-06-2017 13:22:46 CEST | Rugirangoga Augustin | 00:17:13 | 2017 | Rwanda | Rulindo | Kisaro | Gitatsa | Ruberano |  |  | gahama | 10234 |  | 132 | 100 | 32 | Yes | Piped Network with Pump |  | 2017 | Yes | ruberano gatete mugomero gishinge nyakarekare kibingwe |  |  | 2 | Spring | -1.6675834297797398 | 30.0428712210569 | 1965.7 | 24lvl43w |  | Yes | 65 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 65 | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 | Pressure Break Tank¦Distribution Chamber¦washout, Air release |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6582302556645567 | 30.04321174137796 | 1890.3 | 246ewths | 1 | https://waterforpeople.s3.amazonaws.com/images/d11654ed-0acf-4b30-9b9d-13f3de0fc618.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | uyu muyoboro (ivomo) uracyari mushya | 50c378fcc99c34e5725554217a9d9fd5
w961-4ua3-mkww | 1 |  | J7 Rw15 | 1206900711 | 09-03-2017 21:22:06 CET | Mukakarangwa Assoumpta | 00:07:57 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Gishyita |  |  | Bitete-Rwahi network | 1316 |  | 205 | 120 | 85 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.8336417737979869 | 29.94346668826428 | 1815.5 | 2c8iday2 |  | Yes | 12 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 |  | 2013 | Normal | 600 | Yes | 6 | 1.8427360326225883 | 29.938932546871705 | 1676.5 | 2cnjkbst |  | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8660880311490347 | 29.931331776784717 | 1376.9 | 2dq5rh9t | 1 | https://waterforpeople.s3.amazonaws.com/images/ab85e932-d488-4863-98d1-960d0d8308b5.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 7b1b9b83af1f674ecea681cdb6ae49
dfyv-9g0d-7v6e | 1 |  | J7 Rw8 | 1240030365 | 23-03-2017 12:12:53 CET | Amani Desire | 00:29:26 | 2017 | Rwanda | Rulindo | Murambi | Mvuzo | Kabuga |  |  | Gakoma network | 7108 |  | 199 | 101 | 98 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | Nyagisozi |  |  | 2 | Spring | -1.820504948163801 | 30.02259538436087 | 1687.1 | 2bms1qo1 | https://waterforpeople.s3.amazonaws.com/images/6b8ea47d-2903-4696-9e99-df78343c7984.jpg | Yes | 9 | No | [5 empty] | 9 | No | [5 empty] | Yes | 2 | -1.8204311991738096 | 30.02203801775231 | 1655.6 | 2bmnvpfg | https://waterforpeople.s3.amazonaws.com/images/20f0d6c1-af2f-4cc7-a26d-f72564b3f889.jpg | 2004 | Normal | No | [5 empty] | Yes | 1 |  | 2004 | Poor | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8203034841158667 | 30.02161124634951 | 1701.9 | 2bmg52k8 | 2 | https://waterforpeople.s3.amazonaws.com/images/22a0d2f0-662e-4e31-8e07-6fd6ad69782c.jpg | 2004 | Does Not Function | Yes | 6 | 30 | the water is damaged and destroyed | No | water point is distroyed | Does Not Function | 1.the system has 6 water points with 2 located in Rulindo district and other in in Gasabo district in Jabana sector 2. in Rulindo only one water point is functinal the other is distroyed | 8630c3b31f6a69635ad3296694f19ff
842f-k4sv-ht1x | 1 |  | J7 Rw10 | 1307040050 | 18-04-2017 06:48:14 CEST | Tuyisenge Vianney | 00:05:40 | 2017 | Rwanda | Rulindo | Tumba | Gahabwa | Rushaki |  |  | Rushaki water point at Habimana/Nyirambuga pumping system | 30604 |  | 152 | 152 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | The water point is operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/7154f1c6-271e-4b93-826d-fb2a64950fe1.jpg | 2017 | Normal | 2017 | Yes | 1 | -1.7156342103980782 | 29.971602441031553 | 1955.3 | 26tccxac | https://waterforpeople.s3.amazonaws.com/images/f01a99b1-8d36-449d-9d72-1dd715a2b3ce.jpg | 2017 | Normal | No | [5 empty] | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/5d6caa38-7a6b-4eb8-8ecb-df91998990f6.jpg | 2017 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7157215417680711 | 29.971554258738117 | 1938.4 | 26thptqb | 2 | https://waterforpeople.s3.amazonaws.com/images/42f3e22a-76e9-43aa-8fe7-7be15046b944.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | The water point is operational | f9e6c97b128dd9adf0e176aa4d8e38e9
843u-5hrp-93hj | 1 |  | J7 Rw26 | 1198580464 | 07-03-2017 12:02:41 CET | Byukusenge Elie | 00:12:14 | 2017 | Rwanda | Rulindo | Cyungo | Marembo | Nganzo |  |  | Mugomero Murambo | 3456 |  | 150 | 132 | 18 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | Kidomo, Gahinga, Nganzo,Rusayu, Buyaga and Murambo | Governement (District, WASAC) and Water For People | The source of this network is located in Burera District and this2 network srves three villages in Burera and it jas eight water taps ,starting chamber and one reservoir in Ruhunde Sector in2 Burera District | 1 | Spring | -1.5777496463341437 | 29.93714072556937 | 2147.8 | 20haqsiz |  | Yes | 120 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 120 | Yes | 2 |  | 2015 | Normal | 10000 | Yes | 10 | -1.5961706844323926 | 29.91257085345822 | 2085.4 | 21bs0o8l |  | 2015 | Normal | Yes | 3 | Distribution Chamber |  | 2015 | Normal | Yes | 2 |  | 2015 | Normal | 10000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6157293002612292 | 29.911836193188623 | 1959.2 | 2283z3vy | 1 | https://waterforpeople.s3.amazonaws.com/images/0074129e-6e35-4cab-8eb9-a7a05b304a4a.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is not2 use by the community as the Population use the protected spring which is located near the network | 755afb4fd3bb1fce994b147ddd62d7e
2dby-0mwx-quqc | 1 |  | J7 Rw19 | 1239720983 | 23-03-2017 08:16:55 CET | Kayinamura Innocent | 00:11:25 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Kigarama |  |  | Mutagata motorised network | 26296 |  | 169 | 65 | 104 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7865267494573016 | 30.042179863090567 | 1969.2 | 2a2kyt8l | 64 | https://waterforpeople.s3.amazonaws.com/images/d2cb067d-7dd6-41de-ae68-15e4b22273e5.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | e9fc7f60951d17bf2ec5ad6a3616e5
5g9a-k0qs-hsun | 1 |  | J7 Rw19 | 1243750295 | 23-03-2017 18:37:57 CET | Kayinamura Innocent | 00:19:45 | 2017 | Rwanda | Rulindo | Masoro | Kabuga | Kanunga |  |  | Mutagata motorised network | 26296 |  | 143 | 75 | 68 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.801852228745035 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.783622470725573 | 30.05264006381323 | 1831.8 | 29xsb3vy | 64 | https://waterforpeople.s3.amazonaws.com/images/8bb79025-a6bd-4022-bdfb-f3e1edad0c45.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | e2234747123878aa6fef76b419531ff7
3h3r-ed03-st7n | 1 |  | J7 Rw15 | 1213150190 | 12-03-2017 10:07:32 CET | Mukakarangwa Assoumpta | 00:43:01 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kirurumo |  |  | Bitete-Muvumu | 1316 |  | 80 | 5 | 75 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 3 | Spring | -1.8337482672601935 | 29.943433443706404 | 1749 | 2c8obmzu | https://waterforpeople.s3.amazonaws.com/images/febcc48b-20cd-43bc-b51e-3184f033cd5a.jpg | Yes | 11 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/6fcaa858-1792-4b6b-8f89-c5db96e20f16.jpg | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/d005d365-afd7-43e6-ab07-45151574bc63.jpg | 2013 | Poor | 1000 | Yes | 4 | -1.8368127107947887 | 29.93457412501046 | 1635 | 2cdr3pn5 | https://waterforpeople.s3.amazonaws.com/images/b920b230-6c17-4835-8241-55f8b7aa87b2.jpg | 2013 | Normal | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout | https://waterforpeople.s3.amazonaws.com/images/1ac8acb3-a4c1-435c-8eb3-95557ae25aa1.jpg | 2013 | Normal | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/e37d73f5-f8e0-44e1-aaf7-571590c1dbf6.jpg | 2013 | Normal | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8339316130187737 | 29.943060264247208 | 1673.8 | 2c8zmvhi | 1 | https://waterforpeople.s3.amazonaws.com/images/c443809e-627c-446f-96b6-4f4211c30335.jpg | 2013 | Poor | No |  |  |  | Yes |  | Normal | -This Bitete-Muvumu network was rehabilitated in 2013 by Water for people Rwanda,it has 3 sources which are normal and 7 water points in which one which is located at the sources is poor it has not water stand and 2 does not function and it has 4 resrvoirs which funtion normal and it has 6 other concrete structures in which the break pressure has leakage, also it's conduction line has leakege. | 55e7d7f8e8df12bfbf7d2dd391a441cf
ayfc-6by3-ks31 | 1 |  | J7 Rw26 | 1230240489 | 21-03-2017 14:11:28 CET | Byukusenge Elie | 00:32:25 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Kamiyove |  |  | Kabonanyoni | 7894 |  | 40 | 30 | 10 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 3 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6293669960636115 | 29.961366981722335 | 1894 | 22uo2del | 31 | https://waterforpeople.s3.amazonaws.com/images/f8093dee-4328-4c76-a2c7-7ebdc32e7e46.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is located to the source Kibare and the community use it as they do not pay for water. | 8c86fb02bd95afb1ac0a18bf5fab928
cq4b-rm8w-p46c | 1 |  | J7 Rw10 | 1232820287 | 02-01-2015 23:48:15 CET | Tuyisenge Vianney | 00:06:03 | 2017 | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point at Gisha center/Nyirambuga pumping | 30604 |  | 133 | 133 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | GoR | The water point at Gisha center operates well though one water tap valve is leaking.Its better to refix it correctly | 11 | Spring | -1.726524345182751 | 29.956089955799534 | 1943.2 | 27bcpyy0 |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7436788330390818 | 29.965733633527833 | 2042.3 | 283psdhl | 2 | https://waterforpeople.s3.amazonaws.com/images/519600ba-0420-474a-922c-e8bf482280e9.jpg | 2015 | Poor | No |  |  |  | Yes |  | Normal | The water point at Gisha center operates well though one water tap valve is leaking.Its better to refix it correctly | c978bae4a44be916348adaa2491c319
3wg0-d3x4-nu8m | 1 |  | J7 Rw19 | 1435370077 | 04-06-2017 15:53:09 CEST | Kayinamura Innocent | 00:18:17 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 6074 |  | 135 | 31 | 104 | Yes | Piped Network -- Gravity Only |  | 2014 | No |  | Water for People, WASAC and Rulindo District |  | 1 | Spring | -1.768794219980039 | 29.93859037216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.556828330459043 | 2206.4 | 29s1pl5c |  | 2014 | Normal | Yes | 8 | Washout, Air release chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7722665478271253 | 29.94576064577904 | 2004.1 | 29ezynup | 28 | https://waterforpeople.s3.amazonaws.com/images/c3a4b26e-e52e-46ec-b103-32e8d6888eab.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal |  | c266e8af943b7986b05f77961997ad46
9y20-4s5k-34fr | 1 |  | J7 Rw10 | 1309350234 | 20-04-2017 11:20:02 CEST | Tuyisenge Vianney | 00:06:35 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point chez Hategekimana/Nyirambuga pumping | 30604 |  | 169 | 169 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | Operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.685774365199782 | 29.9388418722866 | 2014.5 | 25fykkos | 2 | https://waterforpeople.s3.amazonaws.com/images/6e9dc020-d97c-4dfb-a167-b842fa5f5e50.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | operational | bcde1e1d44ffd746e45e6c1d8a95efa
pv3f-mavx-3pxv | 1 |  | J7 Rw23 | 1218860314 | 15-03-2017 07:54:08 CET | Rugirangoga Augustin | 00:34:31 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutembe | 1012 |  | 229 | 200 | 29 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | this network is not working properly | 1 | Spring | -1.6453375971221083 | 29.88944187456076 | 1765.4 | 23l2vlxq | https://waterforpeople.s3.amazonaws.com/images/d8998167-20cc-4729-a11c-4462d82aa83c.jpg | No | 75 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/8bcb3ca4-20cf-4622-9219-ae39f49ba11a.jpg | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 75 | Yes | 1 |  | 2016 | Normal | 2700 | Yes | 2 | -1.6508336759560134 | 29.884394940764913 | 1503.1 | 23u6c0m3 | https://waterforpeople.s3.amazonaws.com/images/f87da592-b5f2-4e40-956a-2f5034795376.jpg | 2016 | Normal | No | [5 empty] | Yes | 1 |  | 2016 | Normal | 2700 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6491376822935664 | 29.885958356298563 | 1810.6 | 23rd4bsb | 2 |  | 2016 | Poor | No |  |  |  | No | pipes were damaged while road were being constructed | Poor | the two water taps of this network .one works, the other doesn't work | d4585f61caf44d5401ce1cdecd29f17
syxu-b4ss-rf2p | 1 |  | J7 Rw8 | 1220250159 | 16-03-2017 08:47:40 CET | Amani Desire | 02:11:17 | 2017 | Rwanda | Rulindo | Mbogo | Bukro | Buhira |  |  | Musenge Network | 6074 |  | 100 | 48 | 52 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt | https://waterforpeople.s3.amazonaws.com/images/68af26a6-6f1c-4f36-a1da-7d60d7fad320.jpg | Yes | 4.44 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/627d58b6-8faa-48d7-815f-37538a7ddace.jpg | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/045d692b-11b4-4b57-ab99-937c2b49ef10.jpg | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g | https://waterforpeople.s3.amazonaws.com/images/76de2503-be05-4081-bd6c-8714cef37988.jpg | 2014 | Normal | Yes | 8 | Distribution Chamber¦washout and Air release | https://waterforpeople.s3.amazonaws.com/images/40e2075c-da9c-4250-991c-350ef07e193a.jpg | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/85c77334-bbd0-427f-9a3d-d07653d74191.jpg | 2014 | Poor | Yes | https://waterforpeople.s3.amazonaws.com/images/bee5d83c-3249-4dfd-a6d3-045422a3b239.jpg | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7688643144852982 | 29.93843280797594 | 1813.8 | 299dja48 | 28 | https://waterforpeople.s3.amazonaws.com/images/e08b081a-b22a-447d-b576-964d11a9e408.jpg | 2014 | Normal | No |  |  |  | Yes |  | Poor | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | eb2915332c97d42e2a70c71668887ab2
5due-936f-bv0a | 1 |  | J7 Rw26 | 1242130146 | 03-01-2015 04:54:05 CET | Byukusenge Elie | 00:08:57 | 2017 | Rwanda | Rulindo | Rukozo | Mberuka | Mataba |  |  | Kabonanyoni | 7894 |  | 70 | 65 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare, Kabera,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe, Kabyayi, Kabingo, Kamiyove, Murwa, Nyenyeri, Rukingu and Kivomo | Governement (District, WASAC) and Water For People | This is the New pumping system which serves the community located at the uphill, it has 5 sources, one source which is located in Miyove sector, Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro,This network has one reservoir which is not functioning, This network serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6172498103431439 | 29.953608031247878 | 2051.1 | 22amh05s | 31 | https://waterforpeople.s3.amazonaws.com/images/6b3c84dc-dde7-4a2a-acfe-39acbf9d6cb9.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | 54215828f7b06823754a60beb36df3d
8a2y-sbu9-tj8j | 1 |  | J7 Rw15 | 1205071046 | 09-03-2017 19:32:33 CET | Mukakarangwa Assoumpta | 00:06:35 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyarusange |  |  | Gisoro- Nyundo network | 2297 |  | 97 | 55 | 42 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.840451151026817 | 29.948165560771624 | 1795.9 | 2cjrthy1 |  | Yes | 13 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 13 | Yes | 1 |  | 2013 | Normal | 30 | Yes | 6 | 1.8406374522240199 | 29.94836287627501 | 1783.7 | 2ck2jau3 |  | 2013 | Poor | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 7000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8588009277719366 | 29.94615320530807 | 1560 | 2de4bwzp | 1 | https://waterforpeople.s3.amazonaws.com/images/50a2092b-2348-4d43-862a-f07d9cd3289c.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | b1d85a9620646eb94dedc86a9daca211
aaju-fhk6-jkuy | 1 |  | J7 Rw19 | 1202042043 | 17-03-2017 05:21:46 CET | Kayinamura Innocent | 00:18:13 | 2017 | Rwanda | Rulindo | Ngoma | Kabuga | Kiruli |  |  | Musenge network | 6074 |  | 139 | 139 | 0 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma, Karehe, Rutonde, Gitaba, Kiruri, Buhera, Ruhanya, Kibamba and Karibdi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.93859037216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Washout and Air release chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.80257787395027 | 29.971620635766588 | 2124.6 | 2at4jimc | 28 | https://waterforpeople.s3.amazonaws.com/images/0df47e94-8993-42a4-9f76-57f5f435ccd1.jpg | 2017 | Does Not Function | No |  |  |  | Yes |  | Poor | 1.the system has two Pumps but one is damaged and is not working, only one pump is used to pump water 2. Eleven (11) water points served by the distribution reservoir R 50m3 located at Kibamba village do not have water today because water don't reach this reservoir, there is not water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed 2016 5. one water point doesn't Function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction with one | 30b2b344e11503a35bd413ccbdc57a
sm3r-xcsk-nb1e | 1 |  | J7 Rw26 | 1205690098 | 02-01-2015 05:51:02 CET | Byukusenge Elie | 00:10:53 | 2017 | Rwanda | Rulindo | Cyungo | Burehe | Sove |  |  | Nyamagana | 20456 |  | 80 | 50 | 30 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | Well | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6243766666352475 | 29.938047084796594 | 1848.7 | 22mez2d0 | 29 | https://waterforpeople.s3.amazonaws.com/images/f1d1b784-dd96-43e7-a3b6-1b8c07f5a964.jpg | 2011 | Normal | Yes | 10 | 35 | The distribution reservoir does not supply water in this transmission line towards Burehe Cell | Yes |  | Poor | water tap located in near sector Cyungo has water but not regularly | d33b17d676142f8f291e9637ffc58e
ggbg-fp3p-1q1k | 1 |  | J7 Rw24 | 1254700126 | 28-03-2017 10:11:47 CEST | Kabalisa Manzi Christella | 00:05:14 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Cyamutara |  |  | Rwamugaza network | 14106 |  | 243 | 243 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 1 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7826213842918088 | 30.127690457657046 | 1511.1 | 29w4rrz0 | 1 | https://waterforpeople.s3.amazonaws.com/images/3e62d2f3-c666-40dc-b00a-2c401fcdd80c.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal |  | bcef88b3989c9adb0543c064e81f9a
647u-hehv-r3ep | 1 |  | J7 Rw24 | 1246240154 | 28-03-2017 08:19:15 CEST | Kabalisa Manzi Christella | 00:08:41 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Kivubwe |  |  | Rwamugaza network | 14106 |  | 173 | 173 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.764769580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  | https://waterforpeople.s3.amazonaws.com/images/aea96032-dff5-4106-8936-d9eb0fa85831.jpg | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.768106598265787 | 30.083734208337052 | 1694.5 | 2984ad9h | 1 | https://waterforpeople.s3.amazonaws.com/images/a4fe09dd-d576-436f-a8c6-432a779fbd65.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | 17d4a6d89aae70c4542cd7b3451df7
trtx-u1y9-u33k | 1 |  | J7 Rw8 | 1215600735 | 10-03-2017 10:18:45 CET | Amani Desire | 00:27:45 | 2017 | Rwanda | Rulindo | Ngoma | Karambo | Kagwa |  |  | Kabarore- Ngoma- Nyabuko network | 8284 |  | 123 | 41 | 82 | Yes | Piped Network with Pump |  | 2014 | Yes | nyabuko,kagwa, kiruli, busizi,ngaru,kirungu,kiboho,kigina | Governement (District, WASAC) and Water For People |  | 4 | Spring | -1.8123357076877171 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦collection chamber | 2014 | Poor | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.808716485895084 | 29.973362007273437 | 2001 | 2b3a3o2d |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8388196111045352 | 29.98581875431757 | 1746 | 2ch26f0y | 13 | https://waterforpeople.s3.amazonaws.com/images/6970c9bc-1031-4409-bbed-3e22744dc493.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | -the network has 17 water points - water points are in good operational conditions except the water point at the source that is damaged -4 water points don't have water today - the pipes are in good operational conditions - The pump is not working properly as it was expected during Design, Today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy -the transformer at the pumping station doesnt offer the required energy for the pump - the anti hammers of pump are not functioning because of bad installation of pumping house -The system has two pumps with four units with two units pumping in one direction towards Nyabuko and other two in an other direction towards ngoma sector office -The suction tank is in bad physical conditions | 171b0a62b716943c0999ac918dd5d26
q6a6-q91m-cpjr | 1 |  | J7 Rw10 | 1307430109 | 16-04-2017 23:05:46 CEST | Tuyisenge Vianney | 00:04:22 | 2017 | Rwanda | Rulindo | Buyoga | Karama | Kajeneni |  |  | Karambo center water point/Nyirambuga pumping | 30604 |  | 175 | 175 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Operational and functional | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7002700009302065 | 29.974665265626502 | 1946.4 | 263xv44i | 2 | https://waterforpeople.s3.amazonaws.com/images/53d82f1d-a8da-4d8b-80a6-fcac107142d1.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Operational and functional | 80c51397b02ff2e4b9439cd7b6d6ff2
mbj5-253r-285s | 1 |  | J7 Rw24 | 1199071678 | 16-03-2017 08:29:07 CET | Kabalisa Manzi Christella | 00:08:41 | 2017 | Rwanda | Rulindo | Murambi | Mvuzo | Ntyaba |  |  | 0 |  |  | 680 | 680 | 0 | Yes | Piped Network with Pump |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8024532750946713 | 30.042616473975034 | 1748.3 | 2asxebwq |  | Yes | 3 | Yes | 1 |  |  | 2016 | Normal | 3 | Yes | 1 |  | 2016 | Normal | 35000 | Yes | 6 | -1.7869702223247468 | 30.02180157166659 | 2041.1 | 2a3brbay | https://waterforpeople.s3.amazonaws.com/images/52953356-c9a4-4b4e-9a9b-c35b32da623e.jpg | 2016 | Normal | Yes | 30 |  | https://waterforpeople.s3.amazonaws.com/images/bf680757-2a58-4688-a933-aa9546981b30.jpg | 2016 | Normal | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/de28d40c-946d-4ce7-a490-3c4bd145c842.jpg | 2016 | Normal | 35000 | Yes | 3 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7781040434691524 | 30.02810226597052 | 2014.9 | 29onntrt | 1 | https://waterforpeople.s3.amazonaws.com/images/aa899bd9-3d59-44b7-97ac-6540e429f26d.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | e836acd32db341e76e89bff271f244d
bdu5-a8ms-cydw | 1 |  | J7 Rw24 | 1247160180 | 28-03-2017 10:51:29 CEST | Kabalisa Manzi Christella | 00:10:50 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyarurama |  |  | Rwamugaza network | 14106 |  | 168 | 168 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government | This Systems Functions well | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.071178934264683 | 1758 | 292lfl47 | https://waterforpeople.s3.amazonaws.com/images/48c21802-9ec7-4849-8888-cac6733bd961.jpg | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7526463184043184 | 30.075487232827914 | 1707.5 | 28iju7yq | 1 | https://waterforpeople.s3.amazonaws.com/images/a820b3cc-1cf6-4ba6-b28e-922fcbb5b43f.jpg | 2003 | Normal | No |  |  |  | No | Pipes Broken | Poor |  | 1167e283a95eba7f16eeedb8715439
63st-fmwa-qsuw | 1 |  | J7 Rw26 | 1242660266 | 03-01-2015 04:52:13 CET | Byukusenge Elie | 00:10:24 | 2017 | Rwanda | Rulindo | Rukozo | Mberuka | Kabera |  |  | Kabonanyoni | 7894 |  | 138 | 130 | 8 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare, Kabera,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe, Kabyayi, Kabingo, Kamiyove, Murwa, Nyenyeri, Rukingu and Kivomo | Governement (District, WASAC) and Water For People | This is the New pumping system which serves the community located at the uphill, it has 5 sources, one source which is located in Miyove sector, Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro,This network has one reservoir which is not functioning, This network serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Poor | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.638970740989166 | 29.951573940012274 | 2088.2 | 23ak7xob | 31 | https://waterforpeople.s3.amazonaws.com/images/f53c7422-d5c2-4fed-8e58-e3e80abbbf56.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is in good condition | 4f49aa30765e2f3daf7e9cb59b5e2847
mjhq-57s0-3pfj | 1 |  | J7 Rw7 | 1243090076 | 24-03-2017 09:39:01 CET | Safari Bosco | 00:21:06 | 2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Rusenyi |  |  | marenge | 5544 |  | 156 | 156 | 0 | Yes | Piped Network with Pump |  | 2016 | Yes | kabeza,rusenyi | Governement (District, WASAC) and Water For People | Water points is functioning well | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228065710007637 | 30.055376173807932 | 1827.2 | 2bqkzg21 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8352553581387243 | 30.053091431099006 | 1713.3 | 2cb6846q | 2 | https://waterforpeople.s3.amazonaws.com/images/2a8d2730-8d69-4a99-a5af-8fc737002250.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | b93d1bd5ebe94af8223139a83ad59df
n6rt-a032-gxj7 | 1 |  | J7 Rw19 | 1313020090 | 20-04-2017 14:46:59 CEST | Kayinamura Innocent | 00:15:02 | 2017 | Rwanda | Rulindo | Mbogo | Mushali | Bukongi |  |  | Gitabage network |  |  | 168 | 72 | 96 | Yes | Piped Network -- Gravity Only |  | 2008 | No |  | Catholic Church |  | 1 | Spring | -1.7894191074184786 | 29.98061378695303 | 1922.2 | 2a7d12la |  | Yes | 40 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2008 | Normal | 40 | Yes | 1 |  | 2008 | Normal | 700 | Yes | 2 | -1.7927177501595748 | 29.982999206837842 | 1821.5 | 2acti48l |  | 2008 | Normal | No | [5 empty] | Yes | 1 |  | 2008 | Normal | 500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7927886292598962 | 29.98311651714611 | 1830.8 | 2acxo5h3 | 3 | https://waterforpeople.s3.amazonaws.com/images/1ea6b95e-c705-4b10-beba-5b76adb42193.jpg | 2008 | Poor | No |  |  |  | Yes |  | Normal | This network has 3 water points It serves 2 villages and one School | eb15bdc01f1d948cb2f725547bccd42
hsp7-692b-qrh8 | 1 |  | J7 Rw10 | 1236870706 | 22-03-2017 14:33:40 CET | Tuyisenge Vianney | 00:02:57 | 2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point/AEP Kigarama gravity | 2621 |  | 243 | 243 | 0 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | This is one of water points located in grouped area Kigarama village.It is normally operational and functional | 1 | Spring | -1.7875070118422336 | 29.92431620181639 | 2051.7 | 2a47b9m3 |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.77600307446452 | 29.932769025351394 | 1815 | 29l6mrzz | 2 | https://waterforpeople.s3.amazonaws.com/images/e8f7bdd1-45c9-4f78-b04b-9a8bcb8444ba.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | This is one of water points located in grouped area Kigarama village.It is normally operational and functional | d37429d8cb4d908a211affe626441e14
a04f-u21s-rv74 | 1 |  | J7 Rw24 | 1199071676 | 16-03-2017 08:18:40 CET | Kabalisa Manzi Christella | 00:19:44 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Ruri |  |  | 0 | 26296 |  | 945 | 945 | 0 | Yes | Piped Network with Pump |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8024532750946713 | 30.042616473975034 | 1748.3 | 2asxebwq | https://waterforpeople.s3.amazonaws.com/images/3a7dcf69-df0e-460e-b78b-d9c3fc0590f8.jpg | Yes | 3 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/0322cdcc-52ad-4a38-b885-427481c319cb.jpg | collection chamber | 2016 | Normal | 3 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/82beef5e-5347-4b20-8404-710c2b8651ef.jpg | 2016 | Normal | 35000 | Yes | 45 | -1.8024154053071508 | 30.042612013573287 | 1723.2 | 2asv0lhm |  | 2016 | Normal | Yes | 38 |  |  | 2016 | Normal | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/dcb0d169-7f98-43f3-adad-34e0152ad93f.jpg | 2016 | Normal | 35000 | Yes | 3 | https://waterforpeople.s3.amazonaws.com/images/56680404-88c8-47dc-8409-dcf1e03fb8a4.jpg | 2016 | Normal | Yes | https://waterforpeople.s3.amazonaws.com/images/9f6f7f4a-4a56-4900-9fc3-f9c6bf3daa07.jpg | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8023448061909204 | 30.04256916613823 | 1701 | 2asquk95 | 1 | https://waterforpeople.s3.amazonaws.com/images/8ee0f6ca-4290-458b-bb1a-2c168c532284.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 6d744a51d0da97d90d84c4965a7af6
arnn-uvtq-fku8 | 1 |  | J7 Rw24 | 1251570312 | 28-03-2017 10:00:03 CEST | Kabalisa Manzi Christella | 00:06:53 | 2017 | Rwanda | Rulindo | Kisaro | Mubuga | Rutabo |  |  | Gahama Kisaro network | 10234 |  | 148 | 148 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6671501074688961 | 30.041830412153367 | 1945.4 | 24l5zh36 |  | Yes | 3 | Yes | 1 |  |  | 2012 | Normal | 3 | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 |  |  | 2012 | Normal | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Poor | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6687884527213004 | 30.041131785842182 | 2032.9 | 24nv14or | 1 | https://waterforpeople.s3.amazonaws.com/images/c46d090b-4ba0-4ba8-8a22-3772c56dba85.jpg | 2012 | Poor | No |  |  |  | No | System under rehabilitation | Poor |  | e5a0ec3d28ac3cfa77be28fa862e36a
7k8x-h940-bg7n | 1 |  | J7 Rw19 | 1215030253 | 13-03-2017 06:51:28 CET | Kayinamura Innocent | 00:39:30 | 2017 | Rwanda | Rulindo | Ngoma | Munyarwanda | Ngaru |  |  | Kabarore-Ngoma-Nyabuko network | 8284 |  | 106 | 50 | 56 | Yes | Piped Network with Pump |  | 2014 | Yes | Nyabuko, kagwa, Kiruri, Busizi, Ngaru, Kirungu, Kiboha and Kigina | Governement (District, WASAC) and Water For People | The network has 17 water points and it serves 8 villages | 4 | Spring | -1.8123357076877171 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦Collection Chamber | 2014 | Normal | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.8118879629206273 | 30.003478805087482 | 2031 | 2b8iu32a |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 4 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8293034311648553 | 30.006477126101984 | 1927.8 | 2c1bz6w0 | 17 | https://waterforpeople.s3.amazonaws.com/images/5bc64c19-a067-4697-9d44-1baeebc1f8f9.jpg | 2014 | Poor | Yes | 1 | 10 | it was due to the road construction | Yes |  | Normal | - the network has 17 water points - water points are in good operation conditions except the water point at the source that is damaged - 4 water points don't have water today - the pipe are in good operations - the pump is not working properly as it was expected during, today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy - the transformer at the pumping station doesn't offer the required energy for the pump - the anti-hammers of pumps are not functioning because of bad installation of pumping house - the system has 4 pumps units with two units pumping in one direction towards Nyabuko, towards Ngoma sector office - the suction tank is in bad physical condition | b7f4e8a0a433b74b3837c5d0ff75ee20
jge8-ccp4-rf7k | 1 |  | J7 Rw10 | 1205750588 | 10-03-2017 14:27:37 CET | Tuyisenge Vianney | 00:07:54 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Gitwa |  |  | Water point at Gasiza Health Post/Tare-Rusiga pumping | 9577 |  | 134 | 134 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Gasiza health post water point is operating normally | 10 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 4000 | Yes | 1 | -1.7373503348717956 | 29.903078901901488 | 2165.1 | 27t9ieom | https://waterforpeople.s3.amazonaws.com/images/613243a5-8313-4cda-b4f4-033cba2c556e.jpg | 2015 | Normal | No | [5 empty] | Yes | 3 |  | 2015 | Normal | 8000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.737469097673669 | 29.903365740788146 | 2151.4 | 27tg26c9 | 2 | https://waterforpeople.s3.amazonaws.com/images/a55e2452-16a3-4d71-9cd3-ab6966104f94.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point located at Gasiza health post | 492e718efc9bb6f3aa7bb1c99dc565
ch70-jhqe-jhfa | 1 |  | J7 Rw10 | 1205770080 | 09-03-2017 10:21:40 CET | Tuyisenge Vianney | 00:20:15 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Buhande |  |  | Water point from Rutare gravity on Tare-Rusiga pumping system | 9577 |  | 129 | 129 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Government in partnership with water for people | This is water point at Kubashinwa Gasiza near Bushoki police is among the 4water points of Rutare gravity from collection chamber of 8Rusumo sources feeding Tare pumping system | 8 | Spring | 1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 2 |  | 2015 | Normal | 2000 | Yes | 4 | -1.7401609422300985 | 29.91862556826173 | 1870.9 | 27xwt7si | https://waterforpeople.s3.amazonaws.com/images/145fedf2-4e1b-40ca-858f-bd824aed8873.jpg | 2015 | Normal | No | [5 empty] | Yes | 1 |  | 2015 | Normal | 2000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7402390327146628 | 29.918810508688804 | 1844.5 | 27y0z910 | 4 | https://waterforpeople.s3.amazonaws.com/images/b4c3bd5a-d3fb-4c7e-8ac5-5581da08d31f.jpg | 2015 | Normal | No |  |  |  | Yes |  | Poor | This water at Kubashinwa is operating poorly since there are some spare parts damaged like taps | f967701b3f3f4372726db43a91e023a
y1q5-sf5a-y2qj | 1 |  | J7 Rw24 | 1224850097 | 16-03-2017 06:14:05 CET | Kabalisa Manzi Christella | 00:07:52 | 2017 | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 14106 |  | 495 | 495 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | no problem | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 16 | Normal | Yes | 8 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7358377293093425 | 30.03267193411816 | 2044.6 | 27qr0jqe | 1 | https://waterforpeople.s3.amazonaws.com/images/899b01b1-7b52-42ac-a37c-9dc286dfa7b9.jpg | 2012 | Normal | No |  |  |  | No | Water seller was not around | Normal | This Water Point/system functions well | 13c39b96ec35c6d86ef7de02ae25d96
2cbf-hvbm-y4r5 | 1 |  | J7 Rw19 | 1216830126 | 10-03-2017 04:19:58 CET | Kayinamura Innocent | 00:17:51 | 2017 | Rwanda | Rulindo | Ngoma | Karambo | Butare |  |  | Shishi network |  |  | 122 | 40 | 82 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | kigina | Governement (District, WASAC) and Water For People | poor management | 1 | Spring | -1.8097197675805605 | 29.979881122155494 | 1794.6 | 2b4xn0ly |  | No | 28 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 28 | Yes | 1 |  | 2014 | Normal | 700 | Yes | 2 | -1.809674509873321 | 29.981912015157096 | 1778.3 | 2b4v9a7f |  | 2014 | Normal | No | [5 empty] | Yes | 1 |  | 2014 | Normal | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.809844129356897 | 29.9845091349461 | 1684.5 | 2b55dnid | 4 | https://waterforpeople.s3.amazonaws.com/images/7b86663e-d0ad-49b9-bbf1-e67f8a072860.jpg | 2014 | Does Not Function | No |  |  |  | Yes |  | Poor | 1. Outlet of start chamber had been damaged 2. poor management | e768e69c85931174810412dbc43e4ab
u4ce-uw8a-mj7 | 1 |  | J7 Rw10 | 1211790230 | 10-03-2017 09:59:09 CET | Tuyisenge Vianney | 00:11:21 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Byimana |  |  | Water Point at College Foundation Sina Gerard/Tare-Rusiga pumping | 9577 |  | 92 | 92 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This is a water point located at College Foundation Sina Gerard | 8 | Spring | -1.7379838326200818 | 29.906994158112184 | 2048.8 | 27ub0ptp |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 4000 | Yes | 1 | -1.6793033064768899 | 29.88814742225158 | 2066.7 | 2559d3wh | https://waterforpeople.s3.amazonaws.com/images/af9ff7be-216a-41a5-a5da-44a54e604c39.jpg | 2015 | Normal | No | [5 empty] | Yes | 3 |  | 2015 | Normal | 8000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.679875558898144 | 29.888033386479623 | 2073.3 | 2567atds | 2 | https://waterforpeople.s3.amazonaws.com/images/651f8870-3db4-4a83-b6cf-09e52e89c904.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water point located at Sina Gerard College is served by Tare-Rusiga pumping on the distribution line leading to Nyirangarama. | e94c739e7c9cc7eeadd0b7b64d7f8935
c484-wt4n-uj5d | 1 |  | J7 Rw19 | 1233910498 | 24-03-2017 04:48:57 CET | Kayinamura Innocent | 00:07:02 | 2017 | Rwanda | Rulindo | Masoro | Kivugiza | Rebero |  |  | Mutagata motorised network | 26296 |  | 376 | 123 | 253 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7910064119882625 | 30.067678946323255 | 1763.7 | 2a9zp0g4 | 64 | https://waterforpeople.s3.amazonaws.com/images/f872d194-c9c5-4916-b287-99f9fce64727.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | e0418be35db6873c14d8874b6f83f385
sdfp-87v9-yfd0 | 1 |  | J7 Rw7 | 1246380144 | 23-03-2017 16:09:15 CET | Safari Bosco | 00:26:32 | 2017 | Rwanda | Rulindo | Murambi | Gatwa | Kigarama | [5 empty] | 209 | 209 | 0 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  |  | This Water point has few users because many people have water in their housholds | 3 | Spring | -1.8081127252820783 | 30.019302406005654 | 1889.4 | 2b2ado4h |  | Yes | 14 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2001 | Normal | 14 | Yes | 1 |  | 2001 | Normal | 12000 | Yes | 7 | -1.8083188633668612 | 30.018599981640595 | 1825.6 | 2b2mac7t |  | 2001 | Normal | No | [5 empty] | Yes | 1 |  | 2001 | Normal | 12000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8400248712226657 | 30.047248516443364 | 1521.4 | 2cj27vp4 | 2 | https://waterforpeople.s3.amazonaws.com/images/882ef901-cd0e-4fee-8975-6ec77c7f4965.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | This Water point has few users because people have water in their homes | 4b8cceb849374382699f6fbb72f0842e
79nq-hk6h-dqk3 | 1 |  | J7 Rw23 | 1320020107 | 23-04-2017 14:44:16 CEST | Rugirangoga Augustin | 00:24:47 | 2017 | Rwanda | Rulindo | Buyoga | Butare | Kankanga | [5 empty] | 151 | 100 | 51 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | shagasha gatare gatenderi gahororo | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 11 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2014 | Poor | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7008244427577213 | 30.028711528823916 | 1625 | 264ulytb | 2 | https://waterforpeople.s3.amazonaws.com/images/49a0d20c-075d-4c64-ab7d-e5613dde0caf.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal |  | ac1a33845aed3bdabc319f62caa048e8
c8jq-hgtx-erp0 | 1 |  | J7 Rw15 | 1204890444 | 08-03-2017 20:50:27 CET | Mukakarangwa Assoumpta | 00:08:10 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 6436 |  | 165 | 40 | 125 | Yes | Piped Network with Pump |  | 2013 | Yes | Nyarushinya | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2006.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8678905774206922 | 29.98022118123867 | 1926.6 | 2dt5iy56 | 1 | https://waterforpeople.s3.amazonaws.com/images/c5ef352f-9704-47d1-a9c7-6ae995a7a62c.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | bc6a38dd1f38ef4575d179585d2d4e
gqh9-kk8h-rc2b | 1 |  | J7 Rw7 | 1246610283 | 23-03-2017 15:15:51 CET | Safari Bosco | 00:20:26 | 2017 | Rwanda | Rulindo | Murambi | Bubangu | Taba |  |  | rwiseke | 9536 |  | 193 | 193 | 0 | Yes | Piped Network with Pump |  | 2001 | No |  | Governement (District, WASAC) and Water For People | The water point has no problem | 3 | Spring | -1.8081127252820783 | 30.019302406005654 | 1889.4 | 2b2ado4h |  | Yes | 14 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2001 | Normal | 14 | Yes | 1 |  | 2001 | Normal | 1200 | Yes | 7 | -1.8083188633668612 | 30.018599981640595 | 1825.6 | 2b2mac7t |  | 2001 | Normal | No | [5 empty] | Yes | 1 |  | 2001 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8454218995269738 | 30.043558100586658 | 1646.6 | 2crzpyc3 | 1 | https://waterforpeople.s3.amazonaws.com/images/4ef737c5-7435-4fc1-a200-afed53577cbc.jpg | 2001 | Normal | No |  |  |  | Yes |  | Normal |  | 16904e75c86c898c1eae65ee2a79a614
ax54-dthq-nf40 | 1 |  | J7 Rw23 | 1218290071 | 15-03-2017 06:11:26 CET | Rugirangoga Augustin | 00:18:06 | 2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Gihanga II |  |  | 151 | 151 | 0 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | gatiba gatwa |  | Gihanga and Gihanga II have common source and common intake tank | 1 | Spring | -1.6358367374763643 | 29.91135277934778 | 1996.9 | 235d9tex |  | Yes | 15 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 15 | Yes | 1 |  | 2016 | Normal | 7000 | Yes | 3 | -1.6358367374763643 | 29.91135277934778 | 1996.9 | 235d9tex |  | 2016 | Normal | No | [5 empty] | Yes | 1 |  | 2016 | Normal | 7000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6483025593595437 | 29.925298393597362 | 1861 | 23pzpcvo | 2 | https://waterforpeople.s3.amazonaws.com/images/fca70347-01ec-4e94-90eb-57d5f4babbc0.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | gihanga works well | 818f48b6037c4ce9a2bd37257ca93a2
s3a0-96tv-5wt0 | 1 |  | J7 Rw23 | 1217630111 | 11-03-2017 20:02:59 CET | Rugirangoga Augustin | 00:15:12 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Cyondo |  |  | Ruramba | 1564 |  | 173 | 150 | 23 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | this network is new but affected by road construction that is why some tanks and water taps do not get water | 1 | Groundwater (well, etc.) | -1.612504606727932 | 29.86882944818841 | 1922.4 | 222s9irk |  | Yes | 60 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 60 | No | [5 empty] | Yes | 2 | -1.6213170406640873 | 29.869799421143036 | 1873.1 | 22hcseq1 |  | 2016 | Normal | Yes | 2 | Pressure Break Tank |  | 2016 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6231715259446775 | 29.868800062729406 | 1837.2 | 22kfj18g | 2 | https://waterforpeople.s3.amazonaws.com/images/f2ab173f-a206-480e-9e4b-3d82f018663d.jpg | 2016 | Does Not Function | No |  |  |  | No | water is not available because pipes have been damaged by the road construction project | Does Not Function | Water is not Flowing because pipes were destroyed during road construction | b9fe3968c0abbcbfcb8e9c474728a6b6
j5f8-7ge5-q5xx | 1 |  | J7 Rw15 | 1199080278 | 09-03-2017 20:47:03 CET | Mukakarangwa Assoumpta | 00:06:56 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Gisoro- Nyundo network | 2297 |  | 188 | 80 | 108 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.840451151026817 | 29.948165560771624 | 1795.9 | 2cjrthy1 |  | Yes | 13 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 13 | Yes | 1 |  | 2013 | Normal | 13 | Yes | 6 | 1.8406374522240199 | 29.94836287627501 | 1783.7 | 2ck2jau3 |  | 2013 | Poor | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 7000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8505143806786524 | 29.943535619146584 | 1554 | 2d0erkh7 | 1 | https://waterforpeople.s3.amazonaws.com/images/fe7a92fd-7ce3-4d24-bd29-cc8e349149f6.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | e61fd7bdd7de51d631b18df4674bbc
uyqk-ux2j-g347 | 1 |  | J7 Rw8 | 1240030340 | 23-03-2017 10:29:49 CET | Amani Desire | 00:10:27 | 2017 | Rwanda | Rulindo | Murambi | Bubangu | Gashubi |  |  | Mutagata Motorised Network | 26296 |  | 140 | 35 | 105 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.79689442728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8416933514132 | 30.027738962431428 | 1832.5 | 2cltn9kl | 64 | https://waterforpeople.s3.amazonaws.com/images/ab430f45-474e-4cce-a565-321d1332681b.jpg | 2016 | Normal | No |  |  |  | Yes |  | Poor | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | 7cc48686e24caa2eaf8d87d21093216b
n193-e663-un5s | 1 |  | J7 Rw10 | 1224690269 | 13-03-2017 21:36:18 CET | Tuyisenge Vianney | 00:09:05 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Kigamba water point/Rutomvu gravity | 3015 |  | 172 | 172 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | Water point was closed not working | 1 | Spring | -1.677891751247546 | 29.90118126071259 | 1802.6 | 252xezpf |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6928194604864426 | 29.904868658617737 | 1747.4 | 25rlpqaw | 1 | https://waterforpeople.s3.amazonaws.com/images/02772e2a-dc24-45ea-b94f-0221a9c2d90e.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | The water point was closed due to people claiming the water cost is too high to afford | 5ef2c2357e35ddbc263b5b99b547833
nav7-ee4j-tuws | 1 |  | J7 Rw24 | 1330550070 | 25-04-2017 00:23:58 CEST | Kabalisa Manzi Christella | 00:09:33 | 2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Karera |  |  | Rwamugaza network | 14106 |  | 182 | 182 | 0 | Yes | Piped Network -- Gravity Only |  | 2014 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7374173333138418 | 30.006563288387298 | 1723.9 | 27td3141 |  | 2003 | Normal | Yes | 14 |  |  | 2003 | Normal | Yes | 1 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8053410610868925 | 30.093479846723525 | 1509.5 | 2axpgm4m | 1 | https://waterforpeople.s3.amazonaws.com/images/be0bdd11-5e46-46ed-9cc3-a6e75f0b0820.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal |  | b1348a831b6c3ab66f3fc0bf3f90e875
xdpw-tbfr-f42y | 1 |  | J7 Rw23 | 1206540154 | 08-03-2017 18:25:12 CET | Rugirangoga Augustin | 00:18:34 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Mutima |  |  | Rutare I | 345 |  | 169 | 140 | 29 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | mutima base | Governement (District, WASAC) and Water For People | The water point is functional | 1 | Spring | -1.6423106459400025 | 29.877266381687242 | 1724.3 | 23g32p5g |  | Yes | 20 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Poor | 20 | Yes | 1 |  | 2017 | Normal | 3800 | Yes | 2 | -1.6421782827296525 | 29.877214231989047 | 1817 | 23fuqmok |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6422376903962363 | 29.877041925587367 | 1803.7 | 23fyb8b6 | 2 |  | 2017 | Normal | No |  |  |  | Yes |  | Normal | robinet imwe barayifunze | 66d31d4beaf6367aff6e28ea191933
nmgr-y1v3-mqx7 | 1 |  | J7 Rw26 | 1245550322 | 03-01-2015 04:49:24 CET | Byukusenge Elie | 00:07:40 | 2017 | Rwanda | Rulindo | Rukozo | Mbuye | Ruhanga |  |  | Kabonanyoni | 7894 |  | 150 | 145 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare, Kabera,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe, Kabyayi, Kabingo, Kamiyove, Murwa, Nyenyeri, Rukingu and Kivomo | Governement (District, WASAC) and Water For People | This is the New pumping system which serves the community located at the uphill, it has 5 sources, one source which is located in Miyove sector, Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro,This network has one reservoir which is not functioning, This network serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 2015 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6140628855502286 | 29.947463020870387 | 1975.4 | 225d55qq | 31 | https://waterforpeople.s3.amazonaws.com/images/3326247f-2e2b-4de5-b21e-2d26333a0b95.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is in good condition | 73bf7a1e19f8d6a398b7f46daa51b81
q3k9-rtt2-dhu4 | 1 |  | J7 Rw10 | 1202112191 | 14-03-2017 23:06:49 CET | Tuyisenge Vianney | 00:04:34 | 2017 | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Kingazi4 wpt/Nyakabizi1&2 | 1259 |  | 157 | 157 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | This water operates well however it doesnot meet the demand of the people | 1 | Spring | -1.803447729664134 | 29.930708856826865 | 1927.1 | 2aukc7xn |  | Yes | 20 | No | [5 empty] | 20 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.807755547055205 | 29.91604431158269 | 1655.8 | 2b1oy1js | 1 | https://waterforpeople.s3.amazonaws.com/images/9e47f64c-556c-4ffa-8c5c-df8df4248c98.jpg | 2013 | Does Not Function | No |  |  |  | No | Does nolonger function | Does Not Function | This water does nolonger operate because they closed it after realizing that it doesnot have enough water to deliver | beb6bbab8f92c940f72fa246428abd70
ga8x-sqvc-2w2p | 1 |  | J7 Rw23 | 1320220083 | 23-04-2017 14:42:31 CEST | Rugirangoga Augustin | 00:09:59 | 2017 | Rwanda | Rulindo | Buyoga | Gitumba | Rutabo |  |  | kiruruma | 8295 |  | 128 | 80 | 48 | Yes | Piped Network with Pump |  | 2014 | Yes | rutabo gatenderi gatare shagasha | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 11 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2014 | Normal | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 9000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6780121330554885 | 30.044889181505766 | 2100.7 | 2534k82o | 1 | https://waterforpeople.s3.amazonaws.com/images/f4b04c42-4af4-4b66-93f3-2cfa9682d708.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | d7b182fc814a288e32b388aff483ac5b
r5g4-393q-y1a9 | 1 |  | J7 Rw10 | 1208640310 | 10-03-2017 12:37:33 CET | Tuyisenge Vianney | 00:07:33 | 2017 | Rwanda | Rulindo | Bushoki | Mukoto | Marembo |  |  | Marembo water point/Tare-Rusiga pumping | 9577 |  | 90 | 90 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This is Marembo water point.It has its own storage tank | 8 | Spring | -1.7379838326200818 | 9.90585605970111 | 2048.8 | 7zfjjxu |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 4000 | Yes | 1 | -1.7136359012630078 | 29.903612799493278 | 2100.8 | 26q1a7rw | https://waterforpeople.s3.amazonaws.com/images/1e4dde23-d0b0-42db-a492-493876278199.jpg | 2015 | Normal | No | [5 empty] | Yes | 1 |  | 2015 | Normal | 8000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.713465158789737 | 29.90356428864639 | 2069.3 | 26pr5uhn | 1 | https://waterforpeople.s3.amazonaws.com/images/c9f7a65e-980f-40a0-9781-62d793b41e74.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water point | 827bc622ab325ebf5f8979813858019
tm91-cx50-1edc | 1 |  | J7 Rw8 | 1242980146 | 23-03-2017 10:42:17 CET | Amani Desire | 00:10:22 | 2017 | Rwanda | Rulindo | Murambi | Bubangu | Mayange |  |  | Mutagata Motorised Network | 26296 |  | 198 | 160 | 38 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release chamber |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.856166926883045 | 30.03714762996553 | 1771.2 | 2d9r5hzn | 64 | https://waterforpeople.s3.amazonaws.com/images/79a72823-6087-495f-a170-4b0af38c6ab4.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | d2b87bbce384f1a29eb875fe857cc330
5jm4-hxk3-w05w | 1 |  | J7 Rw10 | 1205581394 | 15-03-2017 19:10:33 CET | Tuyisenge Vianney | 00:14:26 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Gatsinde |  |  | Kiringo wpt/Nyirambuga pumping | 30604 |  | 178 | 178 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | GoR | The water point has been constructed very soon.Water comes rarely.When water is not present they fetch from Buramira water points | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.6712468074392397 | 29.927313775049342 | 1769.7 | 24rxhqmh | https://waterforpeople.s3.amazonaws.com/images/2f9efee0-e1a2-4605-88ca-f3e78066e40b.jpg | 2012 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6711254692997108 | 29.927116339614138 | 1771.8 | 24rqcjd3 | 1 | https://waterforpeople.s3.amazonaws.com/images/afff362b-c0bf-4019-a2d0-3bf8f9d8d584.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | The water point has been constructed very soon.Water comes rarely.When water is not present they fetch from Buramira water points.Currently,their water storage tanks | 6f978d53dfadcc2397cb4198735f0d0
8b0r-tjws-u9k8 | 1 |  | J7 Rw8 | 1242950263 | 22-03-2017 20:21:44 CET | Amani Desire | 00:12:29 | 2017 | Rwanda | Rulindo | Murambi | Mvuzo | Rurama |  |  | Mutagata Motorised Network | 26296 |  | 155 | 60 | 95 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release chamber |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7929371284295872 | 30.02146409348254 | 2088.2 | 2ad6lnue | 64 | https://waterforpeople.s3.amazonaws.com/images/a5d938bd-7765-4dee-8953-bd91d89a9d1f.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | c01011319cb78ee5eb4a2cc1c54225bf
4ubc-wder-9wkb | 1 |  | J7 Rw10 | 1313930058 | 20-04-2017 08:22:17 CEST | Tuyisenge Vianney | 00:07:44 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Gatare |  |  | Gatare water point near cafe plantation/Nyirambuga pumping | 30604 |  | 143 | 143 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Water point abandoned and nolonger operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | Yes | 1 | -1.6878614919371457 | 29.942390138214048 | 2035.3 | 25jf065b | https://waterforpeople.s3.amazonaws.com/images/64d35163-054f-477c-a6b4-a270aa223a4a.jpg | 2012 | Normal | Yes | 2 | Pressure Break Tank¦Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/125f4341-f3dc-4696-af1d-acd6f8434b7d.jpg | 2017 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.687746462874477 | 29.94256131869302 | 2025.7 | 25j7uyw1 | 2 | https://waterforpeople.s3.amazonaws.com/images/9ef51838-8ffe-40df-a67e-615e4db7484e.jpg | 2012 | Does Not Function | No |  |  |  | No | The storage tank is operational however its water point was abondoned and nolonger operational | Does Not Function | The storage tank is operational however its water point was abondoned and nolonger operational as well as and water meter taps removed | 1650b0621afbaba2e62196fa84d858f
gmhq-hwgy-129 | 1 |  | J7 Rw23 | 1236940801 | 23-03-2017 06:27:26 CET | Rugirangoga Augustin | 00:28:24 | 2017 | Rwanda | Rulindo | Kisaro | Sayo | Rusongati |  |  | Kiruruma | 8295 |  | 163 | 160 | 3 | Yes | Piped Network with Pump |  | 2014 | Yes | rutabo gitaba nyarubuye remera rusongati rugarama cyasuli Munini | Governement (District, WASAC) and Water For People | the water tap does not work | 1 | Spring¦Groundwater (well, etc.) | -1.668151432446623 | 30.0466574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 15 | -1.6111677762752643 | 29.8839135826884 | 1852 | 220khftj |  | 2014 | Normal | Yes | 5 | Pressure Break Tank |  | 2014 | Normal | Yes | 3 |  | 2014 | Normal | 4000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6655773235202498 | 30.013901935082696 | 2081.2 | 24ijwzaj | 2 | https://waterforpeople.s3.amazonaws.com/images/2b349490-6521-4375-9b4a-18d8d5399683.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | there is no problem with the network | a1efd6e22ef3b86517a5d45b3f19329
xkr1-wwmn-vpw1 | 1 |  | J7 Rw15 | 1205890650 | 09-03-2017 05:54:56 CET | Mukakarangwa Assoumpta | 00:07:49 | 2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Rimwe |  |  | kirikumuryango network |  |  | 120 | 60 | 60 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8844389333831084 | 29.949657952421965 | 1200.3 | 2eki9wh4 | 1 | https://waterforpeople.s3.amazonaws.com/images/b9683cdb-f2d6-4467-86a1-208ee024831b.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 28706666f0bd13d6f38918286f27ee1
puj6-aujk-c880 | 1 |  | J7 Rw26 | 1230030735 | 21-03-2017 14:13:31 CET | Byukusenge Elie | 00:07:37 | 2017 | Rwanda | Rulindo | Rukozo | Mbuye | Nyarusebeya |  |  | Kabonanyoni | 7894 |  | 60 | 55 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6075387266929553 | 29.956074404280635 | 1962.5 | 21ukd3s8 | 31 | https://waterforpeople.s3.amazonaws.com/images/aa50c068-7914-4744-89a2-3ddfcf62c05e.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The community does not use it as they use water tap located at Sindiye Source. | b78eece2ffde70fe24f6155a2f0daee
hh51-356p-rx21 | 1 |  | J7 Rw15 | 1205920340 | 09-03-2017 21:36:45 CET | Mukakarangwa Assoumpta | 00:05:53 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Ngona |  |  | Bitete-Rwahi network | 1316 |  | 122 | 35 | 87 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.8336417737979869 | 29.346668826428 | 1815.5 | 2c8id6ca |  | Yes | 12 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 |  | 2013 | Normal | 600 | Yes | 6 | 1.8427360326225883 | 29.938932546871705 | 1676.5 | 2cnjkbst |  | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.86338001352638 | 29.92757372958154 | 1403.4 | 2dlp0fwr | 1 | https://waterforpeople.s3.amazonaws.com/images/2abb280f-885b-4edc-89c6-52fdf746e2ac.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 68dafa471bcaaaab4a19e3da5678730
44wa-1heg-uegs | 1 |  | J7 Rw15 | 1200340571 | 09-03-2017 06:15:39 CET | Mukakarangwa Assoumpta | 00:14:27 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Kigali |  |  | kirikumuryango network |  |  | 220 | 120 | 100 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8750079565735702 | 29.940669882946953 | 1393.5 | 2e4wu4y6 | 1 | https://waterforpeople.s3.amazonaws.com/images/4672e299-bb0f-4388-8e16-fd92baf88180.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 5e5d4a1dc7875ac75d79ef7c0ea684d
3k18-uu11-nv16 | 1 |  | J7 Rw15 | 1200310693 | 09-03-2017 17:44:28 CET | Mukakarangwa Assoumpta | 00:08:30 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Nyabyondo |  |  | kirikumuryango network |  |  | 312 | 150 | 162 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Poor | 10000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.9073364634353267 | 29.980183460497692 | 1376.1 | 2fmdok0p | 1 | https://waterforpeople.s3.amazonaws.com/images/4aa7d71c-be25-4789-9a1c-b90f5e184d62.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | water tap was constructed by IETK company limited located in Rulindo district | 4423de1192abfb6f409a7a25989c581d
vjw9-rh6x-k84j | 1 |  | J7 Rw24 | 1224860223 | 16-03-2017 07:43:16 CET | Kabalisa Manzi Christella | 00:07:05 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Karugaju |  |  | Rwamugaza | 14106 |  | 345 | 345 | 0 | Yes | Piped Network -- Gravity Only |  | 2014 | No |  | Governement (District, WASAC) and Water For People | no problem | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3.5 | Yes | 2 |  |  | 2003 | Normal | 3.5 | Yes | 1 |  | 2003 | Normal | 8000 | Yes | 20 | -1.7416188180333267 | 29.988511802248155 | 1861.3 | 280b531p |  | 2014 | Normal | Yes | 16 |  |  | 2014 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7325263554185224 | 30.060475742463158 | 1564.6 | 27l9y2po | 1 | https://waterforpeople.s3.amazonaws.com/images/8b010e60-0a82-4310-8bee-9c1998c025ff.jpg | 2014 | Does Not Function | No |  |  |  | No | System under rehabilitation | Poor | no problem | 6660a82b1b8bb950b6cb6a9533e9dfb
aev6-d8qd-qcur | 1 |  | J7 Rw10 | 1236020202 | 03-01-2015 02:02:29 CET | Tuyisenge Vianney | 00:04:38 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point at Nyirabirori cell/Nyirambuga pumping | 30604 |  | 169 | 169 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People |  | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6913209526920316 | 29.937818900655458 | 2119.6 | 25p505f6 | 1 | https://waterforpeople.s3.amazonaws.com/images/3ab722df-7313-43fd-949c-7fdc41899dec.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Water point operates well with one tap closed and another one functioning | a9ac48eaa60a688929c895bf982265b
edwq-ca95-4bjn | 1 |  | J7 Rw10 | 1214532899 | 15-03-2017 16:58:14 CET | Tuyisenge Vianney | 00:06:28 | 2017 | Rwanda | Rulindo | Rusiga | Kirenge | Rebero |  |  | Kirenge water point/Tare-Rusiga pumping | 9577 |  | 181 | 181 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This water point operates well and normally | 10 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7939764969712915 | 29.927012660775716 | 2103.6 | 2aewiq12 | 1 | https://waterforpeople.s3.amazonaws.com/images/159a253b-bfda-4292-9ee3-17d6be6eb50d.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water point operates well and normally | 2125cd43aa6b790d5abca5e159c219
jfda-e7jv-cgn9 | 1 |  | J7 Rw8 | 1238250200 | 23-03-2017 11:53:31 CET | Amani Desire | 00:09:33 | 2017 | Rwanda | Rulindo | Masoro | Shengampuri | Umubuga |  |  | Mutagata Gravity Network | 26296 |  | 175 | 58 | 117 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | Ruri,musenga,umubuga,amataba,rusine,marenge |  |  | 1 | Spring | -1.8023389079852206 | 30.042447389592418 | 1691.2 | 2asq94nc |  | Yes | 8 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2004 | Poor | 8 | Yes | 1 |  | 2004 | Poor | 3500 | Yes | 6 | -1.8078446763653504 | 30.066649761552014 | 1669.8 | 2b1uaz5m |  | 2004 | Poor | Yes | 4 | Distribution Chamber¦Washout and Air release chamber |  | 2004 | Poor | Yes | 2 |  | 2004 | Poor | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8111113218224222 | 30.07384384942692 | 1602.7 | 2b78zq0y | 12 | https://waterforpeople.s3.amazonaws.com/images/3c3684d7-fa27-4138-8ba0-58499e48240c.jpg | 2004 | Poor | No |  |  |  | No | pipes are broken and water do not reach the water point | Poor | 1.the extension to nyabinyana village has 2 reservoirs and two water points which is under construction 2.this system have been constructed in 2004 3.it serves a part of Masoro sector and parts is located in Gasabo district 4. 2 water points and one reservoir have been constructed in 2016 5.in general this network has 27 water points in wich 12 are in Rulindo district and others are in Gasbo district | dd671c35eaf81f29bd70a385a5b2b29
etb3-pdm9-mkqm | 1 |  | J7 Rw23 | 1215351055 | 15-03-2017 06:56:02 CET | Rugirangoga Augustin | 00:26:17 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare I | 345 |  | 229 | 200 | 29 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | this network has no problem | 2 | Spring | -1.6301134502114292 | 29.875285172506338 | 2066.9 | 22vwpv40 |  | Yes | 50 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Poor | 50 | Yes | 1 |  | 2014 | Poor | 4500 | Yes | 2 | -1.6508336759560134 | 29.8843940764913 | 1503.1 | 23u6c0m3 |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6514295309745453 | 29.88121425506491 | 1709.4 | 23v5gla4 | 2 | https://waterforpeople.s3.amazonaws.com/images/118cea58-c26b-4fe9-92d6-ecda8ed86a49.jpg | 2016 | Normal | No |  |  |  | Yes |  | Poor | this network has been destroyed by the road construction | 55c47c9ccc15165b3ab7663487a4f138
7h30-p39a-38wg | 1 |  | J7 Rw10 | 1223620662 | 15-03-2017 18:57:58 CET | Tuyisenge Vianney | 00:09:47 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Giko cell water point/Nyirambuga pumping | 30604 |  | 134 | 134 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | GoR | Giko cell water point/Nyirambuga pumping operates very well | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6815049000077666 | 29.91011898264954 | 2093.7 | 258wch5p | 1 |  | 2012 | Normal | No |  |  |  | Yes |  | Normal | Giko cell water point/Nyirambuga pumping operates well | 6192becd84cd2c71555e2d3ff2dd7
v1r3-vr00-edd5 | 1 |  | J7 Rw10 | 1306970163 | 18-04-2017 06:45:43 CEST | Tuyisenge Vianney | 00:11:27 | 2017 | Rwanda | Rulindo | Tumba | Gahabwa | Rushaki |  |  | Rushaki water point Bizimana/Nyirambuga pumping system | 30604 |  | 152 | 152 | 0 | Yes | Piped Network with Pump |  | 2017 | Yes | Rushaki of Gahabwa-Tumba as well as Kavumo and Karambi of Karama-Buyoga | Governement (District, WASAC) and Water For People | Water point is operational. | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | Yes | 1 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/464f740a-4093-42ca-9939-cf54a37dee93.jpg | 2017 | Normal | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/b33d0e67-2f6f-4391-bfbc-5a96e6f20e92.jpg | 2017 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.719669636020445 | 29.977247100184954 | 1825.6 | 2700am4c | 2 | https://waterforpeople.s3.amazonaws.com/images/916267ce-251f-4dab-bd2c-27f80c6307cf.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | The water point is operational | 1a23e7722803dd1ed5f1e492ea2ebce
3scj-r50n-xbaa | 1 |  | J7 Rw10 | 1207230351 | 10-03-2017 10:54:58 CET | Tuyisenge Vianney | 00:13:54 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Bubiro |  |  | Gakenke-Muyongwe-Karyango-Mugera Water point/Tare-Rusiga pumping | 9577 |  | 300 | 300 | 0 | Yes | Piped Network with Pump |  | 2015 | Yes | Bubiro village of Rulindo and Mugera village of Gakenke | Governement (District, WASAC) and Water For People | This water point is located in opposite side of road dividing Rulindo and Gakenke districts.It's located in Gakenke district,Muyongwe sector,Karyango cell,Mugera village | 8 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte | https://waterforpeople.s3.amazonaws.com/images/b59df924-4e0f-443d-87b1-8cc24cde6de2.jpg | Yes | 40 | No | [5 empty] | 40 | Yes | 1 |  | 2015 | Normal | 4000 | Yes | 1 | -1.6891059134846897 | 29.885070202931804 | 2150.5 | 25lgtwpu | https://waterforpeople.s3.amazonaws.com/images/7a473eb4-97d7-4e06-a55d-8a7ea3695a9b.jpg | 2015 | Normal | No | [5 empty] | Yes | 3 |  | 2015 | Normal | 4000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6891742491346506 | 29.88501381589485 | 2151.7 | 25lkzxya | 2 | https://waterforpeople.s3.amazonaws.com/images/31c243be-9212-46b7-902f-057ea1935585.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water point operates normally and sucessfully delivers water to the people of Bubiro village of Rulindo district and Mugera village of Gakenke district. | 15ce37e61ebde44971bfd1b9774672b
3aaw-m7ht-s9v0 | 1 |  | J7 Rw15 | 1243760103 | 23-03-2017 06:19:41 CET | Mukakarangwa Assoumpta | 00:06:26 | 2017 | Rwanda | Rulindo | Kinihira | Marembo | Cyogo |  |  | Nyamagana-Kinihira |  |  | 184 | 65 | 119 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 18 | Distribution Chamber¦Ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6692530156439316 | 29.93947614390856 | 1932 | 24on0hc2 | 2 | https://waterforpeople.s3.amazonaws.com/images/482e0f2d-dba3-400f-b586-3005bbfcb100.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | 34c93ab8dc2987d8e0fbeb68c4de6f
u0ha-wu8w-6rdx | 1 |  | J7 Rw7 | 1229980393 | 23-03-2017 15:44:33 CET | Safari Bosco | 00:41:59 | 2017 | Rwanda | Rulindo | Murambi | Gatwa | Kigarama |  |  | rwisike | 9536 |  | 209 | 209 | 0 | Yes | Piped Network -- Gravity Only |  | 2001 | Yes | gatare na kigarama | Governement (District, WASAC) and Water For People | The Water Points works well except in the dry season | 3 | Spring | -1.8081127252820783 | 30.019302406005654 | 1889. | 2b2ado4h |  | Yes | 14 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2001 | Normal | 14 | Yes | 1 |  | 2001 | Normal | 1200 | Yes | 7 | -1.8083188633668612 | 30.018599981640595 | 1825.6 | 2b2mac7t |  | 2001 | Normal | No | [5 empty] | Yes | 1 |  | 2001 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8375142992106768 | 30.041234018208442 | 1671 | 2cews2t8 | 1 | https://waterforpeople.s3.amazonaws.com/images/d88e4e22-7fb0-421d-99b8-87fc84f1012a.jpg | 2001 | Normal | No |  |  |  | Yes |  | Normal |  | bd936978d67525d6d935586eead5f131
pkte-8m2m-3hqm | 1 |  | J7 Rw23 | 1248480062 | 25-03-2017 20:47:43 CET | Rugirangoga Augustin | 00:37:07 | 2017 | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | Kiduha | 0 |  | 151 | 130 | 21 | Yes | Piped Network -- Gravity Only |  | 2007 | Yes | kankanga gasave | Italians(LAKE ANGELS) | Giko Village doesn’t have Water | 1 | Groundwater (well, etc.) | -1.692136727874054 | 30.02146392212493 | 1866.9 | 25qh8a2e |  | No | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Poor | 20 | Yes | 1 |  | 2007 | Poor | 2200 | Yes | 3 | -1.6932117321635163 | 30.026191374639453 | 1765.8 | 25s9j3fp |  | 2007 | Poor | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7022396340075416 | 30.026849345348403 | 1599.1 | 2676k33g | 2 | https://waterforpeople.s3.amazonaws.com/images/19376762-a70f-4f69-bb58-8e34a67f15bb.jpg | 2007 | Poor | No |  |  |  | Yes |  | Poor | this network needs rehabilitation | fce5fe0e7771a3351dec03944c213
p70a-y69f-k2nf | 1 |  | J7 Rw15 | 1238970133 | 21-03-2017 16:54:16 CET | Mukakarangwa Assoumpta | 00:14:44 | 2017 | Rwanda | Rulindo | Kinihira | Rebero | Taba |  |  | Miyove-Kinihira | 10452 |  | 122 | 60 | 62 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6681056590693237 | 29.986715424463537 | 1943.6 | 24mqjn4r | 2 | https://waterforpeople.s3.amazonaws.com/images/8e55ce32-3ddd-45ac-bf03-c21c0dde7265.jpg | 2015 | Normal | No |  |  |  | Yes |  | Poor |  | 1e69ac67c178f2fc74c4cd4bb099ebdd
jyk1-ggwm-ykwm | 1 |  | J7 Rw26 | 1234510390 | 21-03-2017 14:14:12 CET | Byukusenge Elie | 00:04:48 | 2017 | Rwanda | Rulindo | Rukozo | Mbuye | Musare |  |  | Kabonanyoni | 7894 |  | 40 | 35 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber |  | 2015 | Normal | Yes | 3 |  | 2015 | Poor | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6151513399298594 | 29.954779131169424 | 1772.7 | 22761eqj | 31 | https://waterforpeople.s3.amazonaws.com/images/0e472d85-aa43-435b-8592-31d1cd3583a1.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is located to the source Kabwiru II and the community use it as they do not pay for water. | cc1cfb214ba1691314fc81d29fdc79
m271-2rj7-p2tp | 1 |  | J7 Rw10 | 1301860049 | 14-04-2017 21:19:29 CEST | Tuyisenge Vianney | 00:11:39 | 2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Gitaba |  |  | Murambo catchment |  |  | 118 | 118 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | Gitaba,Murambo of Kayenzi and Muko of Mukoto | Rulindo district | Mpango spring catchment has been benefited to capture water to supply the Rulindo districg headquarters jointly with Rutembe spring catchment area | 1 | Spring | -1.7043297281583143 | 29.91732894426777 | 1391.2 | 26amznol | https://waterforpeople.s3.amazonaws.com/images/c5466a24-9747-4e9b-925c-8b6e0c3fb8d3.jpg | Yes | 20 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/1e5df911-6002-415c-a0c4-9265d4d80eb6.jpg | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 20 | Yes | 1 |  | 2015 | Normal | 100 | Yes | 1 | -1.7043255683189573 | 29.91733336629575 | 1338 | 26amznol | https://waterforpeople.s3.amazonaws.com/images/aca233d8-8b96-4f98-a089-2e890d75e3d0.jpg | 2015 | Normal | No | [5 empty] | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/40bb6412-cb02-490b-939d-b0ea28a3ec65.jpg | 2015 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7040379113230626 | 29.917556066981533 | 1786 | 26a5q353 | 1 | https://waterforpeople.s3.amazonaws.com/images/931fe6a3-af2d-4b62-9bba-3830dc67f9ee.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Mpango spring catchment has been benefited to capture water to supply the Rulindo districg headquarters jointly with Rutembe spring catchment area | dcc8be9eeaac178b85da5b7617b74279
w5qe-suyp-wfpn | 1 |  | J7 Rw10 | 1196910722 | 07-03-2017 13:39:51 CET | Tuyisenge Vianney | 00:25:01 | 2017 | Rwanda | Rulindo | Bushoki | Mukoto | Muko |  |  | Rusave water supply system/Water point at Anselme Gerant | 567 |  | 116 | 116 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Government | The water tap operates normally.It had been constructed in 1999 and reconstructed in 2013 by the government | 2 | Spring | -1.6994181353408764 | 29.906771285906107 | 1541.3 | 262intkr | https://waterforpeople.s3.amazonaws.com/images/08ea5100-c00a-48f5-8664-4f83c74d3c5d.jpg | Yes | 120 | No | [5 empty] | 120 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | 1.6994181353408764 | 29.906771285906107 | 1541.3 | 262intkr | 3 | https://waterforpeople.s3.amazonaws.com/images/87f9a8c2-f865-4ac0-a757-ee5e924b5fe0.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | The water point located at Gerant Anselme is connected to Rusave water supply system and is normally operational. | 84ce252362478876b9dde15858813b
jpy2-98sv-wqe4 | 1 |  | J7 Rw15 | 1207990180 | 08-03-2017 21:35:17 CET | Mukakarangwa Assoumpta | 00:06:41 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 6436 |  | 354 | 120 | 234 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8656752426612007 | 29.962994559886997 | 1919.5 | 2dphcppp | 1 | https://waterforpeople.s3.amazonaws.com/images/9fba594e-667b-438e-91c4-90eec9a9404c.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | a47dcd9d1c21f3eacb5769282499351
x61w-7f98-6x5v | 1 |  | J7 Rw24 | 1256650168 | 28-03-2017 08:41:37 CEST | Kabalisa Manzi Christella | 00:05:01 | 2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Rusekabuye |  |  | Rwamugaza network | 14106 |  | 195 | 195 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 3500 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7901701956519225 | 30.100472027823823 | 1662.8 | 2a8ma1ho | 1 | https://waterforpeople.s3.amazonaws.com/images/68f79c53-ac36-4f09-a55a-07f05a5b4658.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | b4a6c94d114a8434ff43ff3ea64d828
c7ch-7pmf-9put | 1 |  | J7 Rw26 | 1423920267 | 02-06-2017 09:28:08 CEST | Byukusenge Elie | 00:04:54 | 2017 | Rwanda | Rulindo | Cyinzuzi | Rudogo | Musenyi |  |  | Kararama | 6572 |  | 98 | 10 | 88 | Yes | Piped Network with Pump |  | 2009 | Yes | Not Water Tap | Water For People |  | 3 | Spring | -1.750378530192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2009 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 7 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2009 | Normal | Yes | 14 | Pressure Break Tank¦Distribution Chamber |  | 2009 | Normal | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 1 |  | 2012 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7701149274111974 | 30.014276258857425 | 1952.2 | 29bfyhbi | 1 | https://waterforpeople.s3.amazonaws.com/images/3cee5cd6-4a2d-4a31-8100-9aee9c408186.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal |  | 81d1a77f3dc2f7cefbe8e6938395c959
w48d-nj9e-ja9u | 1 |  | J7 Rw10 | 1278730070 | 05-04-2017 21:06:38 CEST | Tuyisenge Vianney | 00:12:18 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Gifuba |  |  | Rutare source catchment area | 9577 |  | 108 | 108 | 0 | Yes | Piped Network -- Gravity Only |  | 1960 | Yes | Gifuba,Nyirangarama and Terambere villages | Government | Rutare source catchment was constructes in late 1960s and its discharge is about 1l/s i.e. 20l/20s | 1 | Spring | -1.6705676828047722 | 29.878696276428556 | 2067 | 24qt0942 | https://waterforpeople.s3.amazonaws.com/images/7b1a2456-1668-4851-bea2-fdb63902a9c3.jpg | Yes | 20 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/a56a86e4-c4b8-482d-9ff8-0b2925813864.jpg | "Springbox" --Intake Structure at a Spring | 1960 | Poor | 20 | Yes | 1 |  | 1960 | Poor | 100 | No | [8 empty] | Yes | 1 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/de5716d5-6473-46b3-aeff-0ccc1942c3c0.jpg | 1960 | Poor | Yes | 1 |  | 1960 | Poor | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6707320268395076 | 29.878551296756896 | 1978.7 | 24r34me9 | 0 | https://waterforpeople.s3.amazonaws.com/images/df6497fa-be29-437a-8473-412a5393dc69.jpg | 1960 | Poor | No |  |  |  | Yes |  | Poor | Rutare source catchment was constructes in late 1960s and its discharge is about 1l/s i.e. 20l/20s.The source needs recapturing and the water point at the source needs to be strongly protected and reinforced | 56740b299ee64b83e0d4249390fbef
jdv3-dvht-j9db | 1 |  | J7 Rw10 | 1301130066 | 15-04-2017 22:06:22 CEST | Tuyisenge Vianney | 00:12:02 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Gasiza market water point1/Nyagahondo gravity system | 844 |  | 228 | 228 | 0 | Yes | Piped Network -- Gravity Only |  | 2010 | No |  | Caritas | The water point is closed because people denied to pay for the water.When the rain falls down the water turbidity is so high.And the storage tank since its installation hasn't been cleaned. | 1 | Spring | -1.7298781428197503 | 29.909858739201194 | 2099.2 | 27gw668q |  | Yes | 30 | No | [5 empty] | 30 | No | [5 empty] | Yes | 1 | -1.730297289475732 | 29.91789334234272 | 1796.2 | 27hl6dpm | https://waterforpeople.s3.amazonaws.com/images/6f417ba7-47ba-4216-83a3-653c13b01949.jpg | 2010 | Normal | No | [5 empty] | Yes | 2 |  | 2010 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7304402963326195 | 29.919078047124806 | 1758.4 | 27hu3vsm | 1 | https://waterforpeople.s3.amazonaws.com/images/3023180d-46b0-43f2-9092-b375fc2a2744.jpg | 2010 | Does Not Function | No |  |  |  | No | The water point is closed because people denied to pay for the water.When the rain falls down the water turbidity is so high.And the storage tank since its installation hasn't been cleaned. | Does Not Function | The water point is closed because people denied to pay for the water.When the rain falls down the water turbidity is so high.And the storage tank since its installation hasn't been cleaned.The water is present within the water point though people do not benefit its water | 63e98fc62b204fee45483785e6a62fe2
tq89-m84f-jcfs | 1 |  | J7 Rw11 | 1197470090 | 06-03-2017 17:15:09 CET | Bruce Uwonkunda | 06:15:39 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Bugarura | [5 empty] | 5000 | 3000 | 2000 | Yes | Piped Network -- Gravity Only |  | 2000 | Yes | Burura, Kijabagwe, Bijarura | Governement (District, WASAC) and Water For People |  | 5 | Spring | -1.9864102848206613 | 30.10285278749357 | 1514.3 | 2j95wgtg | https://waterforpeople.s3.amazonaws.com/images/1c0346b3-9e99-4749-8b8a-740a6684b695.jpg | Yes | 20 | Yes | 4 | https://waterforpeople.s3.amazonaws.com/images/ac8de0ff-67bd-47cc-97d6-a6f4f15e1840.jpg | "Springbox" --Intake Structure at a Spring | 2010 | Normal | 20 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/5bae3e30-9e13-41e0-86ae-3c9e9002f4f2.jpg | 2010 | Normal | 6500 | Yes | 2 | -1.986348890786168 | 30.102928716837567 | 1448.5 | 2j91qfl1 | https://waterforpeople.s3.amazonaws.com/images/5199eba0-8d99-495b-97f8-7e987c41b8cb.jpg | 2010 | Poor | Yes | 20 | Sedimentation Tank¦Pressure Break Tank¦Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/e16b6bf0-909f-42b3-a1f7-e0a5feb72714.jpg | 2010 | Does Not Function | Yes | 6 | https://waterforpeople.s3.amazonaws.com/images/9155ccf8-f216-4c04-93ba-c21ca54dc9c6.jpg | 2010 | Poor | 10000 | Yes | 1 |  | 2010 | Does Not Function | Yes | https://waterforpeople.s3.amazonaws.com/images/6346eb99-36ec-483f-b5db-a417abf4239d.jpg | 2010 | Does Not Function | Yes | https://waterforpeople.s3.amazonaws.com/images/cded57e5-0a93-4642-8f1e-ecad1836b494.jpg | Disinfection/Chlorination | 2010 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.9863147383568587 | 30.102892165245397 | 1515.1 | 2j8zy4ro | 14 | https://waterforpeople.s3.amazonaws.com/images/37574d1d-44e4-42f1-a2d3-6d7046b51029.jpg | 2010 | Does Not Function | Yes | 5 | 15 | bad maintenance | No | service providers perfomance | Does Not Function | need repair | a32bd02bc9b8b0bfb049b1a9d7d3d78
vqsq-j8e2-19wa | 1 |  | J7 Rw15 | 1217480049 | 12-03-2017 10:47:06 CET | Mukakarangwa Assoumpta | 00:13:18 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Karama |  |  | Bitete-Muvumu | 1316 |  | 121 | 40 | 81 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 3 | Spring | 1.8337482672601935 | 29.943433443706404 | 1749 | 2c8obmzu |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1000 |  | 2013 | Poor | 1000 | Yes | 4 | 1.8368127107947887 | 29.93457412501046 | 1635 | 2cdr3pn5 |  | 2013 | Normal | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse,Washout |  | 2013 | Poor | Yes | 1 |  | 2013 | Normal | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8561361892027648 | 29.923418925967866 | 1404.6 | 2d9pd6aq | 1 | https://waterforpeople.s3.amazonaws.com/images/9cb1ed37-fd96-4422-b566-2eca09935f20.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | Water point is functioning well, but around the water point needs some clean up | 77b12f227b6ac4babd766d1db75bc4f
ger3-63vd-75ru | 1 |  | J7 Rw24 | 1221860350 | 16-03-2017 06:03:20 CET | Kabalisa Manzi Christella | 00:05:41 | 2017 | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 14106 |  | 495 | 495 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | no problem | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Poor | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.736818324096243 | 30.03354173891469 | 1976.7 | 27sdd10v | 1 | https://waterforpeople.s3.amazonaws.com/images/f8331040-57e9-4cbd-ac90-a892fcc5bab2.jpg | 2012 | Normal | No |  |  |  | No | Water seller was not around | Normal | This Water Point/system functions well | 22b9aabd376493bf6c92598d1651dffe
7pfc-yrtm-hq6v | 1 |  | J7 Rw19 | 1201040677 | 10-03-2017 04:16:01 CET | Kayinamura Innocent | 00:31:40 | 2017 | Rwanda | Rulindo | Ngoma | Karambo | Butare |  |  | Shishi network |  |  | 122 | 44 | 78 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | Kigina | Governement (District, WASAC) and Water For People | poor management | 1 | Spring | -1.8097197675805605 | 29.979881122155494 | 1794.6 | 2b4xn0ly | https://waterforpeople.s3.amazonaws.com/images/98bfc00b-15a6-44bf-a36b-23353cf3ea88.jpg | No | 28 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/e6f1244e-19ab-4fc9-afdb-ba7a48522fa5.jpg | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 28 | Yes | 1 |  | 2014 | Normal | 700 | Yes | 2 | -1.809674509873321 | 29.981912015157096 | 1778.3 | 2b4v9a7f | https://waterforpeople.s3.amazonaws.com/images/19fd5448-f1fb-4d79-a16d-ac7c6f6f2a68.jpg | 2014 | Normal | No | [5 empty] | Yes | 1 |  | 2014 | Normal | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8095902973335831 | 29.981984611674967 | 1738.4 | 2b4qhtd7 | 4 | https://waterforpeople.s3.amazonaws.com/images/a02d660a-08b6-4682-abd1-93102a637099.jpg | 2014 | Poor | No |  |  |  | Yes |  | Poor | 1.Outlet of start chamber had been damaged 2. poor management | 6dc2dbf5f0b36355f366c4263a99664
kkg3-qywm-60fj | 1 |  | J7 Rw26 | 1209260143 | 12-03-2017 07:21:51 CET | Byukusenge Elie | 00:12:18 | 2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 20456 |  | 35 | 35 | 0 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank | This network serves four sectors Cyungo,Rukozo, Base,Base and Kinihira, It has some problems in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible because it serves many populations and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6240040793564425 | 29.948025945141403 | 1832.8 | 22lsy120 | 29 | https://waterforpeople.s3.amazonaws.com/images/42898fea-2775-4606-b6c1-9d86cdebbebb.jpg | 2011 | Normal | Yes | 10 | 30 | Bad tee connections of distribution reservoir in Rukozo centre which connected in Sakara Main reservoir and the types of pipeline needs rehabilitation | Yes |  | Poor | water tap in Rukozo Health Center is in good condition | 251b6f6dc5849eac9085634feb94b578
ufr6-t63u-xjt1 | 1 |  | J7 Rw15 | 1235770963 | 21-03-2017 15:58:29 CET | Mukakarangwa Assoumpta | 00:12:05 | 2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Magezi |  |  | Miyove-Kinihira | 10452 |  | 141 | 60 | 81 | Yes | Piped Network -- Gravity Only |  | 1989 | Yes | Taba | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse,Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6653680844061667 | 29.98545697649887 | 2016.1 | 24i7evda | 1 | https://waterforpeople.s3.amazonaws.com/images/64e017b8-cb96-4c30-9fdd-859409a2e1f9.jpg | 1989 | Poor | No |  |  |  | Yes |  | Poor |  | e3139edef0c36415b82d3c4dec72442a
5s9d-jtbk-snqu | 1 |  | J7 Rw15 | 1241800163 | 21-03-2017 16:40:24 CET | Mukakarangwa Assoumpta | 00:25:25 | 2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Gatembe |  |  | Miyove-Kinihira | 10452 |  | 149 | 60 | 89 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2021.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6719764965077701 | 29.980837208015384 | 1970.8 | 24t4ye74 | 1 | https://waterforpeople.s3.amazonaws.com/images/54e869cb-5f99-4126-ab5d-0a82ee843bb8.jpg | 1989 | Poor | No |  |  |  | Yes |  | Poor |  | f11d0769882e956997acc6b1c06e5b
1aqw-vnqj-2nk7 | 1 |  | J7 Rw15 | 1239070226 | 22-03-2017 18:04:28 CET | Mukakarangwa Assoumpta | 00:36:36 | 2017 | Rwanda | Rulindo | Kinihira | Butunzi | Barayi |  |  | Nyamagana-Kinihira |  |  | 151 | 80 | 71 | Yes | Piped Network with Pump |  | 2015 | Yes | All villages of Butunzi and Marembo cells and karambi village | Governement (District, WASAC) and Water For People | Is pumping network which is complex because it comes from Cyungo sector as gravity network and it transforms into pumping network at Kinihira sector. | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/e9e38614-699d-4dca-bc7a-fe9cb89047c7.jpg | 2015 | Normal | 1000 | Yes | 7 | -1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j | https://waterforpeople.s3.amazonaws.com/images/adfb4edc-5f1e-4f01-b15d-70863ddc4013.jpg | 2015 | Normal | Yes | 8 | Distribution Chamber¦Ventouse, Washout | https://waterforpeople.s3.amazonaws.com/images/8f89299b-0fb0-459d-a8cb-3d6361c6b075.jpg | 2015 | Normal | Yes | 3 | https://waterforpeople.s3.amazonaws.com/images/cad97ed7-e374-482a-827d-7baec4b7461e.jpg | 2015 | Normal | 6000 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/41794f80-81e7-4cac-9cb7-f6ae67881ad2.jpg | 2015 | Normal | Yes | https://waterforpeople.s3.amazonaws.com/images/e41e6571-b80e-442d-956a-ae48e8fd2280.jpg | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.671290209863282 | 29.962034763774913 | 1978.5 | 24s0gwx0 | 3 | https://waterforpeople.s3.amazonaws.com/images/f3544a97-9f1b-406d-8d11-9c7ad7181363.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | -Nyamagana-Kinihira network is a complex network which has its saurces from cyungo and comes as gravity network to kinihira sector after reaching Kinihira sector it transforms into pupmping network. -Is a network which has approximately 7km and serves 2 cells(Butunzi and Marembo) and Karambi village of Kinihira and is constructed in 2015. | c9f76f99d60816abcde624df2b4b9b8
2pau-yyey-s37m | 1 |  | J7 Rw10 | 1215400227 | 10-03-2017 13:01:19 CET | Tuyisenge Vianney | 00:05:13 | 2017 | Rwanda | Rulindo | Bushoki | Mukoto | Marembo |  |  | Marembo police station/Tare-Rusiga pumping | 9577 |  | 90 | 90 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This is a water point located in Marembo village at Police station | 10 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 4000 | No | [8 empty] | No | [5 empty] | Yes | 1 |  | 2015 | Normal | 8000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7175821821186639 | 29.899965424219335 | 2152.6 | 26wkgfp3 | 1 | https://waterforpeople.s3.amazonaws.com/images/5dc63503-8626-4090-8a4f-d2a9153b3675.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point located at Marembo/Bushoki police station | 1c65c46fee84e78d60c2f4bc7aa22d3
8dcv-mxn4-t13j | 1 |  | J7 Rw24 | 1253380247 | 28-03-2017 09:55:50 CEST | Kabalisa Manzi Christella | 00:07:23 | 2017 | Rwanda | Rulindo | Kisaro | Mubuga | Nyakarekare |  |  | Gahama Kisaro network | 10234 |  | 150 | 150 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6671501074688961 | 30.041830412153367 | 1945.4 | 24l5zh36 |  | Yes | 3 | Yes | 1 |  |  | 2012 | Normal | 3 | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 |  | https://waterforpeople.s3.amazonaws.com/images/67f88944-1b03-4b03-a2d1-fde7b10d0e3d.jpg | 2012 | Poor | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Poor | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6501645340429594 | 30.03223561470376 | 2192.3 | 23t2g082 | 1 | https://waterforpeople.s3.amazonaws.com/images/c52042a0-780a-48bc-a8bc-649839d29675.jpg | 2012 | Poor | No |  |  |  | No | System under rehabilitation | Poor |  | 6271768a11b47ddc7a9ded06fd7c8dc
hk84-x69x-kufw | 1 |  | J7 Rw19 | 1219490529 | 13-03-2017 06:50:42 CET | Kayinamura Innocent | 00:29:04 | 2017 | Rwanda | Rulindo | Ngoma | Munyarwanda | Kirungu |  |  | Kabarore-Ngoma-Nyabuko network | 8284 |  | 77 | 77 | 0 | Yes | Piped Network with Pump |  | 2014 | Yes | Nyabuko, Kagwa, Kiruri, Busizi, Ngaru, Kirungu, Kiboha and Kigina | Governement (District, WASAC) and Water For People | The network has 17 water points and it serves 8 villages | 4 | Spring | -1.8123357076877171 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦Collection Chamber | 2014 | Normal | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.8118879629206273 | 30.003478805087482 | 2031 | 2b8iu32a |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 4 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8346003212488884 | 30.006696262376302 | 1925.3 | 2ca3ixia | 17 | https://waterforpeople.s3.amazonaws.com/images/2bfd9d52-540e-43a4-a25e-fafa328fb1f7.jpg | 2014 | Poor | Yes | 1 | 10 | it was due to the road construction | Yes |  | Normal | - the network has 17 water points - Water points are in good operation conditions except the water point at the source that is damaged - 4 water points don't have water toady - the pipe are in good conditions - the pump is not working properly as it was expected during Design, today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy for the pump - the transformer at the pumping station doesn't offer the required energy for the pump - the anti-hammers of pumps are not functioning because of bad installation of pumping house - the system has 4 pumps units with two units pumping in one direction towards Nyabuko, towards Ngoma sector office - the suction tank is in bad physical condition | 9235c3e9a9f6eb10668f111749fc564
xjx5-xkr9-5ucg | 1 |  | J7 Rw24 | 1325190061 | 25-04-2017 16:49:20 CEST | Kabalisa Manzi Christella | 00:09:31 | 2017 | Rwanda | Rulindo | Kisaro | Murama | Kibingwe |  |  | Gahama Kisaro network | 10234 |  | 122 | 122 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6200005552162142 | 30.02248352098647 | 2050.5 | 22f6snnk | https://waterforpeople.s3.amazonaws.com/images/c06ddb1f-67a5-48c4-9a8e-a5dc726f327d.jpg | Yes | 120 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/aa32cc1f-46c2-4126-9106-e12716c16ace.jpg |  | 2012 | Normal | 120 | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 6 | -1.6200005552162142 | 30.02248352098647 | 2050.5 | 22f6snnk |  | 2012 | Normal | Yes | 12 |  |  | 2012 | Normal | Yes | 1 |  | 2012 | Normal | 30000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6198998948133962 | 30.022373002080094 | 2050 | 22f08vzz | 1 | https://waterforpeople.s3.amazonaws.com/images/79605d62-c7f0-4d35-a899-9d2d4d33a0a1.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 345dfdf9be5a9910e97a986b419b4c11
1j7n-xbpr-adn0 | 1 |  | J7 Rw10 | 1302850191 | 16-04-2017 23:08:28 CEST | Tuyisenge Vianney | 00:03:52 | 2017 | Rwanda | Rulindo | Buyoga | Karama | Karambo |  |  | Karambo water point/Nyirambuga pumping | 30604 |  | 165 | 165 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Operational and functional | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7035250682661154 | 29.975530233307936 | 1971.6 | 269bczqj | 1 | https://waterforpeople.s3.amazonaws.com/images/c3273dc7-48eb-45d1-b150-46b45c34f1dd.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Operational and functional | 3dd91ee7df23cd1ebde2818d2b1935
ns6v-u205-tjp9 | 1 |  | J7 Rw10 | 1277830075 | 05-04-2017 21:47:27 CEST | Tuyisenge Vianney | 00:06:04 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Tare |  |  | Tare-Rusiga pumping system/Water point at Tare | 9577 |  | 109 | 109 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Tare water point connected on Tare-Rusiga pumping system.It is well operating | 1 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6701984188962895 | 29.890771754997264 | 1832 | 24q6z7tn | 1 | https://waterforpeople.s3.amazonaws.com/images/883a18ce-021b-478b-b40d-f1e31f9437a3.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Tare water point connected on Tare-Rusiga pumping system.It is well operating | 383c4914b18dc9a365c8858b73816
ampm-21m3-6cmx | 1 |  | J7 Rw19 | 1242950082 | 23-03-2017 08:09:12 CET | Kayinamura Innocent | 00:10:18 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Kigarama |  |  | Mutagata motorised network | 26296 |  | 169 | 57 | 112 | Yes | Piped Network with Pump |  | 2016 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7815330300212935 | 30.04641783994509 | 1903.9 | 29ubvieo | 64 | https://waterforpeople.s3.amazonaws.com/images/65443f15-a7f0-4b6a-9957-e5b30ffacb7d.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 12c163176ae5f1c848b2546573b954
e0jq-weya-hcwh | 1 |  | J7 Rw24 | 1226630216 | 15-03-2017 15:45:23 CET | Kabalisa Manzi Christella | 00:16:27 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kamatongo |  |  | 0 | 6572 |  | 1125 | 0 | 1125 | Yes | Piped Network with Pump |  | 2014 | No |  | Governement (District, WASAC) and Water For People | Water doesn’t reach destination | 3 | Spring | 1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Does Not Function | 4.5 | Yes | 2 |  | 2009 | Normal | 3000 | Yes | 3 | -1.7555179528295524 | 30.03970289656239 | 1690.5 | 28napmb1 |  | 2014 | Does Not Function | Yes | 8 |  |  | 2014 | Does Not Function | Yes | 2 |  | 2014 | Does Not Function | 3000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7611463663575349 | 30.049963770592537 | 1527.4 | 28wlwnyr | 1 | https://waterforpeople.s3.amazonaws.com/images/b2a4b2e5-b7f9-4c76-a5ce-e8bc05510a07.jpg | 2014 | Does Not Function | Yes | 365 | 0 | Since the system was built no water is flowing | No | Water is not Flowing | Does Not Function | System is not working | 613d5246bcc8c666b03184b1c0d3b698
ttar-jtj1-me57 | 1 |  | J7 Rw10 | 1301910066 | 15-04-2017 22:00:32 CEST | Tuyisenge Vianney | 00:07:57 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Water point at Nyagahondo source1/Nyagahondo gravity system | 844 |  | 228 | 228 | 0 | Yes | Piped Network -- Gravity Only |  | 2010 | No |  | Caritas | The water point is operational though its water tap stand was removed and damaged | 2 | Spring | -1.7298781428197503 | 29.909858739201194 | 2099.3 | 27gw668q | https://waterforpeople.s3.amazonaws.com/images/8bda8449-3bbe-4333-9aaf-66ad3c419187.jpg | No | 30 | No | [5 empty] | 30 | Yes | 1 |  | 2010 | Normal | 100 | Yes | 1 | -1.7298968446980312 | 29.90989974161766 | 2081.7 | 27gxd1ga | https://waterforpeople.s3.amazonaws.com/images/2e353508-b683-4005-857e-a5dbe6523c26.jpg | 2010 | Normal | No | [5 empty] | Yes | 2 |  | 2010 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7300237826891116 | 29.910016289209644 | 2061.7 | 27h53obg | 1 | https://waterforpeople.s3.amazonaws.com/images/b256f262-2b11-4e90-bfef-ad45cc9b1624.jpg | 2010 | Normal | No |  |  |  | Yes |  | Normal | The water point is operational though its water tap stand was removed and damaged | f7ccf6422fe6479b50de3b988bec364
r85r-uyn4-dspe | 1 |  | J7 Rw10 | 1238570100 | 03-01-2015 00:41:30 CET | Tuyisenge Vianney | 00:07:23 | 2017 | Rwanda | Rulindo | Tumba | Taba | Nyirataba |  |  | Nyirataba1 water point/Nyirambuga pumping | 30604 |  | 169 | 169 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | It's a water point located at Nyirataba and it operates and somehow privately managed by the one called Munyaneza | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7322699443413452 | 29.96077139345786 | 2134.3 | 27kugs7r | 2 | https://waterforpeople.s3.amazonaws.com/images/f8f3dbd8-2062-4dc9-9b81-f3de5ade4acf.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | It's a water point located at Nyirataba and it operates and somehow privately managed by the one called Munyaneza | aa3d85d47d7d7d64e7a917d33c1c21f
pnj0-ykqg-ffh1 | 1 |  | J7 Rw10 | 1230340226 | 03-01-2015 02:09:09 CET | Tuyisenge Vianney | 00:02:53 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Bukiga water point/Nyirambuga pumping | 30604 |  | 169 | 169 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Everything operates normally the water is available everyday | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.694061527983303 | 29.94139492917054 | 2106.9 | 25to4x79 | 2 | https://waterforpeople.s3.amazonaws.com/images/c64a3607-7daa-4276-8e1d-5fe58b8fe78f.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Everything operates normally the water is available everyday with one tap valve closed | a3c519191b9bde56417dd034253a8b6
ng76-9kdx-1qda | 1 |  | J7 Rw23 | 1212010849 | 12-03-2017 18:40:59 CET | Rugirangoga Augustin | 00:19:34 | 2017 | Rwanda | Rulindo | Base | Gitare | Gisiza |  |  | Rwicanyoni | 698 |  | 116 | 115 | 1 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | kirwa gatete gisiza | Governement (District, WASAC) and Water For People | there is no problem with this network | 2 | Spring | -1.6644377224987001 | 29.903649586570488 | 1928 | 24go1jh8 |  | Yes | 10 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 10 | Yes | 1 |  | 2016 | Normal | 8600 | Yes | 3 | -1.6605194594779042 | 29.90927074216649 | 1808.8 | 24a6nmdw |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6523017774737847 | 29.90190494758474 | 1771.6 | 23wluqob | 2 | https://waterforpeople.s3.amazonaws.com/images/476f580f-8eea-40b9-8d68-00ce2fbd4a4b.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | no problem the network has | d5bf88ea27587825388774f5ec23f646
gn36-pp1x-gqjq | 1 |  | J7 Rw10 | 1304640049 | 15-04-2017 21:57:59 CEST | Tuyisenge Vianney | 00:11:58 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Water point near Gitera/Nyagahondo water gravity system | 844 |  | 228 | 228 | 0 | Yes | Piped Network -- Gravity Only |  | 2010 | Yes | Remera,Rulindo,Buvumo and Budaha | Caritas | The water point is operational though its water tap stand was removed and damaged | 1 | Spring | -1.7300896141913849 | 29.913647647456465 | 1839.3 | 27h8o9z4 | https://waterforpeople.s3.amazonaws.com/images/87e5b4bd-4eed-4966-b26e-37fcf03a06b1.jpg | Yes | 30 | No | [5 empty] | 30 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/e25f4c00-c082-46c2-bc94-09b05139276a.jpg | 2010 | Normal | 1000 | Yes | 1 | -1.730005663406602 | 29.913458261407513 | 1815.8 | 27h3wt4u | https://waterforpeople.s3.amazonaws.com/images/4eb711ad-ca2b-4348-b7c8-8f24d2e19f4a.jpg | 2010 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7300764072375148 | 29.91382939071082 | 1931.1 | 27h82ude | 1 | https://waterforpeople.s3.amazonaws.com/images/8ff6a3db-dc16-4a2e-bc15-2647dd77e396.jpg | 2010 | Normal | No |  |  |  | Yes |  | Normal | The water point is operational though its water tap stand was removed and damaged | e7bbff30c7c16e5d81c2b450cfbcda
mwd8-0k7d-tbpv | 1 |  | J7 Rw19 | 1215030207 | 09-03-2017 18:12:19 CET | Kayinamura Innocent | 00:13:06 | 2017 | Rwanda | Rulindo | Ngoma | Karambo | Karambi |  |  | Gahama network |  |  | 117 | 29 | 88 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | Jyambere | Governement (District, WASAC) and Water For People | two water points had been damaged | 1 | Spring | -1.824762618736981 | 29.979015616308 | 1718 | 2bttoe1a |  | No | 15 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 15 | Yes | 1 |  | 2014 | Normal | 1800 | Yes | 2 | -1.8248055237148662 | 29.983823341228508 | 1657.7 | 2btw24hq |  | 2014 | Normal | Yes | 1 | Distribution Chamber |  | 2014 | Normal | Yes | 1 |  | 2014 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.825080041193721 | 29.983972627920718 | 1626.4 | 2bucq9fj | 5 | https://waterforpeople.s3.amazonaws.com/images/9d40e20b-4117-4084-a2f1-0a0604d943f2.jpg | 2014 | Poor | No |  |  |  | Yes |  | Poor | Two water points have broken parts and source stayed | 6176216c62e68dbe6c6a1375f27d17b
w4by-b9fr-63wg | 1 |  | J7 Rw26 | 1212100066 | 12-03-2017 07:08:55 CET | Byukusenge Elie | 00:09:52 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Kivomo |  |  | Nyamagana | 20456 |  | 78 | 70 | 8 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank | This network serves four sectors Cyungo,Rukozo, Base,Base and Kinihira, It has some problems in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible because it serves many populations and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6530926323390507 | 29.955032607753225 | 1804.6 | 23xwvzvi | 29 | https://waterforpeople.s3.amazonaws.com/images/dea4d485-470c-4454-9a50-7f5a50343676.jpg | 2011 | Poor | Yes | 10 | 25 | The bad connection to the distribution line and the types of pipeline has needs to be replaced. | No | The pipeline connecting to the reservoir located at E.P.Mutara has been damaged | Poor | centre Kivomo | 30691e6049659fa617f1e8dfecf356
a98p-d8he-mf73 | 1 |  | J7 Rw26 | 1206550195 | 02-01-2015 05:52:39 CET | Byukusenge Elie | 00:06:40 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Kabingo |  |  | Nyamagana | 20456 |  | 65 | 60 | 5 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6477768801369446 | 29.92143711352921 | 1779.7 | 23p45dse | 29 | https://waterforpeople.s3.amazonaws.com/images/31afb055-564a-4ebc-b811-44fd57b8480f.jpg | 2011 | Normal | No |  |  |  | Yes |  | Poor | Water are available at centre Kabingo | 115e6fb3bb934929f6fc29f4fd07398
h3a4-hes8-yq91 | 1 |  | J7 Rw23 | 1196590671 | 07-03-2017 21:14:55 CET | Rugirangoga Augustin | 00:30:14 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Kiruli |  |  | Migogo | 558 |  | 223 | 200 | 23 | Yes | Piped Network -- Gravity Only |  | 2009 | Yes | kiruli bukangano kabahama rubanda | Italians(LAKE ANGELS) | This system is functional but needs Rehabilitation | 1 | Spring | -1.632311918504939 | 29.90125938622729 | 1810.2 | 22zjp8ec |  | No | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2009 | Poor | 20 | Yes | 2 |  | 2009 | Poor | 3000 | Yes | 3 | -1.6350822337877793 | 29.89531663121816 | 1775.7 | 2344max5 |  | 2009 | Poor | No | [5 empty] | Yes | 2 |  | 2012 | Poor | 3000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6405299528718018 | 29.894628212028383 | 1727.2 | 23d4i402 | 1 |  | 2009 | Poor | No |  |  |  | Yes |  | Poor | System is working but it has some issues | ed907b50b37fb54034bd3268525dbaf8
6y2q-hvwk-cg0u | 1 |  | J7 Rw19 | 1215030206 | 09-03-2017 18:12:00 CET | Kayinamura Innocent | 00:19:34 | 2017 | Rwanda | Rulindo | Ngoma | Karambo | Karambi |  |  | Gahama network |  |  | 117 | 25 | 92 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | Jyambere | Governement (District, WASAC) and Water For People | two water point had been damaged | 1 | Spring | -1.824762618736981 | 29.979015616308 | 1718 | 2bttoe1a |  | No | 15 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 15 | Yes | 1 |  | 2014 | Normal | 1800 | Yes | 2 | -1.8248055237148662 | 29.983823341228508 | 1657.7 | 2btw24hq |  | 2014 | Normal | Yes | 1 | Distribution Chamber |  | 2014 | Normal | Yes | 1 |  | 2014 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8246372836543814 | 29.98423633493774 | 1606.4 | 2btlxr7m | 5 | https://waterforpeople.s3.amazonaws.com/images/fdbd5a65-4815-404c-8018-ade61fec17b8.jpg | 2014 | Does Not Function | No |  |  |  | Yes |  | Poor | Two water points have broken parts and source stayed | 27637a482f9832892ca4b9cfe14fe025
1wp5-6ssd-u0hg | 1 |  | J7 Rw23 | 1321070106 | 23-04-2017 14:42:15 CEST | Rugirangoga Augustin | 00:30:20 | 2017 | Rwanda | Rulindo | Buyoga | Ndarage | Kagozi |  |  | ndarage |  |  | 155 | 130 | 25 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | gahondo kagozi gikingo karambi | Governement (District, WASAC) and Water For People | This Systems has a problem at the source has two sources that are blocked due to roots from nearby bushes and trees. | 1 | Spring | -1.6829614865475908 | 30.031434012077444 | 1962 | 25bb9sey |  | Yes | 60 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 60 | Yes | 1 |  | 2014 | Normal | 5000 | Yes | 5 | -1.6902852583901373 | 30.03414816539013 | 1811.8 | 25nf3391 |  | 2014 | Normal | No | [5 empty] | Yes | 1 |  | 2014 | Normal | 6700 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7039371017766145 | 30.0406973201015 | 1583.9 | 269zrs1i | 1 | https://waterforpeople.s3.amazonaws.com/images/5678ab58-d6b8-4ccc-a2a3-b2426d699cf9.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | This system doesn’t function well, and the Water Point is new | b128c6918233f39015289057ef461154
x65j-8fr2-pk3c | 1 |  | J7 Rw15 | 1211680086 | 08-03-2017 19:36:27 CET | Mukakarangwa Assoumpta | 00:09:52 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Nyarushinya |  |  | kinywamagana pumping network | 6436 |  | 238 | 150 | 88 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8619875921623514 | 29.98290954678947 | 1656.6 | 2djdnrn9 | 1 | https://waterforpeople.s3.amazonaws.com/images/8e0a30ba-20c5-4d5c-a096-928ef546c54b.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | 77c57d1f7ee5d2c59dc43705e961c61
w0am-uy6p-v2ap | 1 |  | J7 Rw15 | 1210500542 | 09-03-2017 21:46:11 CET | Mukakarangwa Assoumpta | 00:10:23 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Rwahi |  |  | Bitete-Rwahi network | 1316 |  | 450 | 450 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.8336417737979869 | 29.94346668826428 | 1815.5 | 2c8iday2 |  | Yes | 12 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 |  | 2013 | Normal | 600 | Yes | 6 | 1.8427360326225883 | 29.938932546871705 | 1676.5 | 2cnjkbst |  | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8598036998838425 | 29.92658830368411 | 1448.5 | 2dfrv9c1 | 1 | https://waterforpeople.s3.amazonaws.com/images/2bd3cb19-48ec-42c1-b767-b8be21f0cfbe.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | water point is for Rwahi primary school. | 91f944124c89fee23c95578871ba55b
6pjm-tvng-retg | 1 |  | J7 Rw10 | 1281440049 | 05-04-2017 19:22:56 CEST | Tuyisenge Vianney | 00:10:58 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Gifuba |  |  | Rutare-Nyirangarama gravity system/Water point at ADEPR NYIRANGARAMA | 726 |  | 108 | 108 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | Government | This water point located at ADEPR Nyirangarama is connected to Rutare-Nyirangarama gravity system,which was constructed late 1960s. | 1 | Spring | -1.6705676828047722 | 29.878696276428556 | 2067 | 24qt0942 |  | Yes | 20 | No | [5 empty] | 20 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6644537967869457 | 29.88497050243692 | 1778.9 | 24gp8ejl | 1 | https://waterforpeople.s3.amazonaws.com/images/102c186a-4592-4ffa-9116-f03caaff2e99.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water point located at ADEPR Nyirangarama is connected to Rutare-Nyirangarama gravity system,which was constructed late 1960s. | 18db6da4fe783c52c9a7aabc222173
2udg-5gx8-duc6 | 1 |  | J7 Rw8 | 1242950097 | 22-03-2017 20:20:27 CET | Amani Desire | 00:22:47 | 2017 | Rwanda | Rulindo | Murambi | Mvuzo | Munyinya |  |  | Mutagata Motorised Network | 26296 |  | 130 | 130 | 0 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.801852228450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release chamber |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.786551377615702 | 30.02214389372764 | 2029.7 | 2a2mr3wd | 64 |  | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | 504559e0da58946aa7488a1da15c9bf3
j28f-gb9k-ugsa | 1 |  | J7 Rw26 | 1213140151 | 12-03-2017 07:10:57 CET | Byukusenge Elie | 00:11:48 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Kivomo |  |  | Nyamagana | 20456 |  | 700 | 700 | 0 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank | This network serves four sectors Cyungo,Rukozo, Base,Base and Kinihira, It has some problems in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible because it serves many populations and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.652616326730594 | 29.954468736719612 | 1823.9 | 23x4b6u0 | 29 | https://waterforpeople.s3.amazonaws.com/images/57ca9a6d-52c3-471b-b90e-82b79dc5c943.jpg | 2011 | Normal | Yes | 10 | 22 | Bad tee connections and the types of pipeline needs rehabilitation | Yes |  | Poor | Water tap serves students and staff in G.S.Mutara and It is in good condition | 1e77fc668f9e2ffa6128bbe08f87d2bb
u211-jfar-2mt6 | 1 |  | J7 Rw10 | 1302730104 | 15-04-2017 23:35:15 CEST | Tuyisenge Vianney | 00:08:56 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Gifumba |  |  | Source Murungurira/Murungurira-Nyakariba gravity system |  |  | 188 | 188 | 0 | Yes | Piped Network -- Gravity Only |  | 2010 | No |  | Local government | The water point is nolonger operationa.The GTS[ Former water management private operator ] has stoped working on the maintenance issue saying that District will tackle the issue | 2 | Spring | -1.8402167628378279 | 29.95851325730038 | 1898.8 | 2cjdj3i9 | https://waterforpeople.s3.amazonaws.com/images/3dbd0a71-88e7-4a89-a905-9a3919cc607b.jpg | No | 50 | No | [5 empty] | 50 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/1a7cecad-6a32-4f59-a9e4-3ae1620cfed6.jpg | 2010 | Poor | 100 | Yes | 1 | -1.8404101842800151 | 29.95893517009418 | 1839.9 | 2cjpfrlx | https://waterforpeople.s3.amazonaws.com/images/55755ef2-9bce-4845-a3a5-5bf40599bab8.jpg | 2010 | Poor | Yes | 1 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/0915c791-cb5b-4710-926e-21e15e156703.jpg | 2010 | Does Not Function | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8403879546069806 | 29.95892530951682 | 1824.7 | 2cjnngsl | 1 | https://waterforpeople.s3.amazonaws.com/images/5a699529-c16f-4935-8cbd-37477ce54f35.jpg | 2010 | Poor | No |  |  |  | No | The water point is nolonger operationa.The GTS[ Former water management private operator ] has stoped working on the maintenance issue saying that District will tackle the issue | Poor | The water point is nolonger operationa.The GTS[ Former water management private operator ] has stoped working on the maintenance issue saying that District will tackle the issue | 6477ffa96ce735cdba6711982377a245
pfc1-fc3d-10up | 1 |  | J7 Rw7 | 1240250075 | 24-03-2017 08:54:47 CET | Safari Bosco | 00:26:45 | 2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Kabeza |  |  | marenge | 5544 |  | 120 | 120 | 0 | Yes | Piped Network with Pump |  | 2016 | Yes | gacyamo,rusenyi,kabeza,rusenyi,kigomwa,marenge,mutagata,gasharu,kabuga,marembo | Governement (District, WASAC) and Water For People | People are enjoying the services and use this water except in the rain season | 2 | Spring | -1.8285370486353667 | 30.0634607908055994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 7 | -1.8228065710007637 | 30.055376173807932 | 1827.2 | 2bqkzg21 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8374251200473661 | 30.052529985710212 | 1673.2 | 2cerf6gd | 2 | https://waterforpeople.s3.amazonaws.com/images/92bce61e-0f50-4ff0-83de-cdc1011159ef.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | b87af1b893f349797a643b7dbcf69e
gce0-cg0m-e6m7 | 1 |  | J7 Rw10 | 1236430172 | 02-01-2015 23:42:17 CET | Tuyisenge Vianney | 00:05:08 | 2017 | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point at Gisha church/Nyirambuga Pumping | 30604 |  | 133 | 133 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | The water point at Gisha church operates well though one water tap valve was damaged it's better to refix a new one. | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7458156847277226 | 29.966060623239272 | 2088.4 | 287974y4 | 2 | https://waterforpeople.s3.amazonaws.com/images/81704106-a908-44b2-aa52-ab80193674d0.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The water point at Gisha church operates well though one water tap valve was damaged it's better to refix a new one. | 59fcdc5abbc7dcf365a235a10a46d98
x8sw-066s-u7qy | 1 |  | J7 Rw15 | 1217630745 | 12-03-2017 13:01:14 CET | Mukakarangwa Assoumpta | 00:08:04 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kagunda |  |  | Muvumu- Taba |  |  | 94 | 35 | 59 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.8242130164596562 | 29.931083430301516 | 1700.7 | 2bswxje6 |  | Yes | 25 | No | [5 empty] | 25 | Yes | 1 |  | 2013 | Normal | 800 | Yes | 3 | 1.828985219687556 | 29.926634523104315 |  | 2c0sxawy |  | 2013 | Poor | Yes | 9 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 7500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.838213649254746 | 29.924069437343316 | 1604.9 | 2cg2ge94 | 1 | https://waterforpeople.s3.amazonaws.com/images/ea605c43-8d03-417a-be61-a02a013069a9.jpg | 2013 | Normal | Yes | 1 | 3 | Those rehabilitating Rushinya source had strayed it | Yes |  | Poor |  | 2aa4010d0d1e921d89a8277842517f9
ujvs-bucd-rayx | 1 |  | J7 Rw15 | 1205890695 | 09-03-2017 17:12:10 CET | Mukakarangwa Assoumpta | 00:07:26 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Nyamirembe |  |  | kirikumuryango network |  |  | 256 | 120 | 136 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.976612576966872 | 1632.8 | 2e5fw0l2 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 10000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.9018907604776734 | 29.97490790354944 | 1367 | 2fddsqw5 | 1 | https://waterforpeople.s3.amazonaws.com/images/1e2e8f55-310a-4db8-b588-058a9f4ad866.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 1062ca60333ea021a9783eed209dd8f0
rag8-5ux2-chnx | 1 |  | J7 Rw15 | 1235670570 | 22-03-2017 19:19:56 CET | Mukakarangwa Assoumpta | 00:07:49 | 2017 | Rwanda | Rulindo | Kinihira | Butunzi | Ndorandi |  |  | Nyamagana-Kinihira |  |  | 139 | 50 | 89 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦Ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6697484304472705 | 29.94861109532155 | 1911.2 | 24pg6q1q | 2 | https://waterforpeople.s3.amazonaws.com/images/fa5ece81-3e2c-40ec-a482-0ad8932b694b.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | fe77153ff43e33269b8bf15419b9299e
2px3-t9b6-sj8m | 1 |  | J7 Rw10 | 1315700063 | 20-04-2017 18:08:52 CEST | Tuyisenge Vianney | 00:06:44 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | Water point chez Nsabayezu/Kivomo-Ntakara gravity |  |  | 198 | 198 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Not operational | 2 | Spring | -1.827334932521246 | 29.95090160939001 | 1943.1 | 2by2osad |  | Yes | 50 | No | [5 empty] | 50 | No | [5 empty] | No | [8 empty] | Yes | 1 | water point valve chamber | https://waterforpeople.s3.amazonaws.com/images/3e7d9b3d-b18a-4253-81b4-6afd5eba7278.jpg | 2015 | Does Not Function | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8196613151268473 | 29.95951446038552 | 1745.3 | 2ble1bd7 | 1 | https://waterforpeople.s3.amazonaws.com/images/57e04bfa-0633-44b2-bbcd-6ea719165fc4.jpg | 2015 | Does Not Function | No |  |  |  | No | not operational | Does Not Function | Not operational water point damaged.And the pipeline got broken and no maintenance has been done till now.People are fetching fro swamps,or Ntakara spring | 3c654e3c68b8832be65c1a3068b35be
es9b-971w-as6n | 1 |  | J7 Rw10 | 1225600369 | 13-03-2017 22:06:38 CET | Tuyisenge Vianney | 00:08:19 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Kivomo |  |  | Kivomo water point/Buramira gravity | 1255 |  | 127 | 127 | 0 | Yes | Piped Network -- Gravity Only¦Private Tap with Piped Supply |  | 2015 | No |  | GoR | The water point operates well | 1 | Spring | -1.6883400866741962 | 29.91133431277988 | 1897.9 | 25k7kyy1 | https://waterforpeople.s3.amazonaws.com/images/4a3a61d7-c0aa-4220-be44-a3a093462c2a.jpg | Yes | 30 | No | [5 empty] | 30 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6748128011920669 | 29.921076822689624 |  | 24xu1hje | 1 | https://waterforpeople.s3.amazonaws.com/images/b0af6ff6-e0b7-440f-89c4-78d3e6047bd9.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The water point functions well | f7fdd07f19e4dd1f4fddacdc1ef646
tqf7-17uu-y02r | 1 |  | J7 Rw15 | 1199341048 | 09-03-2017 17:05:26 CET | Mukakarangwa Assoumpta | 00:06:46 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Rweya |  |  | kirikumuryango network |  |  | 212 | 90 | 122 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 10000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.9037596986719323 | 29.97249207322494 | 1370.4 | 2fggjde4 | 1 | https://waterforpeople.s3.amazonaws.com/images/05440010-06e3-463c-b3aa-fab58f934add.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | d2e8bef2f4a09166d8f5e1f2ec692
nnt3-k8bs-9x2q | 1 |  | J7 Rw10 | 1238580051 | 02-01-2015 23:38:00 CET | Tuyisenge Vianney | 00:13:43 | 2017 | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point 2 at Gisha/Nyirambuga pumping | 30604 |  | 133 | 133 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This water tap near Gisha operates well with two taps stands.Its water storage tank valve chamber does nolonger have a cover.Float valve of water storage while being repaired got broken and in result when water gets full is shed away in disorder.The water system private operator does not cooperate with people which ends in not putting everything in place | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.748993706633349 | 29.966446426723415 | 2122.5 | 28ciizbk | https://waterforpeople.s3.amazonaws.com/images/7dfb2a94-7b9d-4af0-abd5-877d303e12ef.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7490810247011976 | 29.96631982981142 | 2096.5 | 28cnvvrj | 2 | https://waterforpeople.s3.amazonaws.com/images/8d4f279d-4ef9-4948-b1f8-fed78d47ed08.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap near Gisha operates well with two taps stands.Its water storage tank valve chamber does nolonger have a cover.Float valve of water storage while being repaired got broken and in result when water gets full is shed away in disorder.The water system private operator does not cooperate with people which ends in not putting everything in place | bda9bdc37f415b4c1caa0e3c0ade6b3
tas3-5y93-pa8b | 1 |  | J7 Rw24 | 1248070208 | 28-03-2017 10:17:27 CEST | Kabalisa Manzi Christella | 00:06:53 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Gitambi |  |  | Rwamugaza network | 14106 |  | 230 | 230 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 1 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7896334632641964 | 30.114952036571975 | 1596.2 | 2a7q4mxp | 1 | https://waterforpeople.s3.amazonaws.com/images/f4a6a4ab-915b-4b0a-9af8-a51b1ebed15c.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | f98c1891cad4b1b82e527968ed56287
ay3w-fw8a-c4h4 | 1 |  | J7 Rw23 | 1244270049 | 25-03-2017 20:47:10 CET | Rugirangoga Augustin | 01:59:48 | 2017 | Rwanda | Rulindo | Buyoga | Butare | Giko |  |  | Kiduha | 0 |  | 151 | 130 | 21 | Yes | Piped Network -- Gravity Only |  | 2007 | Yes | kankanga giko gasave | Governement (District, WASAC) and Water For People | System's source doesn’t produce enough water | 1 | Spring | -1.692136727874054 | 30.02146392212493 | 1866.9 | 25qh8a2e |  | No | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Poor | 20 | Yes | 1 |  | 2007 | Poor | 2200 | Yes | 3 | -1.6932117321635163 | 30.026191374639453 | 1765.8 | 25s9j3fp |  | 2007 | Poor | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.700810215069687 | 30.02866094240071 | 1635.7 | 264u0j7i | 2 | https://waterforpeople.s3.amazonaws.com/images/a3aac7f7-c993-4499-865e-471bf499efbe.jpg | 2007 | Normal | No |  |  |  | Yes |  | Poor | System needs rehabilitation | 96a0933c8aab44f6a17617f777d256b0
ehrb-gpt7-k6uf | 1 |  | J7 Rw26 | 1201690428 | 02-01-2015 05:48:18 CET | Byukusenge Elie | 00:13:42 | 2017 | Rwanda | Rulindo | Cyungo | Rwili | Karambi |  |  | Nyamagana | 20456 |  | 80 | 20 | 60 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.60523988557085 | 29.929967059128266 | 1943 | 21qrfeg3 | 29 | https://waterforpeople.s3.amazonaws.com/images/3e08bcb2-7dea-42e9-9c27-722774301b97.jpg | 2011 | Normal | Yes | 7 | 60 | bad connection of tee junctions even not well located main distribution reservoir at Sakara Village | No | The distribution reservoir does not supply water in this transmission line because of bad connection of tee junctions towards Gatovu | Poor | It needs some rehabilitation | 18c0d1122fb11847633a3245bb96c2b
5vsg-s6nw-ubmj | 1 |  | J7 Rw10 | 1319850054 | 21-04-2017 16:34:16 CEST | Tuyisenge Vianney | 00:07:01 | 2017 | Rwanda | Rulindo | Rusiga | Taba | Bitare |  |  | Bitare-Gahondo sources catchment area | 9577 |  | 113 | 113 | 0 | Yes | Piped Network -- Gravity Only |  | 2017 | No |  | Government of Rwanda | operational but on conduction line outlet while waiting water storage tanks construction works completion to connect it. | 2 | Spring | -1.8240400967512485 | 29.93064274686712 | 1670 | 2bsmt63u | https://waterforpeople.s3.amazonaws.com/images/ad159275-3cf4-4932-90e8-f223cac3e6c8.jpg | Yes | 10 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/f2174da7-236d-4048-93dd-0c3d9a827c46.jpg | "Springbox" --Intake Structure at a Spring | 2017 | Normal | 10 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/c2a16b7a-87ac-4d0b-8c3e-bc4edbdd8a0f.jpg | 2017 | Normal | 400 | Yes | 2 | -1.8238276965916431 | 29.93008258368084 | 1649.4 | 2bs9pmsk | https://waterforpeople.s3.amazonaws.com/images/77de11b2-8d76-4929-83a4-12bb096db8ff.jpg | 2017 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8240029157247801 | 29.930340925965883 | 1634.2 | 2bskffon | 2 | https://waterforpeople.s3.amazonaws.com/images/36f4091e-fe4d-4011-baaa-75e458edbe46.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | operational but on conduction line outlet while waiting water storage tanks construction works completion to connect it. | 8cd69f6ee82c0852da68f7fbeb73f4c
r65s-pkp9-ww8n | 1 |  | J7 Rw8 | 1210050087 | 10-03-2017 10:23:31 CET | Amani Desire | 00:16:08 | 2017 | Rwanda | Rulindo | Ngoma | Kabuga | Nyabuko |  |  | Kabarore-Ngoma-Nyabuko network | 8284 |  | 122 | 25 | 97 | Yes | Piped Network with Pump |  | 2014 | Yes | nyabuko,kagwa,kiruli,busizi,ngaru,kirungu,kiboha,kigina | Governement (District, WASAC) and Water For People | The network has 17 water points | 4 | Spring¦Groundwater (well, etc.) | -1.8123357076877171 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦collection chamber | 2014 | Poor | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.808716485895084 | 29.973362007273437 | 2001 | 2b3a3o2d |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8220001164704407 | 29.976031383317068 | 1909.3 | 2bp9cr1s | 17 | https://waterforpeople.s3.amazonaws.com/images/2af4d222-002f-4242-9f46-c575986a90e0.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | -the network has 17 water points - water points are in good operational conditions except the water point at the source that is damaged -4 water points don't have water today -the pipes are in good operational conditions -the pump is not working properly as it was expected during Design ,Today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy -the transformer at the pumping station doesnt offer the required energy for the pump - the anti hammers of pump are not functioning because of bad installation of pumping house -the system has two pumps with four units with two units pumping in one direction towards Nyabuko and other two in an other direction towards ngoma sector office -The suction tank is in bad physical conditions | 72eada2512d22aec9620fafbd722733
53nd-fyfm-vd7w | 1 |  | J7 Rw10 | 1213211699 | 13-03-2017 21:39:13 CET | Tuyisenge Vianney | 00:04:44 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Kigamba2 water point/Rutomvu gravity | 3015 |  | 172 | 172 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | water point damaged not operating | 1 | Spring | -1.677891751247546 | 29.90118126071259 | 1802.6 | 252xezpf |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.696211810741497 | 29.90703297314582 | 1736.6 | 25x853zy | 1 | https://waterforpeople.s3.amazonaws.com/images/22ded9fd-fc26-4f1b-8425-a3935029e1af.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | The water point does nolonger operate | e1cae1c4888e0ea7d9431d4fcb3e562
4dfs-yt1j-6nrv | 1 |  | J7 Rw15 | 1211480539 | 09-03-2017 22:00:18 CET | Mukakarangwa Assoumpta | 00:09:25 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyarunyinya |  |  | Bitete-Rwahi network | 1316 |  | 132 | 35 | 97 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.8336417737979869 | 29.94346668826428 | 1815.5 | 2c8iday2 |  | Yes | 12 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 |  | 2013 | Normal | 600 | Yes | 6 | 1.8427360326225883 | 29.938932546871705 | 1676.5 | 2cnjkbst |  | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8454667038251817 | 29.93742467149026 | 1644.6 | 2cs23nxq | 1 | https://waterforpeople.s3.amazonaws.com/images/dd040404-d62e-4fc3-87e4-6768a0462567.jpg | 2013 | Poor | No |  |  |  | Yes |  | Normal |  | a92eb9f9f4a471ec173feea76e4144
a2ju-bv6v-mgsq | 1 |  | J7 Rw10 | 1212340916 | 13-03-2017 21:27:57 CET | Tuyisenge Vianney | 00:07:42 | 2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Gitaba |  |  | Ngarama water point/Rutomvu gravity | 3015 |  | 110 | 110 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | Water pointing operating but taps are damaged. | 1 | Spring | -1.677891751247546 | 29.90118126071259 | 1802.6 | 252xezpf |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | Yes | 1 | -1.6873121081806874 | 29.902879802563163 | 1798.5 | 25ii9bkk | https://waterforpeople.s3.amazonaws.com/images/a810d168-519c-4dcf-a039-d5e99c56b962.jpg | 2013 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.687304750963793 | 29.90267734819043 | 1767.9 | 25ihnvyq | 1 | https://waterforpeople.s3.amazonaws.com/images/036c1adc-613c-4a56-9442-b82aa78b3fb0.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | The water operates in moderate conditions. It needs to be rehabilitated for better conditions | 4ebac7f4c139c28316f3315859ed83f5
g65q-9ase-khw8 | 1 |  | J7 Rw24 | 1254810791 | 28-03-2017 10:58:16 CEST | Kabalisa Manzi Christella | 00:12:05 | 2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Karambi |  |  | Gahama Kisaro network | 10234 |  | 184 | 184 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6671501074688961 | 30.041830412153367 | 1945.4 | 24l5zh36 |  | Yes | 3 | Yes | 1 |  |  | 2012 | Normal | 3 | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 |  |  | 2012 | Normal | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Poor | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6278818230384238 | 30.049070560680843 | 2057.9 | 22s7y8ju | 1 | https://waterforpeople.s3.amazonaws.com/images/0a2b941f-e275-4d97-a7c5-f67ca93be2d4.jpg | 2012 | Normal | No |  |  |  | No | Road construction destroyed some pipes | Poor |  | 2da87e6e90d978f8105d7726e4d4
yxej-ykxk-cwwb | 1 |  | J7 Rw8 | 1220440157 | 10-03-2017 12:20:17 CET | Amani Desire | 00:15:48 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Rwambogo |  |  | Rwambogo | 934 |  | 156 | 50 | 106 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.7494428720359798 | 29.92803731989297 | 1795.4 | 28d9bh8w |  | Yes | 60 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 60 | Yes | 1 |  | 2016 | Normal | 700 | Yes | 1 | -1.7469516964101284 | 29.923916567592556 | 1765.3 | 28952jl3 |  | 2016 | Poor | No | [5 empty] | Yes | 1 |  | 2016 | Normal | 350 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7476930577179193 | 29.924114739731767 | 1764.2 | 28ad4mcp | 3 | https://waterforpeople.s3.amazonaws.com/images/b961618b-ab22-4705-a5fd-1e369ebb1e21.jpg | 2016 | Normal | No |  |  |  | No | the water doesnt reach the distribution Reservoir nor the water point as it takes water from Reservoir | Poor | -The water point doesnt have water at this time -water don't reach the distribution Reservoir because the pipe that enters water to the tank is disconnected and broken | 409546d15220c56723183da4377827c
bgsw-kavy-jbtp | 1 |  | J7 Rw23 | 1237100581 | 23-03-2017 17:25:45 CET | Rugirangoga Augustin | 00:22:00 | 2017 | Rwanda | Rulindo | Buyoga | Ndarage | Karambi |  |  | Ndarage |  |  | 112 | 100 | 12 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | karambi Gahondo Bunyana Rugarama Gasave | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.6829614865475908 | 30.031434012077444 | 1962.1 | 25bb9sey |  | Yes | 30 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 30 | Yes | 1 |  | 2014 | Normal | 6700 | Yes | 5 | -1.6902852583901373 | 30.03414816539013 | 1811.8 | 25nf3391 |  | 2014 | Normal | No | [5 empty] | Yes | 1 |  | 2014 | Normal | 6700 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.692622924617372 | 30.033053746928864 | 668.4 | 25raeisq | 1 | https://waterforpeople.s3.amazonaws.com/images/233c878c-dff7-466e-82f5-c639170f4dca.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | this network has no problem | 34e5ba3b18113d499eab18fe1a11e5a
exg5-3g5s-rnf8 | 1 |  | J7 Rw19 | 1315830161 | 20-04-2017 14:50:31 CEST | Kayinamura Innocent | 00:16:50 | 2017 | Rwanda | Rulindo | Mbogo | Mushali | Bukongi |  |  | Gitabage network |  |  | 168 | 45 | 123 | Yes | Piped Network -- Gravity Only |  | 2008 | No |  | Catholic Church |  | 1 | Spring | -1.7894191074184786 | 29.98061378695303 | 1922.2 | 2a7d12la |  | Yes | 40 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2008 | Normal | 40 | Yes | 1 |  | 2008 | Normal | 700 | Yes | 2 | -1.7927177501595748 | 29.982999206837842 | 1821.5 | 2acti48l |  | 2008 | Normal | No | [5 empty] | Yes | 1 |  | 2008 | Normal | 500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7978963422707452 | 29.986142412943206 | 1737.4 | 2aldwnmd | 3 | https://waterforpeople.s3.amazonaws.com/images/fb0caa0c-d353-4e90-ae49-f36b8cf87fd9.jpg | 2008 | Poor | No |  |  |  | Yes |  | Normal | This network has 3 water points It serves 2 villages and one School | 3b9de6febe3e967f9eea646ffe08991
aq8p-15tn-qmcd | 1 |  | J7 Rw24 | 1215891253 | 16-03-2017 07:38:18 CET | Kabalisa Manzi Christella | 00:06:49 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Kisigiro |  |  | Rwamugaza | 14106 |  | 605 | 605 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government | no problem | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3.5 | Yes | 2 |  |  | 2003 | Normal | 3.5 | Yes | 1 |  | 2003 | Normal | 8000 | Yes | 20 | -1.7416188180333267 | 29.988511802248155 | 1861.3 | 280b531p |  | 2003 | Normal | Yes | 16 |  | https://waterforpeople.s3.amazonaws.com/images/77855cbe-348b-4270-9796-d60c80d36df5.jpg | 2003 | Poor | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7352735970133317 | 30.048975177181454 | 1792.3 | 27pto9zd | 1 | https://waterforpeople.s3.amazonaws.com/images/6ca50ded-4e5e-4534-928c-164128732d96.jpg | 2003 | Poor | No |  |  |  | No | System under rehabilitation | Normal | no problem | 2218a9fc996c49c238ff7d5e7769631f
x9kc-w36d-sy2c | 1 |  | J7 Rw8 | 1236140689 | 23-03-2017 10:02:03 CET | Amani Desire | 00:12:12 | 2017 | Rwanda | Rulindo | Murambi | Bubangu | Gashubi |  |  | Mutagata Motorised Network | 26296 |  | 140 | 39 | 101 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.834164682410857 | 30.026381636254932 | 1922.6 | 2c9dbv1j | 64 | https://waterforpeople.s3.amazonaws.com/images/d6dc38c7-2fbb-4624-bb00-c17d1ede54e0.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | 1d4148fc39f093fecd92973edacfc46
k5g7-37d5-smxj | 1 |  | J7 Rw10 | 1305650068 | 16-04-2017 22:01:00 CEST | Tuyisenge Vianney | 00:05:21 | 2017 | Rwanda | Rulindo | Base | Gitare | Mugenda I |  |  | Water point at Innocent's/Nyirambuga pumping system | 30604 |  | 117 | 117 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | The water point is operational but water comes rarely.This is a collection of 2 catchment area of Nyirambuga1 and Nyirambuga2 with almost 8 sources | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6621752332845048 | 29.899104604472196 | 1961.7 | 24cxhkq7 | 2 | https://waterforpeople.s3.amazonaws.com/images/fa51d76f-de11-430c-99ed-08aa5263eaa7.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | The water point is operational but water comes rarely.This is a collection of 2 catchment area of Nyirambuga1 and Nyirambuga2 with almost 8 sources | 65fc3af47e468059696fb981206f571b
vtca-nrnj-vru4 | 1 |  | J7 Rw23 | 1244040063 | 23-03-2017 17:25:53 CET | Rugirangoga Augustin | 00:19:17 | 2017 | Rwanda | Rulindo | Buyoga | Busoro | Rugarama |  |  | Ndarage |  |  | 189 | 170 | 19 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | karambi Gahondo Bunyana Rugarama Gasave | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.6829614865475908 | 30.031434012077444 | 1962.1 | 25bb9sey |  | Yes | 30 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 30 | Yes | 1 |  | 2014 | Normal | 6700 | Yes | 5 | -1.6902852583901373 | 30.03414816539013 | 1811.8 | 25nf3391 |  | 2014 | Normal | No | [5 empty] | Yes | 1 |  | 2014 | Normal | 6700 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.703928491477521 | 30.040723418209694 | 1580.3 | 269z6cfr | 1 | https://waterforpeople.s3.amazonaws.com/images/abc4ffef-c140-4b93-b488-a985b33127bc.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal |  | 6251e34a193d1bd2d75179cadd69c4d
n9u6-sh8u-9nay | 1 |  | J7 Rw8 | 1229050909 | 23-03-2017 10:33:47 CET | Amani Desire | 00:08:02 | 2017 | Rwanda | Rulindo | Murambi | Bubangu | Rebero |  |  | Mutagata Motorised Network | 26296 |  | 148 | 70 | 78 | Yes | Piped Network with Pump |  | 2016 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8442088038069209 | 30.02895076303688 | 1809.2 | 2cpz32f5 | 64 | https://waterforpeople.s3.amazonaws.com/images/97cd9c63-f9f1-446e-8bb4-f16ec807265d.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | e67e8ebcc8f2bbcc7351dfacaa5fa631
29t7-m5wt-krdp | 1 |  | J7 Rw10 | 1305990192 | 18-04-2017 07:06:07 CEST | Tuyisenge Vianney | 00:07:35 | 2017 | Rwanda | Rulindo | Tumba | Barari | Gaseke |  |  | Water point chez Rujugiro/Nyirambuga pumping system | 30604 |  | 149 | 149 | 0 | Yes | Piped Network with Pump |  | 2016 | Yes | Gaseke/Barari/Tumba and Rebero/Kayenzi/Bushoki | Governement (District, WASAC) and Water For People | The water point is operational though no tap has ever been fixed.It has been mapped in Rebero of Kayenzi in Bushoki.However,it should be counted in Gaseke of Barari in Tumba.Therefore,remove from Rebero/Kayenzi/Bushoki and be considered in Gaseke/Barari/Tumba. | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.713026331305272 | 29.929612773541663 | 1758.3 | 26p0ys2o | 2 | https://waterforpeople.s3.amazonaws.com/images/6fd132b6-cd59-4f59-9d4b-1c8b2b629de0.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | The water point is operational though no tap has ever been fixed.It has been mapped in Rebero of Kayenzi in Bushoki.However,it should be counted in Gaseke of Barari in Tumba.Therefore,remove from Rebero/Kayenzi/Bushoki and be considered in Gaseke/Barari/Tumba. | 51448ca47fbbef046825536c0d4d
qa37-4ajw-p8k0 | 1 |  | J7 Rw10 | 1305650063 | 16-04-2017 21:46:10 CEST | Tuyisenge Vianney | 00:10:32 | 2017 | Rwanda | Rulindo | Bushoki | Mukoto | Buvumo |  |  | Rukungeri-Bushoki cafe washing factory gravity system |  |  | 124 | 124 | 0 | Yes | Piped Network -- Gravity Only |  | 2007 | No |  | Local government in partnership with Bushoki cafe washing factory | The water point does nolonger operate people are fetching from the nearest spring | 1 | Spring | -1.7148709303768315 | 29.907839695503355 | 1825.3 | 26s33yti | https://waterforpeople.s3.amazonaws.com/images/2d43ee3a-64e4-4adb-96c6-501675cb1cfd.jpg | Yes | 40 | No | [5 empty] | 40 | Yes | 100 | https://waterforpeople.s3.amazonaws.com/images/af6d2cd5-ff5d-4235-a299-1f184bd3ffe7.jpg | 2007 | Normal | 800 | Yes | 1 | -1.7144755108000147 | 29.90789903792824 | 1825.2 | 26rfamme | https://waterforpeople.s3.amazonaws.com/images/283dd225-f420-4076-af20-0ef11b369656.jpg | 2007 | Poor | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7144572934193414 | 29.908083106975777 | 1807.6 | 26re3rew | 1 | https://waterforpeople.s3.amazonaws.com/images/4f187b23-56dd-4779-9815-9ff89b99fa96.jpg | 2007 | Does Not Function | No |  |  |  | Yes |  | Poor | The water point does nolonger operate people are fetching from the nearest spring | f740ff2769955153dae7bdac59ecba54
nqwj-0k30-xrdt | 1 |  | J7 Rw23 | 1216750516 | 15-03-2017 07:36:13 CET | Rugirangoga Augustin | 00:28:50 | 2017 | Rwanda | Rulindo | Base | Gitare | Nyamugali |  |  | Rutembe | 1012 |  | 229 | 200 | 29 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | This system of Rutembe is not functional due to broken piepes | 2 | Groundwater (well, etc.) | -1.6452293607002955 | 29.88940159790624 | 1774.8 | 23kwbua6 |  | Yes | 50 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 50 | Yes | 1 |  | 2016 | Poor | 3500 | Yes | 2 | -1.6350822337877793 | 29.89531663121816 | 1775 | 2344max5 |  | 2016 | Does Not Function | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.654627189348805 | 29.882200064317892 | 1737.9 | 240fzava | 2 | https://waterforpeople.s3.amazonaws.com/images/e5734ee8-6e82-4d15-bb0a-b13498eb2d19.jpg | 2016 | Does Not Function | No |  |  |  | No | water is not available because some pipes have been damaged while road were being built | Does Not Function | the last reservoir is also at high elevation compared to the source.(design issue) | 5320805b18171392c689f871e221c6
nah3-x753-8m1p | 1 |  | J7 Rw24 | 1219900776 | 15-03-2017 17:12:21 CET | Kabalisa Manzi Christella | 00:09:30 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Kisigiro |  |  | Rwamugaza | 14106 |  | 605 | 605 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | No Problem with the Water Point | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 23 |  | https://waterforpeople.s3.amazonaws.com/images/4d62f662-0fb2-4775-a1be-300af5c8b0fa.jpg | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7426916345830576 | 30.04334463656035 | 1965.8 | 2823fwsx | 1 | https://waterforpeople.s3.amazonaws.com/images/d185b5d5-7273-4f8b-8fd2-dac0e9d271f3.jpg | 2012 | Normal | No |  |  |  | No | Water seller was not around | Normal | This Water Point/system functions well | c13a1c45d55936ebc95eba6d23364e
gsh1-yqtd-pnf8 | 1 |  | J7 Rw8 | 1198270695 | 10-03-2017 12:31:20 CET | Amani Desire | 00:17:31 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Rwambogo |  |  | Rwambogo | 934 |  | 156 | 52 | 104 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.7494428720359798 | 29.92803731989297 | 1795.4 | 28d9bh8w |  | Yes | 60 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring¦collection chamber | 2016 | Normal | 60 | Yes | 1 |  | 2016 | Normal | 700 | Yes | 1 | -1.7469516964101284 | 29.923916567592556 | 1765.3 | 28952jl3 |  | 2016 | Poor | No | [5 empty] | Yes | 1 |  | 2016 | Normal | 350 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7465599946010537 | 29.923709307759918 | 1757.9 | 288h97dx | 3 | https://waterforpeople.s3.amazonaws.com/images/a4f95ca1-006f-45da-b749-03ab3d58f140.jpg | 2016 | Does Not Function | No |  |  |  | No | Today water doesnt reach the distribution reservoir as the pipe connecting to the reservoir is disconnected and it is why it doesnt reach the water point | Does Not Function | -no water at all points exceptthe water point at the source -water don't reach the Reservoir because the pipe that enters water to the tank is disconnected and broken | 9633348abbbe304bd12723eaaf3ea46
rwm0-ggbb-5ste | 1 |  | J7 Rw10 | 1304810050 | 16-04-2017 22:49:51 CEST | Tuyisenge Vianney | 00:06:17 | 2017 | Rwanda | Rulindo | Buyoga | Busoro | Rugarama |  |  | Water at Kaziba chez Verene/Nyirambuga pumping system | 30604 |  | 189 | 189 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Operational and functional as water available | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7129245551662051 | 29.992691627630236 | 2069.2 | 26ov0gie | 2 | https://waterforpeople.s3.amazonaws.com/images/137af857-e4a4-495c-9490-e0490bd1646c.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Operational and functional as water available | 96e2cff83242aac03181f6e928ff1824
cqjx-s9jn-a5kq | 1 |  | J7 Rw24 | 1217040348 | 15-03-2017 15:05:55 CET | Kabalisa Manzi Christella | 00:19:40 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kamatongo |  |  | 0 | 6572 |  | 1125 | 0 | 1125 | Yes | Piped Network with Pump |  | 2014 | No |  | Governement (District, WASAC) and Water For People | Water system is not yet functional since it was built | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2009 | Normal | 4.5 | Yes | 2 |  | 2014 | Does Not Function | 3000 | Yes | 6 | -1.7555179528295524 | 30.03970289656239 | 1690.5 | 28napmb1 |  | 2014 | Does Not Function | Yes | 13 |  |  | 2014 | Does Not Function | Yes | 2 |  | 2014 | Does Not Function | 3000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7691763631255042 | 30.05822830852931 | 1574.6 | 299vzqsm | 1 | https://waterforpeople.s3.amazonaws.com/images/b9b38290-3a44-47f4-819a-ec613d1b47aa.jpg | 2014 | Does Not Function | Yes | 365 | 0 | Since the system was built water hasn’t reached tap | No | three years without Water | Does Not Function | Water doesn’t reach destination | 5d13e62f88e215e77b51adae97a3581a
trde-qgm3-9xsm | 1 |  | J7 Rw15 | 1235250314 | 21-03-2017 18:05:25 CET | Mukakarangwa Assoumpta | 00:15:08 | 2017 | Rwanda | Rulindo | Kinihira | Butunzi | Barayi |  |  | Miyove- Kinihira | 10452 |  | 1600 | 1600 | 0 | Yes | Piped Network -- Gravity Only |  | 2001 | Yes | GS Kinihira | GKWW |  | 1 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 1989 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6713076749201647 | 29.962336020350133 | 1982.1 | 24s12civ | 1 | https://waterforpeople.s3.amazonaws.com/images/89ec0764-4c1b-49b2-a10e-f82d79e5c364.jpg | 1989 | Poor | No |  |  |  | Yes |  | Poor | water point for GS Kinihira | 7e9bd93b7190552f286d64ce9e9da3
e4v1-pssg-crn7 | 1 |  | J7 Rw26 | 1431010310 | 02-06-2017 08:58:12 CEST | Byukusenge Elie | 00:09:00 | 2017 | Rwanda | Rulindo | Cyinzuzi | Migendezo | Gitabage |  |  | Kararama | 6572 |  | 120 | 110 | 10 | Yes | Piped Network with Pump |  | 2009 | Yes | Not Water Tap | Water For People |  | 3 | Spring | -1.750378530192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 7 | -1.7464433654475461 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 14 | Sedimentation Tank¦Pressure Break Tank¦Distribution Chamber |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.766876526307512 | 29.99710164002383 | 2143.3 | 2963216r | 1 | https://waterforpeople.s3.amazonaws.com/images/337e7444-4c27-4b23-905a-c03bf9ba6057.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal |  | ef57f6513a27c6e3756faa63782357d
h6s2-a5cc-qkds | 1 |  | J7 Rw15 | 1217630768 | 12-03-2017 13:12:04 CET | Mukakarangwa Assoumpta | 00:10:10 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Muvumu |  |  | Muvumu- Taba |  |  | 132 | 75 | 57 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.8242130164596562 | 29.93108343031516 | 1700.7 | 2bswxje6 |  | Yes | 25 | No | [5 empty] | 25 | Yes | 1 |  | 2013 | Normal | 800 | Yes | 3 | 1.828985219687556 | 29.926634523104315 | 1627.1 | 2c0sxawy |  | 2013 | Poor | Yes | 9 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 7500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8511074139425547 | 29.917181956656734 | 1631.3 | 2d1dw4yr | 1 | https://waterforpeople.s3.amazonaws.com/images/18fcfe3a-1fed-4e2e-9d6b-887d34a6236c.jpg | 2013 | Normal | Yes | 1 | 3 | Those rehabilitating Rushinya source had strayed it | Yes |  | Poor |  | f47619fa41a541c7bee295458fcb3ef
hs7u-c7nb-exmw | 1 |  | J7 Rw10 | 1275930160 | 06-04-2017 19:18:02 CEST | Tuyisenge Vianney | 00:06:06 | 2017 | Rwanda | Rulindo | Bushoki | Mukoto | Buyogoma |  |  | Buyogoma water point |  |  | 130 | 130 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Government of Rwanda | This water point is nolonger operational and its closed due to non-metered water device installation.It is connected to Rutomvu gravity system | 1 | Spring | -1.677891751247546 | 29.90118126071259 | 1802.6 | 252xezpf |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6915164563008338 | 29.902201751508077 | 1794.7 | 25pgbdn2 | 1 | https://waterforpeople.s3.amazonaws.com/images/3f7bbcd5-3aad-4386-8007-56deb7a59873.jpg | 2013 | Does Not Function | No |  |  |  | No | This water point is nolonger operational and its closed due to non-metered water device installation.It is connected to Rutomvu gravity system | Does Not Function | This water point is nolonger operational and its closed due to non-metered water device installation.It is connected to Rutomvu gravity system | 739bc2a84c3bf91bf73e4cab161989e7
etts-t7nk-ec8e | 1 |  | J7 Rw24 | 1325920255 | 24-04-2017 23:23:19 CEST | Kabalisa Manzi Christella | 00:08:28 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Karambi |  |  | Rwamugaza network | 14106 |  | 73 | 73 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7374173333138418 | 30.006563288387298 | 1723.9 | 27td3141 |  | 2003 | Normal | Yes | 14 |  |  | 2003 | Normal | Yes | 1 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7362337052267534 | 30.07336983035694 | 1545.9 | 27retw8t | 1 | https://waterforpeople.s3.amazonaws.com/images/317adf1b-01f8-4730-baca-d447715c9a14.jpg | 2013 | Does Not Function | No |  |  |  | No | robinet yarapfuye | Poor |  | 284474dfa1e7a89ce2260c3566d3c93
e170-5hjp-0wrs | 1 |  | J7 Rw15 | 1207980332 | 09-03-2017 06:00:41 CET | Mukakarangwa Assoumpta | 00:06:11 | 2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Rimwe |  |  | kirikumuryango network |  |  | 120 | 60 | 60 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8781266333430318 | 29.943320905532847 | 1362.1 | 2ea2ldpl | 1 | https://waterforpeople.s3.amazonaws.com/images/a80b4e13-f45d-477e-86a2-546566fdd300.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | d6a493c698914753dd7d864e0468
afbs-28cg-e5w2 | 1 |  | J7 Rw23 | 1187141436 | 08-03-2017 06:52:39 CET | Rugirangoga Augustin | 00:54:45 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Rubanda |  |  | Migogo | 558 |  | 170 | 120 | 50 | Yes | Piped Network -- Gravity Only |  | 2013 | Yes | kiruli bukangano kabahama rubanda | LAKE ANGELS | No Problem with the Water Point | 1 | Spring | 1.632311918504939 | 29.90125938622729 | 1810.2 | 22zjp8ec |  | No | 60 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2009 | Poor | 60 | Yes | 2 |  | 2009 | Poor | 3000 | Yes | 3 | 1.6350822337877793 | 29.89531663121816 | 1775.7 | 2344max5 |  | 2009 | Poor | No | [5 empty] | Yes | 2 |  | 2009 | Poor | 3000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6414527283470774 | 29.900197640418515 | 1530.5 | 23envfax | 2 |  | 2013 | Poor | No |  |  |  | Yes |  | Poor | System needs rehabilitation | 86f643873b16ff034294c439b811520
9t30-n51m-rkvq | 1 |  | J7 Rw15 | 1243820127 | 21-03-2017 17:46:27 CET | Mukakarangwa Assoumpta | 00:09:30 | 2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Ntunguru |  |  | Miyove-Kinihira | 10452 |  | 168 | 70 | 98 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2021.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6733399500056403 | 29.96946029819898 | 1962 | 24vdxcdq | 1 | https://waterforpeople.s3.amazonaws.com/images/7ae4ce93-2957-4b56-bc42-edd7618f93bc.jpg | 1989 | Poor | No |  |  |  | Yes |  | Poor |  | 8812181c3b3598d51a9e76a7af84db96
9576-vvfw-nrsb | 1 |  | J7 Rw19 | 1252860176 | 25-03-2017 11:31:56 CET | Kayinamura Innocent | 01:28:11 | 2017 | Rwanda | Rulindo | Masoro | Kivugiza | Musenga |  |  | Mutagata Gravity network | 26296 |  | 185 | 140 | 45 | Yes | Piped Network -- Gravity Only |  | 1987 | Yes | Ruri, Musenga, Rukurazo, Umubuga, Amataba, Rusine, Marenge |  |  | 1 | Spring | -1.8023389079852206 | 30.042447389592418 | 1691.2 | 2asq94nc |  | Yes | 8 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2004 | Poor | 8 | Yes | 1 |  | 2004 | Poor | 3500 | Yes | 6 | -1.8078446763653504 | 30.06649761552014 | 1669.8 | 2b1uaz5k |  | 2004 | Poor | Yes | 4 | Distribution Chamber¦Washout and Air release |  | 2004 | Poor | Yes | 2 |  | 2004 | Poor | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7998585126814564 | 30.077788235439673 | 1473 | 2aomlmw9 | 12 | https://waterforpeople.s3.amazonaws.com/images/9edc743e-54bd-4dc9-9340-60731928a4a2.jpg | 2015 | Does Not Function | No |  |  |  | Yes |  | Poor | 1. the Extension to Nyabinyana village has 2 reservoirs and two water points which is under construction 2. this system have been constructed in 2004 3. it serve a party of Masoro Sector and other party is located in Gasabo District 4. 2 water points and one reservoir have been constructed in 2016. 5. in general, this network has 27 water points in which 12 are in Rulindo District and the remaining are in Gasabo District. | 31762d960a9d61342bf46815e79b35
yw58-cf0q-7d8y | 1 |  | J7 Rw8 | 1209180089 | 10-03-2017 11:29:29 CET | Amani Desire | 00:24:28 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | Nganzo-Kabarore |  |  | 198 | 98 | 100 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | nkanga,kagwa | Governement (District, WASAC) and Water For People | Water points are damaged and destroyed and are not functioning - water Pipes are broken | 1 | Spring | -1.8123160408683467 | 29.96796382144226 | 1787.1 | 2b98fpsv |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 20 | Yes | 1 |  | 2014 | Poor | 400 | Yes | 3 | -1.8123911178819008 | 29.967599969457293 | 1761.4 | 2b9d76mz |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Does Not Function | 800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8192127665439741 | 29.962026748097962 | 1694.7 | 2bkn8t5w | 5 | https://waterforpeople.s3.amazonaws.com/images/d49dd24b-d14b-4852-8208-c555a765b501.jpg | 2014 | Does Not Function | Yes | 5 | 30 | pipes and infrastructures are destroyed | No | the pipes that connect water to this water point is broken | Does Not Function | -the water point at the source is damaged but it is functioning -the pipeline is damaged, all distribution pipes are broken -there are no water at all water points | 53efd1d87ac46ab27e5f27c84df4364
ea46-6y6f-mxpr | 1 |  | J7 Rw23 | 1210600166 | 09-03-2017 08:43:49 CET | Rugirangoga Augustin | 00:25:05 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 1458 |  | 77 | 70 | 7 | Yes | Piped Network -- Gravity Only |  | 2005 | No |  | Governement (District, WASAC) and Water For People | This Water Point was Funded by Charity Water | 1 | Spring | -1.6426625760859115 | 29.882931577022582 |  | 23gnwvd9 |  | Yes | 60 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2005 | Normal | 75 | Yes | 1 |  | 2005 | Normal | 7000 | Yes | 2 | -1.6503480343855401 | 29.882910347806035 | 1718.1 | 23td5ryl |  | 2005 | Normal | Yes | 2 | Pressure Break Tank |  | 2017 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6503159107324792 | 29.88283872375492 | 1739.5 | 23tbdh58 | 2 |  | 2016 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | ba5bb4f1109d1a9e14d934feaf98a5f6
3b48-49r5-1cyt | 1 |  | J7 Rw10 | 1221960368 | 13-03-2017 22:02:44 CET | Tuyisenge Vianney | 00:07:32 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Nkore source catchment |  |  | 172 | 172 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | The water source operates well | 1 | Spring | -1.6883400866741962 | 29.91133431277988 | 1897.9 | 25k7kyy1 | https://waterforpeople.s3.amazonaws.com/images/7948d0f6-3d4b-41db-ba46-338c153de464.jpg | Yes | 40 | No | [5 empty] | 40 | Yes | 1 |  | 2013 | Normal | 50 | Yes | 1 | -1.6883153151379338 | 29.911190736188804 | 1499.2 | 25k5so4n | https://waterforpeople.s3.amazonaws.com/images/7bce3a7a-55e2-4dc5-9404-6f23a1197470.jpg | 2013 | Normal | No | [5 empty] | Yes | 1 |  | 2013 | Normal | 2000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.688310595101912 | 29.911222614768896 | 1934.4 | 25k5so4o | 1 | https://waterforpeople.s3.amazonaws.com/images/e8b24e56-e591-457d-a7f3-ea8c9aa6267a.jpg | 2013 | Poor | No |  |  |  | Yes |  | Poor | The water point operates well though it is not protected. | 7f21faa4a8f08351f19c9070fc2a12a9
x1ch-9a7d-nh45 | 1 |  | J7 Rw15 | 1240030093 | 21-03-2017 14:30:24 CET | Mukakarangwa Assoumpta | 00:12:13 | 2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Magezi |  |  | Miyove-Kinihira | 10452 |  | 141 | 80 | 61 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6475860727485991 | 29.986424671708463 | 1291.2 | 23osu5so | 1 | https://waterforpeople.s3.amazonaws.com/images/78a8898b-7e2c-4ac9-89ff-ac68d62545e6.jpg | 1989 | Poor | No |  |  |  | Yes |  | Poor | -Water point is poor because it has nit water tap and it does not properly. | dfb7d3d54b53abeb1e5cfbab38a103f
u16h-twjd-19s3 | 1 |  | J7 Rw26 | 1232820627 | 21-03-2017 13:55:34 CET | Byukusenge Elie | 00:06:02 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Kabingo |  |  | Kabonanyoni | 7894 |  | 38 | 35 | 3 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6467406434412326 | 29.966900494971494 | 2017.3 | 23netqtx | 31 | https://waterforpeople.s3.amazonaws.com/images/cf3d0c08-18ff-47a6-9938-e46553069c09.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | d7b4ed7bcc8c83dffd9dd68fcb76e45
1us5-e21v-t6nd | 1 |  | J7 Rw10 | 1276060135 | 06-04-2017 19:13:07 CEST | Tuyisenge Vianney | 00:17:43 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Remera |  |  | Kinyankera gravity system |  |  | 105 | 105 | 0 | Yes | Piped Network -- Gravity Only |  | 2010 | Yes | Buyogoma/Mukoto cell and Remera/Nyirangarama cell | Local government and community | It is located in border of Remera(Nyirangarama) and Buyogoma(Mukoto).Capturing was made to supply private connections of Buyogoma. | 1 | Spring | -1.6950597099281783 | 29.890803301352435 | 2001.6 | 25vb2tp8 | https://waterforpeople.s3.amazonaws.com/images/435059d2-5c10-4901-868b-7f7faad618c9.jpg | Yes | 20 | No | [5 empty] | 20 | Yes | 1 |  | 2015 | Normal | 100 | Yes | 1 | -1.6950167490503893 | 29.89088856384206 | 1999.7 | 25v8p3a4 | https://waterforpeople.s3.amazonaws.com/images/d2a33ce6-160c-4b7f-9e8a-82aed7de6cd3.jpg | 2015 | Normal | No | [5 empty] | Yes | 1 |  | 2015 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6950192665669452 | 29.890829961925103 | 1999 | 25v8p3a4 | 3 | https://waterforpeople.s3.amazonaws.com/images/303a8a9b-e776-4b20-ad7b-174df920da85.jpg | 2010 | Normal | No |  |  |  | Yes |  | Normal | It is located in border of Remera(Nyirangarama) and Buyogoma(Mukoto).Capturing was made to supply private connections of Buyogoma. | 231b8eae9aec20a8b3fe7dc4889ff
yfr5-t7dh-1xun | 1 |  | J7 Rw19 | 1220540108 | 09-03-2017 18:11:13 CET | Kayinamura Innocent | 00:23:48 | 2017 | Rwanda | Rulindo | Ngoma | Karambo | Jyambere |  |  | Gahama network |  |  | 117 | 52 | 65 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | Jyambere | Governement (District, WASAC) and Water For People | two water points had been damaged | 1 | Spring | -1.824762618736981 | 29.979015616308 | 1718 | 2bttoe1a |  | No | 15 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 15 | Yes | 1 |  | 2014 | Normal | 1800 | Yes | 2 | -1.8248055237148662 | 29.983823341228508 | 1657.7 | 2btw24hq |  | 2014 | Normal | Yes | 1 | Distribution Chamber |  | 2014 | Normal | Yes | 1 |  | 2014 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8339594379126452 | 29.988000505802045 | 1636.9 | 2c90tr1k | 5 | https://waterforpeople.s3.amazonaws.com/images/22fb0624-2dad-4cee-9da8-6489687c3c94.jpg | 2014 | Normal | No |  |  |  | Yes |  | Poor | Two water points have broken parts and source stayed | 4722981729785546a42689437961be66
gwv7-7vyp-7nq6 | 1 |  | J7 Rw10 | 1305090067 | 18-04-2017 06:56:47 CEST | Tuyisenge Vianney | 00:06:53 | 2017 | Rwanda | Rulindo | Tumba | Gahabwa | Kabuga |  |  | Water point chez Ntuyenabo/Nyirambuga pumping system | 30604 |  | 155 | 155 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | The water point has been recently completed however no water available till now | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7203198098455623 | 29.950883451129478 | 2069.6 | 2712zs8k | 2 | https://waterforpeople.s3.amazonaws.com/images/5b90ae00-6b05-43c3-945c-a9ea9aa97137.jpg | 2017 | Does Not Function | No |  |  |  | No | The water point has been recently completed however no water available till now | Does Not Function | The water point has been recently completed however no water available till now | 971962c6b46cdd58b76fbfd0e1e8a8bb
g2sh-xxj4-p9ph | 1 |  | J7 Rw23 | 1218330175 | 15-03-2017 08:00:12 CET | Rugirangoga Augustin | 00:22:50 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Kabuga |  |  | Gihanga | 2456 |  | 73 | 60 | 13 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | kabuga mushongi buramba | Governement (District, WASAC) and Water For People | this network works in one part . the other part does not work | 1 | Spring | -1.6358367374763643 | 29.91135277934778 | 1996.9 | 235d9tex |  | Yes | 15 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Poor | 15 | Yes | 1 |  | 2016 | Poor | 7200 | Yes | 6 | -1.6498521069502532 | 29.917613599705728 | 1996.9 | 23sjzjl4 |  | 2016 | Poor | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6453170080059196 | 29.905362830894457 | 1792.1 | 23l1oqul | 2 | https://waterforpeople.s3.amazonaws.com/images/69861e1e-1365-43f3-9a1c-4c52d4143b60.jpg | 2016 | Does Not Function | Yes | 7 | 7 | water does not reach to the water tap | No | low pressure of water | Poor | the network is not working well | 5f1e17e43a3aad903d4ba8724c66f20
165s-xh1v-d8j0 | 1 |  | J7 Rw10 | 1314020243 | 20-04-2017 10:42:00 CEST | Tuyisenge Vianney | 00:05:02 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Gihanga |  |  | Water point at Gihanga under road/Nyirambuga pumping | 30604 |  | 152 | 152 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | Yes | 1 | -1.680704986943682 | 29.940601157297703 | 1856.3 | 257kpszy | https://waterforpeople.s3.amazonaws.com/images/da1be935-302c-467a-879f-c952d8ff18c8.jpg | 2017 | Normal | Yes | 1 | washout | https://waterforpeople.s3.amazonaws.com/images/0e07e9f8-ccb9-4cdf-a1e7-c199aa54ac01.jpg | 2017 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6806253578218284 | 29.94062313515126 | 1864.7 | 257fyc5q | 2 | https://waterforpeople.s3.amazonaws.com/images/32fbe800-0d83-4434-b528-173ba772315f.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | operational | ef12a6589298ae2deb81784d3fcf0d6
37cv-m8tr-ue41 | 1 |  | J7 Rw19 | 1257490234 | 26-03-2017 23:13:51 CEST | Kayinamura Innocent | 01:07:26 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gitaba |  |  | Musenge network | 6074 |  | 195 | 100 | 95 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma, Karehe, Rutonde, Gitaba, Kiruri, Buhera, Ruhanya, Kibamba, Karindi. | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.76879449980039 | 29.938590376456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.780150896458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Washout and Air release |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7853430528373888 | 29.946168635074148 | 1989.1 | 2a0mpn45 | 28 | https://waterforpeople.s3.amazonaws.com/images/7b9e4a44-df5c-4a94-8acc-42d9fb3a6347.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. The system has two Pumps but one is damaged and is not working, only one pump is used to pump water 2. Eleven (11) water points served by the distribution reservoir R 50m3 located at Kibamba village do not have water today because water don't reach this reservoir, there is not water at those water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5. one water point doesn't Function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction. | 70cd97af92785ff74649a56da56f097
awvq-wf26-5btn | 1 |  | J7 Rw19 | 1239840832 | 24-03-2017 04:35:44 CET | Kayinamura Innocent | 00:07:45 | 2017 | Rwanda | Rulindo | Masoro | Kivugiza | Gasenga |  |  | Mutagata motorised network | 26296 |  | 284 | 138 | 146 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.80152228745035 | 30.042875565044753 | 1708.3 | 2are10ng |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7890574023940573 | 30.0753345591099 | 1652.5 | 2a6rlhjl | 64 |  | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | ff56b3912fc42e0dea1bf2c1070809f
rsdr-jb06-p7jv | 1 |  | J7 Rw23 | 1216750376 | 15-03-2017 05:16:20 CET | Rugirangoga Augustin | 00:21:00 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 1789 |  | 192 | 180 | 12 | Yes | Piped Network -- Gravity Only |  | 2012 | Yes | karambi gitovu | Padiri | this network, its source has been reinforced by waterforpeople | 3 | Spring | -1.6128815953757245 | 29.874655017548616 | 1956.1 | 223evzsq |  | Yes | 30 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 30 | Yes | 1 |  | 2016 | Normal | 6450 | Yes | 2 | -1.6111677762752643 | 29.8839135826884 | 1852 | 220khftj |  | 2012 | Normal | Yes | 2 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/f58a2fd9-da3a-475f-bec3-c0272a223378.jpg | 2012 | Normal | Yes | 1 |  | 2012 | Normal | 6450 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6106712957426563 | 29.881291853397048 | 1871.5 | 21zrb75o | 1 | https://waterforpeople.s3.amazonaws.com/images/2d19c2de-5e07-45c7-9839-5fff04dbaf34.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal |  | 2e149c8ecaab36df515d23994358056
xerr-vga2-qx1 | 1 |  | J7 Rw10 | 1319450184 | 21-04-2017 16:22:36 CEST | Tuyisenge Vianney | 00:11:19 | 2017 | Rwanda | Rulindo | Rusiga | Taba | Karenge |  |  | Water point at Kukabuga/Bitare-Gahondo gravity | 9577 |  | 112 | 112 | 0 | Yes | Piped Network -- Gravity Only |  | 1989 | No |  | Catholic Church | Nolonger operational.All infrastructures damaged(pipeline broken due to exposure on surface,) | 2 | Spring | -1.8240400967512485 | 29.93064274686712 | 1670 | 2bsmt63u | https://waterforpeople.s3.amazonaws.com/images/50575ff8-2fde-4427-b631-0bbf82e450b4.jpg | Yes | 10 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/21ab0eb8-72fd-4272-b4d5-2587530691c4.jpg | "Springbox" --Intake Structure at a Spring | 2017 | Normal | 10 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/32f14a14-eb0a-47aa-a6fb-a592fdfd763a.jpg | 2017 | Normal | 400 | Yes | 1 | -1.8251370012419577 | 29.919059776623076 | 1686.4 | 2bufpeye | https://waterforpeople.s3.amazonaws.com/images/69dc3681-9225-448f-afa0-e7b140ece463.jpg | 1989 | Does Not Function | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.825156311837951 | 29.91906602591412 | 1676.2 | 2bugwa5y | 1 | https://waterforpeople.s3.amazonaws.com/images/51d3c5e5-26fd-4875-a23c-cd2188552ac2.jpg | 1989 | Does Not Function | No |  |  |  | No | System demolished. | Poor | Currently at water sources there are two conductions lines with big quantity of water.However,the previous gravity network is not operating at all for the works of recapturing being under progress.The sources are being recaptured to make it pumping system that will also be supplying the Gako(Rusiga) Military Base | 9443756b3ad9c1dec3c686b4559b7a
kuxx-je75-m5c5 | 1 |  | J7 Rw10 | 1214532932 | 15-03-2017 19:58:10 CET | Tuyisenge Vianney | 00:08:32 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Water point at Kayenzi cell near TCT/Nyirambuga pumping system | 30604 |  | 174 | 174 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | GoR | Water point near TCT operates well though water comes easily | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6948927450069844 | 29.9217353167529 | 2135 | 25v1jw9d | 1 | https://waterforpeople.s3.amazonaws.com/images/e35f185a-8f94-458d-9f7d-1d26f2010caa.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Water point near TCT operates well though water comes easily | 806b777e498a25b81ea6d943032ddff
q90s-v6aa-m6vy | 1 |  | J7 Rw23 | 1216750378 | 15-03-2017 05:16:46 CET | Rugirangoga Augustin | 00:39:39 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 1789 |  | 192 | 180 | 12 | Yes | Piped Network -- Gravity Only¦Private Tap with Piped Supply |  | 2016 | Yes | karambi gitovu | Governement (District, WASAC) and Water For People | this network has no problem | 2 | Spring | -1.6128815953757245 | 29.874655017548616 | 1956.1 | 223evzsq |  | Yes | 30 | Yes | 3 | https://waterforpeople.s3.amazonaws.com/images/242ea3f7-a9f7-49b0-9540-4c2ba830caca.jpg | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 30 | Yes | 2 |  | 2012 | Normal | 6450 | Yes | 2 | -1.6111677762752643 | 29.8839135826884 | 1852 | 220khftj |  | 2012 | Normal | Yes | 2 | Distribution Chamber |  | 2012 | Normal | Yes | 2 |  | 2016 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6113970324122844 | 29.877912282931124 | 1898.3 | 220y6eor | 2 | https://waterforpeople.s3.amazonaws.com/images/7557978d-e9c5-42d8-9392-2f2dd322fb70.jpg | 2012 | Poor | No |  |  |  | Yes |  | Normal | this network has no problem | 78d069fe512fd3e962c5c02e694e734b
4awq-1awm-hu1v | 1 |  | J7 Rw10 | 1211230742 | 14-03-2017 22:35:17 CET | Tuyisenge Vianney | 00:07:32 | 2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point/AEP Kigarama | 2621 |  | 243 | 243 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | GoR | This water gravity system,its source and water points operate well. They have a project to augment the quantity of water points to be used by people resettled from high risk zone | 1 | Spring | -1.7875070118422336 | 29.922431620181639 | 2051.7 | 2a47b9lk |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | Yes | 1 | -1.7828082796501106 | 29.929046329093943 | 1899.8 | 29wfhjbu | https://waterforpeople.s3.amazonaws.com/images/2e6b7d0e-ae6f-4829-a983-2a727ea8430d.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7826344054826562 | 29.92919013761413 | 1913.5 | 29w5d61n | 1 | https://waterforpeople.s3.amazonaws.com/images/fa4a0c85-aa60-4ab7-be6a-187227d51462.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water gravity system,its source and water points operate well. They have a project to augment the quantity of water points to be used by people resettled from high risk zone | 0f5b8f01d84d678341874c328ad8dd3
9nga-sn0j-m0sj | 1 |  | J7 Rw26 | 1211150068 | 12-03-2017 07:05:32 CET | Byukusenge Elie | 00:08:51 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Kivomo |  |  | Nyamagana | 20456 |  | 1100 | 1100 | 0 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank | This network serves four sectors Cyungo,Rukozo, Base,Base and Kinihira, It has some problems in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible because it serves many populations and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.654188389271562 | 29.955307782407438 | 1830.9 | 23zps8td | 29 | https://waterforpeople.s3.amazonaws.com/images/18c4c7d2-c3e5-442a-a3ae-1499564f376d.jpg | 2011 | Normal | Yes | 10 | 25 | Bad tee connections and the types of pipeline needs rehabilitation | No | The pipeline connecting to the reservoir has been damaged | Poor | water tap at E.P.Mutara | aca3b9b005fd9143f1ccdf99a3875a
5rcg-3fxe-w9v6 | 1 |  | J7 Rw24 | 1254940082 | 28-03-2017 10:35:17 CEST | Kabalisa Manzi Christella | 00:04:27 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza network | 14106 |  | 229 | 229 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695880900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8081746652627881 | 30.124810205948748 | 1430.8 | 2b2dyakg | 1 | https://waterforpeople.s3.amazonaws.com/images/93caee24-5cd6-44cc-8ec2-b4cf6bd1af6d.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | 95344e618b6d9587b0928e4cf9f9926f
689d-hf3w-hr7g | 1 |  | J7 Rw10 | 1232160421 | 02-01-2015 13:38:41 CET | Tuyisenge Vianney | 00:10:51 | 2017 | Rwanda | Rulindo | Buyoga | Karama | Karambo |  |  | Water point at Karama cell/Nyirambuga pumping | 30604 |  | 165 | 165 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | One water tap valve was removed.It is better to refix a new one.However water comes rarely due as it is common in Buyoga | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.708815983831671 | 29.97470461331463 | 2072.3 | 26i2baqr | https://waterforpeople.s3.amazonaws.com/images/4fb50b93-a3a3-4f16-8796-289fe9d0b67c.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7085793487679242 | 29.974614101646534 | 2074.6 | 26ho0w82 | 2 | https://waterforpeople.s3.amazonaws.com/images/d95ea34a-6405-4313-a3aa-a1f70b30e90d.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | One water tap valve was removed.It is better to refix a new one.However water comes rarely due as it is common in Buyoga | 6f3137481739ecd2f51fb217d68a92a
c297-xak9-6uyk | 1 |  | J7 Rw19 | 1330940049 | 22-04-2017 12:23:03 CEST | Kayinamura Innocent | 00:11:04 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Gahama |  |  |  | 26296 |  | 115 | 115 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 1 | Spring | -1.7925838151091869 | 30.030709112585352 | 1831.9 | 2aclrhqr | https://waterforpeople.s3.amazonaws.com/images/30c56f9b-a370-4c78-87e6-9d6eaa1d4829.jpg | No | 87 | No | [5 empty] | 87 | No | [5 empty] | Yes | 1 | -1.7922226965025903 | 30.030666999320275 | 1844.1 | 2ac0bvyq | https://waterforpeople.s3.amazonaws.com/images/d7b28882-1b4b-4908-940f-1562182b00af.jpg | 2003 | Poor | No | [5 empty] | Yes | 1 |  | 2003 | Poor | 100 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7920653331992022 | 30.030788659220516 | 1809.6 | 2abqsyab | 1 | https://waterforpeople.s3.amazonaws.com/images/7af8a2ca-883a-40ce-9eed-7759b19257e5.jpg | 2003 | Poor | No |  |  |  | Yes |  | Poor | Source gets dirty in the rainy season, | 5f986be25e9db7b9d84d11bf751fcc
evkc-fy63-xqg3 | 1 |  | J7 Rw10 | 1230180157 | 03-01-2015 01:06:32 CET | Tuyisenge Vianney | 00:11:16 | 2017 | Rwanda | Rulindo | Tumba | Gahabwa | Mafene |  |  | Water point at Gahabwa cell(near EP Gahabwa)/Nyirambuga pumping | 30604 |  | 172 | 172 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point at Gahabwa cell and EP Gahabwa currently serves both the school pupils and the remaining people.It operates well and normally.As the school has opened doors very soon and it is planned to hand the water point to the school very soon.Its storage tank however does not have a cover on its valve chamber | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.7224369404559223 | 29.956015014458174 | 2103.5 | 274l7oiw | https://waterforpeople.s3.amazonaws.com/images/86b5d003-d42a-47f2-bfe7-1f89af052359.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7231035580419563 | 29.95691841035897 | 2079.7 | 275p3q29 | 2 | https://waterforpeople.s3.amazonaws.com/images/5bccdd79-6eac-4f78-a5e0-57f06b713bff.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point at Gahabwa cell and EP Gahabwa currently serves both the school pupils and the remaining people.It operates well and normally.As the school has opened doors very soon and it is planned to hand the water point to the school very soon | 53785fb26a2cc3cc47e16dcd2b25b650
2eej-cd07-na2e | 1 |  | J7 Rw19 | 1204700714 | 09-03-2017 18:10:47 CET | Kayinamura Innocent | 00:43:45 | 2017 | Rwanda | Rulindo | Ngoma | Karambo | Karambi |  |  | Gahama network |  |  | 117 | 33 | 84 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | Jyambere | Governement (District, WASAC) and Water For People | two water point had been damaged | 1 | Spring | -1.824762618736981 | 29.979015616308 | 1718 | 2bttoe1a | https://waterforpeople.s3.amazonaws.com/images/dcd5c80b-2ac9-44e2-b1c1-d3eb5df8b6fd.jpg | No | 15 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/13bb60e5-ba43-48fa-8f25-a658a48586b5.jpg | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 15 | Yes | 1 |  | 2014 | Normal | 1800 | Yes | 2 | -1.8248055237148662 | 29.983823341228508 | 1657.7 | 2btw24hq | https://waterforpeople.s3.amazonaws.com/images/9c118654-e930-4f4f-abae-9ae8c97789df.jpg | 2014 | Normal | Yes | 1 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/f967be26-c30f-49dc-8c74-82cd8024b24e.jpg | 2014 | Normal | Yes | 1 |  | 2014 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8246196019411987 | 29.981039239615594 | 1668.8 | 2btkqvz6 | 5 | https://waterforpeople.s3.amazonaws.com/images/eb53317e-3025-4b59-95b7-b26ac2cc969f.jpg | 2014 | Does Not Function | No |  |  |  | Yes |  | Poor | Two water points have broken parts and source stayed | f1a616af8f583c5756b14ffa7edae
96mm-gbth-bbq1 | 1 |  | J7 Rw24 | 1245960344 | 28-03-2017 10:32:24 CEST | Kabalisa Manzi Christella | 00:04:48 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza network | 14106 |  | 229 | 229 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139583 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 2 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695880900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 14 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.80902541789623 | 30.126486321580682 | 1458.9 | 2b3sk500 | 1 | https://waterforpeople.s3.amazonaws.com/images/6c44a774-7905-4a64-b9fd-eef83861b15b.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | 44e07fe685c202274ce450ff5ff17
byhc-9rjx-q5hj | 1 |  | J7 Rw15 | 1221570154 | 12-03-2017 12:49:35 CET | Mukakarangwa Assoumpta | 00:07:32 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kagunda |  |  | Muvumu- Taba |  |  | 94 | 20 | 74 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.8242130164596562 | 29.931083430301516 | 1700.7 | 2bswxje6 |  | Yes | 25 | No | [5 empty] | 25 | Yes | 1 |  | 2013 | Normal | 800 | Yes | 3 | 1.828985219687556 | 29.926634523104315 |  | 2c0sxawy |  | 2013 | Poor | Yes | 9 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 7500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.832570884022093 | 29.928852337809456 | 1614.6 | 2c6qnx3s | 1 | https://waterforpeople.s3.amazonaws.com/images/72a83490-f5bf-42f5-8bf2-8ec049f7d915.jpg | 2013 | Normal | Yes | 1 | 3 | Those rehabilitating Rushinya source had strayed it | Yes |  | Poor |  | e592e0c27caf9aab509a91f19937bb2f
fs52-dm2a-snnn | 1 |  | J7 Rw24 | 1218850557 | 16-03-2017 06:18:13 CET | Kabalisa Manzi Christella | 00:05:13 | 2017 | Rwanda | Rulindo | Burega | Karengeli | Rwamiko |  |  | Rwamugaza | 14106 |  | 440 | 440 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | no problem | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7343459129979093 | 30.027100193223262 | 2048.1 | 27oaayjz | 1 | https://waterforpeople.s3.amazonaws.com/images/fa1af658-9fc4-43c7-b3cd-d575bdd948c7.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | no problem | 72cba4b24e49d5fab3a4b12c77a9f8e1
j533-grmg-01vd | 1 |  | J7 Rw15 | 1221570153 | 12-03-2017 12:46:37 CET | Mukakarangwa Assoumpta | 00:08:43 | 2017 | Rwanda | Rulindo | Rusiga | Taba | Bitare |  |  | Muvumu-Taba |  |  | 113 | 20 | 93 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.8242130164596562 | 29.931083430301516 | 1700.7 | 2bswxje6 |  | Yes | 25 | No | [5 empty] | 25 | Yes | 1 |  | 2013 | Normal | 800 | Yes | 3 | 1.828985219687556 | 29.926634523104315 |  | 2c0sxawy |  | 2013 | Poor | Yes | 9 | Pressure Break Tank¦Distribution Chamber¦Washout, Ventouse |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 7500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.828982369518951 | 29.92654550846956 | 1609.2 | 2c0sxawx | 1 | https://waterforpeople.s3.amazonaws.com/images/67f58354-6cd8-4928-a169-b438e4dc2bd7.jpg | 2013 | Poor | Yes | 1 | 3 | Those rehabilitating Rushinya source had strayed it | Yes |  | Poor |  | f2914e4bc27806cf81eb1f0f43eecfe
3v1m-rq04-0r95 | 1 |  | J7 Rw10 | 1201010489 | 10-03-2017 13:36:21 CET | Tuyisenge Vianney | 00:06:46 | 2017 | Rwanda | Rulindo | Bushoki | Mukoto | Gatare |  |  | Gatare water point/Tare-Rusiga pumping | 9577 |  | 129 | 129 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This is Gatare water point served by the Main reservoir | 10 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 4000 | Yes | 1 | -1.7226508253758965 | 29.904925750522754 | 2182 | 274yb7ft | https://waterforpeople.s3.amazonaws.com/images/4e56ddaa-ad82-476a-8141-a44eb03c7bf4.jpg | 2015 | Normal | No | [5 empty] | Yes | 1 |  | 2015 | Normal | 8000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7225608039881684 | 29.90504194705296 | 2175.9 | 274syazu | 2 | https://waterforpeople.s3.amazonaws.com/images/40c3c221-7fcc-43fe-aaab-33f9ce0fea8c.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Gatare water point operates normally | 9c5127c4ddbc526a0ddbaf9d3f05d
57xj-6px1-7pc9 | 1 |  | J7 Rw24 | 1324790062 | 25-04-2017 00:12:47 CEST | Kabalisa Manzi Christella | 00:11:41 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Kazi |  |  | Rwamugaza network | 14106 |  | 184 | 184 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7374173333138418 | 30.006563288387298 | 1723.9 | 27td3141 |  | 2003 | Normal | Yes | 14 |  |  | 2003 | Normal | Yes | 1 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8102836977450811 | 30.113045087634177 | 1629.4 | 2b5vkr4a | 1 | https://waterforpeople.s3.amazonaws.com/images/873f4d39-7856-4458-9084-bebbb942d5e8.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | 976470a46bb825bccf63b6958f63963
37m6-r8s4-gn6f | 1 |  | J7 Rw24 | 1253520448 | 28-03-2017 08:34:10 CEST | Kabalisa Manzi Christella | 00:06:38 | 2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Gitwa |  |  | Rwamugaza network | 14106 |  | 120 | 120 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7910039659131844 | 30.095356294441387 | 1740.6 | 2a9zp0nt | 1 | https://waterforpeople.s3.amazonaws.com/images/379ea9fd-4b19-4b8f-b4e0-3619716a294e.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | cc97f6b9d65bae15814bbd987846c29f
eqh2-hq3g-pf40 | 1 |  | J7 Rw10 | 1308000079 | 18-04-2017 20:05:03 CEST | Tuyisenge Vianney | 00:08:11 | 2017 | Rwanda | Rulindo | Tumba | Taba | Ruvumba |  |  | Water point chez Darage/Nyirambuga pumping system | 30604 |  | 109 | 109 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Water is supplied in the inlet storage tank however it does not reach this water point.The people have requested to the Water system managing operators to come and fix the issue till now people are fetching from Nyakagezi spring that also got damaged | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7399670699009397 | 29.955281287188633 | 1918.9 | 27xkwjz4 | 2 | https://waterforpeople.s3.amazonaws.com/images/cbd5ce63-3d76-4716-a724-f56e7741b0b7.jpg | 2012 | Does Not Function | No |  |  |  | No | Water does not currently reach the system | Does Not Function | Water is supplied in the inlet storage tank however it does not reach this water point.The people have requested to the Water system managing operators to come and fix the issue till now people are fetching from Nyakagezi spring that also got damaged | b843484c88699d3e8242c4a8b3ecf
5qa7-yjb2-k1ts | 1 |  | J7 Rw23 | 1198700151 | 08-03-2017 16:42:54 CET | Rugirangoga Augustin | 00:33:59 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 1789 |  | 192 | 100 | 92 | Yes | Piped Network -- Gravity Only |  | 2017 | Yes | Karambi Gitovu | Governement (District, WASAC) and Water For People | This water systems partially is functional | 3 | Spring | -1.6451884854420848 | 29.8894890194251 | 1747.3 | 23kty3v2 |  | Yes | 45 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Poor | 45 | Yes | 2 |  | 2016 | Does Not Function | 1000 | Yes | 3 | -1.6508954090796335 | 29.88434869350536 | 1733.1 | 23u9wm8r |  | 2012 | Poor | Yes | 1 | Distribution Chamber |  | 2012 | Normal | Yes | 2 |  | 2016 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6151845490240373 | 29.886537503479744 | 1813 | 2277tp0x | 2 |  | 2017 | Does Not Function | No |  |  |  | Yes |  | Poor | System needs rehabilitation | dd1d8e318680398e34338f776e6c6ff
dfey-h6wv-jmrk | 1 |  | J7 Rw15 | 1212380330 | 09-03-2017 08:15:30 CET | Mukakarangwa Assoumpta | 00:19:50 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Gisoro-Nyundo network | 2297 |  | 188 | 30 | 158 | Yes | Piped Network -- Gravity Only |  | 2013 | Yes | Nyarunyinya,nyabitare,Rwintare | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.840451151026817 | 29.948165560771624 | 1795.9 | 2cjrthy1 | https://waterforpeople.s3.amazonaws.com/images/6764d69a-0e40-449d-b252-461cf161587b.jpg | Yes | 13 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/ecfb0156-0761-44ee-83c6-9a11945766ed.jpg | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 13 | Yes | 2013 | https://waterforpeople.s3.amazonaws.com/images/70813865-1167-4467-9078-bab3acde609e.jpg | 2013 | Normal | 30 | Yes | 6 | -1.8406374522240199 | 29.94836287627501 | 1783.7 | 2ck2jau3 | https://waterforpeople.s3.amazonaws.com/images/1609deb8-4696-4953-87ad-968c51591d89.jpg | 2013 | Poor | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout | https://waterforpeople.s3.amazonaws.com/images/9c529fe1-26ba-4b20-ac67-83c959b180ae.jpg | 2013 | Normal | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/0f71b89f-a8fd-4fa6-bde8-7ebe312becf7.jpg | 2013 | Normal | 7000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8415815986123756 | 29.9484142532025 | 1777.8 | 2cln3hb0 | 1 | https://waterforpeople.s3.amazonaws.com/images/4ae880b2-6c7f-4c22-9bfc-2cf76528aece.jpg | 2013 | Poor | No |  |  |  | Yes |  | Normal | -same tank do not have flotter -water point does not have tap stand | a5c129727a7ff4f58c9c5b1b35b6045
8qm9-45dj-pnhu | 1 |  | J7 Rw24 | 1203841968 | 16-03-2017 08:55:02 CET | Kabalisa Manzi Christella | 00:09:05 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Gihinga |  |  | 0 | 6572 |  | 850 | 850 | 0 | Yes | Piped Network with Pump |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8024532750946713 | 30.042616473975034 | 1748.3 | 2asxebwq |  | Yes | 3 | Yes | 1 |  |  | 2016 | Normal | 3 | Yes | 1 |  | 2016 | Normal | 35000 | Yes | 2 | -1.7575350016834248 | 30.02449548695202 | 1874.2 | 28qmz6dw |  | 2016 | Normal | Yes | 6 |  |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 1000 | Yes | 3 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.75722692409949 | 30.024248553921026 | 1850.1 | 28q4iqmq | 1 | https://waterforpeople.s3.amazonaws.com/images/f9b37fd4-0cbb-46ba-ac96-52771cee7e21.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | fe8fca4dcd0b9fd28c97e63366a5e17
1cu9-n78w-svtt | 1 |  | J7 Rw23 | 1200041194 | 15-03-2017 06:11:05 CET | Rugirangoga Augustin | 00:18:59 | 2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatiba |  |  | Gihanga II |  |  | 151 | 151 | 0 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | gatiba gatwa | Governement (District, WASAC) and Water For People | this networ is ok | 1 | Groundwater (well, etc.) | -1.6358367374763643 | 29.917613599705728 |  | 235d9tgo |  | Yes | 15 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 15 | Yes | 1 |  | 2016 | Normal | 7000 | Yes | 3 | -1.6498521069502532 | 29.917613599705728 | 1996.9 | 23sjzjl4 |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6505921076778869 | 29.930834659033543 | 1792.1 | 23ts1mgc | 2 | https://waterforpeople.s3.amazonaws.com/images/1b372f17-3b8e-4190-bf41-6535d7f24fe6.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 499b93ba79832fb5f0e5f7e35a75cd
ppx7-m356-u5wf | 1 |  | J7 Rw15 | 1243830080 | 21-03-2017 18:17:08 CET | Mukakarangwa Assoumpta | 00:11:35 | 2017 | Rwanda | Rulindo | Kinihira | Butunzi | Kiniihira |  |  | Miyove- Kinihira | 10452 |  | 118 | 60 | 58 | Yes | Piped Network -- Gravity Only |  | 2001 | Yes | Barayi | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6694552396188131 | 29.95963025353782 | 1975.5 | 24oyx5l8 | 1 | https://waterforpeople.s3.amazonaws.com/images/52692c34-1c7a-4d2f-8ccf-1011fb363cde.jpg | 1989 | Poor | No |  |  |  | Yes |  | Poor |  | e2b184ef8256bbeb3931315ca385
dx9d-kuk2-ub | 1 |  | J7 Rw15 | 1200020311 | 09-03-2017 20:34:41 CET | Mukakarangwa Assoumpta | 00:07:18 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Kigali |  |  | Gisoro- Nyundo network | 2297 |  | 220 | 25 | 195 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.840451151026817 | 29.948165560771624 | 1795.9 | 2cjrthy1 |  | Yes | 13 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 13 | Yes | 1 |  | 2013 | Normal | 30 | Yes | 6 | 1.8406374522240199 | 29.94836287627501 | 1783.7 | 2ck2jau3 |  | 2013 | Poor | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 7000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8718062331888126 | 29.945262935223454 | 1407.7 | 2dzmbfek | 1 | https://waterforpeople.s3.amazonaws.com/images/a25cf019-cb01-4f8e-8d57-d83d51dc3cff.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 2ae61b36ef6b59e631d028c374495952
yw1b-sgv0-g47r | 1 |  | J7 Rw10 | 1235010151 | 02-01-2015 12:32:19 CET | Tuyisenge Vianney | 00:06:12 | 2017 | Rwanda | Rulindo | Buyoga | Mwumba | Gakoma |  |  | Water point at Gakoma/Nyirambuga pumping | 30604 |  | 176 | 176 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point at Gakoma It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7000883547950039 | 30.007755782972374 | 2021.2 | 263mjvvx | 2 | https://waterforpeople.s3.amazonaws.com/images/a1c96d2f-cf90-4295-b56a-8bb228740cb9.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point at Gakoma It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water | b5303d932afa972d889b1566d59e2014
avwc-5ub0-v49r | 1 |  | J7 Rw7 | 1442620156 | 04-06-2017 07:40:17 CEST | Rugirangoga Augustin | 00:24:21 | 2017 | Rwanda | Rulindo | Kisaro | Mubuga | Rutabo |  |  | gahama | 10234 |  | 148 | 120 | 28 | Yes | Piped Network with Pump |  | 2017 | No |  |  |  | 2 | Spring | -1.6675834297797398 | 30.042871221056945 | 1965.7 | 24lvl43w | https://waterforpeople.s3.amazonaws.com/images/4b3ed9fd-ba70-4ade-9314-87327c892c68.jpg | Yes | 65 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/5f08c5e6-7d26-48a8-b484-5274a1dd1b4a.jpg | "Springbox" --Intake Structure at a Spring | 2017 | Normal | 65 | Yes | 1 |  | 2017 | Normal | 12000 | Yes | 2012 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | No | [5 empty] | Yes | 2 |  | 2012 | Normal | 12000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6674048832916177 | 30.04261639028342 | 1930.4 | 24lkvb7u | 1 | https://waterforpeople.s3.amazonaws.com/images/dd83d082-1924-491f-b231-03bce5127698.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | iri vomo ni rishya | eaf1a7fbb292b498a73793ddf1735c3
93uh-udmp-ppyr | 1 |  | J7 Rw19 | 1216730127 | 13-03-2017 07:29:19 CET | Kayinamura Innocent | 00:25:43 | 2017 | Rwanda | Rulindo | Ngoma | Mugote | Kiboha |  |  | Kabarore-Ngoma- Nyabuko network | 8284 |  | 74 | 35 | 39 | Yes | Piped Network with Pump |  | 2014 | Yes | Nyabuko, Kagwa, Kiruri, Busizi, Ngaru, Kirungu, Kiboha and Kigina | Governement (District, WASAC) and Water For People | The network has 17 water points and it serves 8 villages | 4 | Spring | -1.8123357076877171 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦Collection Chamber | 2014 | Normal | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.8118879629206273 | 30.003478805087182 | 2031 | 2b8iu32a |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 4 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8129159769832672 | 30.000598174707275 | 1957.3 | 2ba85qcl | 17 | https://waterforpeople.s3.amazonaws.com/images/cec27df6-6f49-43be-ace7-7b2ef6ffb0ff.jpg | 2014 | Normal | Yes | 1 | 10 | it was due to the road construction | Yes |  | Normal | - the network has 17 water points - water points are in good operations conditions except the water point at the source that is damaged - 4 water points don't have water today - the pipes are in good conditions - the pump is not working properly as it was expected during Design, today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy for the pump - the transformer at the pumping station doesn't offer the required energy for the pump - the anti-hammers of pumps are not functioning because of bad installation of pumping house - the system has 4 pumps units with two units pumping in one direction towards Nyabuko, towards Ngoma sector office | 6b9d5c4781320524b12057124ea45d
4tye-mr0a-95xc | 1 |  | J7 Rw8 | 1190180874 | 07-03-2017 11:09:04 CET | Amani Desire | 00:28:20 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 911 |  | 118 | 32 | 86 | Yes | Piped Network -- Gravity Only |  | 1997 | No |  | Governement (District, WASAC) and Water For People | -the Network has been totally rehabilitated in 2016 -in the rain season one source is contaminated with soil and it changes the color of water | 2 | Spring | -1740882760889992 | 29.933869978471744 | 1946.2 | l57wd97toq |  | Yes | 30 | Yes | 2 |  | start and collection chamber | 2016 | Normal | 30 | Yes | 1 |  | 2016 | Normal | 700 | Yes | 1 | -1.7398552316859899 | 29.93657178593082 | 1752.3 | 27xecs6d |  | 2016 | Normal | Yes | 2 | washout and Air release chambers |  | 2016 | Normal | Yes | 2 |  | 2016 | Normal | 800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7396455359844445 | 29.936633784817865 | 1783.9 | 27x1uoh2 | 5 | https://waterforpeople.s3.amazonaws.com/images/165991aa-477a-4b11-a57f-88baeecace24.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | -The water point is not in use due to the unwilling of the people to pay water because there are many springs around where people take water for free _in the rain season water from source contains soil and changes the color | d3f5a12d67a1fb9ea490c985655e6f
1c7w-hmag-9u59 | 1 |  | J7 Rw8 | 1199670570 | 07-03-2017 20:49:35 CET | Amani Desire | 00:31:46 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  | Kibuye | 1232 |  | 186 | 37 | 149 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | the network is new and it is in a good operational condition | 2 | Spring | -1.7319103236390618 | 29.92858227727732 | 1850.6 | 27k9mlsl | https://waterforpeople.s3.amazonaws.com/images/3df32e74-6435-4468-adba-89cb7013a1fc.jpg | Yes | 45 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/4388001e-c3ab-48f8-99ea-fd5d2d277eae.jpg | start and collection chamber | 2016 | Normal | 45 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/443399f4-cab3-43dd-a58b-02e10bb4f4f9.jpg | 2016 | Normal | 1500 | No | [8 empty] | Yes | 1 | washout chamber | https://waterforpeople.s3.amazonaws.com/images/5405c04c-930d-4eb3-89a4-f26403065347.jpg | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7316108891716637 | 29.928393523475364 | 1821.6 | 27jrrln7 | 2 | https://waterforpeople.s3.amazonaws.com/images/65d5c88b-ddec-40d4-b104-47e02b687002.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | the network is new it is in a good operational conditions water points are in good operation condition | a8aa749b13e41463edbe87a954879c0
uknu-auw7-svge | 1 |  | J7 Rw10 | 1300190153 | 15-04-2017 23:32:30 CEST | Tuyisenge Vianney | 00:13:49 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Gifumba |  |  | Gifumba gravity system |  |  | 188 | 188 | 0 | Yes | Piped Network -- Gravity Only |  | 2010 | No |  | Local government | The water point is nolonger operationa.The GTS[ Former water management private operator ] has stoped working on the maintenance issue saying that District will tackle the issue | 1 | Spring | -1.8402167628378279 | 29.95851325730038 | 1898.8 | 2cjdj3i9 |  | Yes | 50 | No | [5 empty] | 50 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/66ce6188-4d82-4dc5-bfeb-f1f9c7f35ea1.jpg | 2010 | Does Not Function | 700 | Yes | 1 | -1.8424785208879615 | 29.96444761663585 | 1775.3 | 2cn4329o | https://waterforpeople.s3.amazonaws.com/images/2472c571-cc6a-4935-bec6-9c1d9fbc5776.jpg | 2010 | Poor | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.842414402469449 | 29.96453456607935 | 1762.4 | 2cn0ign1 | 0 | https://waterforpeople.s3.amazonaws.com/images/ed12c51e-845f-431d-b276-8b36f6134691.jpg | 2010 | Does Not Function | No |  |  |  | No | The water point is nolonger operationa.The GTS[ Former water management private operator ] has stoped working on the maintenance issue saying that District will tackle the issue | Poor | The water point is nolonger operationa.The GTS[ Former water management private operator ] has stoped working on the maintenance issue saying that District will tackle the issue | 7951d9407a449a8dac6783979ebb4353
96ek-6p84-dmr0 | 1 |  | J7 Rw10 | 1234210555 | 22-03-2017 14:32:00 CET | Tuyisenge Vianney | 00:03:17 | 2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point/AEP Kigarama gravity | 2621 |  | 243 | 243 | 0 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | This is one of water points located in grouped area Kigarama village.It is normally operational and functional | 1 | Spring | -1.7875070118422336 | 29.92431620181639 | 2051.7 | 2a47b9m3 |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7776924220492256 | 29.930985580169978 | 1863.4 | 29nz917x | 2 | https://waterforpeople.s3.amazonaws.com/images/7c5e5ca6-40d4-4c18-90a9-131827a9b8de.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | This is one of water points located in grouped area Kigarama village.It is normally operational and functional | f41e95fcfc9a7845d48b3dd17883545
gfdg-chre-6bk5 | 1 |  | J7 Rw10 | 1211790493 | 10-03-2017 15:07:32 CET | Tuyisenge Vianney | 00:06:43 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Ruhanga |  |  | Ruhanga2 water point/Tare-Rusiga pumping | 9577 |  | 147 | 147 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Ruhanga2 water point operates normally | 10 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 4000 | Yes | 1 | -1.7525309526056119 | 29.907799073589796 | 2208 | 28idaf0l | https://waterforpeople.s3.amazonaws.com/images/b87f7ad2-fbf2-48df-a17c-18b067beb9c6.jpg | 2015 | Normal | No | [5 empty] | Yes | 3 |  | 2015 | Normal | 8000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7522227437396922 | 29.908114209387904 | 2174 | 28hutz9l | 2 | https://waterforpeople.s3.amazonaws.com/images/e0ebcac6-2d3f-4744-ae1e-004f356939a5.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Ruhanga2 water point | c8fee1ab03ca668eef1546d5f797943
u5dd-pfye-87aj | 1 |  | J7 Rw8 | 1224050138 | 16-03-2017 08:48:57 CET | Amani Desire | 00:16:59 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gicumbi |  |  | Musenge Network | 6074 |  | 141 | 35 | 106 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber¦washout and Air release chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.770990621820735 | 29.94191950017113 | 1945.7 | 29cwclzv | 28 | https://waterforpeople.s3.amazonaws.com/images/f4df813e-1b67-428d-bbd4-e052947d8ec6.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | dece931c38a8ad7fcc73c12a266dec2
t7ap-njqw-55y4 | 1 |  | J7 Rw19 | 1216780219 | 13-03-2017 06:48:53 CET | Kayinamura Innocent | 00:30:32 | 2017 | Rwanda | Rulindo | Ngoma | Munyarwanda | Ngaru |  |  | Kabarore-Ngoma-Nyabuko network | 8284 |  | 106 | 56 | 50 | Yes | Piped Network with Pump |  | 2014 | Yes | Nyabuko, Kagwa, Kiruri, Busizi, Ngaru, Kirungu, Kiboha and Kigina | Governement (District, WASAC) and Water For People | The network has 17 water points and it serves 8 villages | 4 | Spring | -1.8123357076877171 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦Collection Chamber | 2014 | Normal | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.8118879629206273 | 30.003478805087482 | 2031 | 2b8iu32a |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 4 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.827752087785369 | 30.006530669915954 | 1956.6 | 2byrp04h | 17 | https://waterforpeople.s3.amazonaws.com/images/2fbdadfe-fb7e-4a0d-aef7-d983dd786b89.jpg | 2014 | Poor | Yes | 1 | 10 | it was due to the road Construction | Yes |  | Normal | -The network has 17 water points - water points are in good operation conditions except the water point at the source that is damaged - 4 water points don't have water toady - The pipe are in good conditions - The pump is not working properly as it was expected during Design, today the pump is pumping less than the qi quantity of water needed or expected during Design due to the lack of sufficient energy -The transformer at the pumping station doesn't offer the required energy for the pump - The anti-hammers of pumps are not functioning because of bad installation of pumping house - the system has 4 pumps units with twounits pumping in one direction towards Nyabuko, towards Ngoma sector office - The suction tank is in bad physical condition | 65bf663e36e6ec55c8bf39992b98daf9
fa26-4f6x-bse | 1 |  | J7 Rw15 | 1201250751 | 09-03-2017 06:43:17 CET | Mukakarangwa Assoumpta | 00:07:47 | 2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Kabagabaga |  |  | kirikumuryango network |  |  | 850 | 850 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse ,Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8900844326254285 | 29.95777498105821 | 1376.2 | 2etuntbt | 1 | https://waterforpeople.s3.amazonaws.com/images/4a5ec541-2b98-428a-af1a-bf5916e009c3.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | water point is for GS Kijabagwe | ffa2bd7ac735e03fe264fb4b861a376
1vfh-ej42-2sgv | 1 |  | J7 Rw8 | 1313980252 | 20-04-2017 14:37:41 CEST | Amani Desire | 00:15:30 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Karindi |  |  |  | 510 |  | 120 | 45 | 75 | Yes | Piped Network -- Gravity Only |  | 2007 | No |  |  |  | 1 | Spring | -1.7578467252021364 | 29.934200875734504 | 1873.5 | 28r5flfy | https://waterforpeople.s3.amazonaws.com/images/c7330b28-85c5-4e8b-aefd-9d2cf44f3eb2.jpg | Yes | 180 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/1bcb37a5-3081-468d-83f3-c4d53d80ccaf.jpg | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 180 | Yes | 1 |  | 2007 | Normal | 1000 | Yes | 1 | -1.7654627249632726 | 29.93269199258442 | 1824.8 | 293r3we6 | https://waterforpeople.s3.amazonaws.com/images/3e458f31-5e08-437f-994a-179bcd06086b.jpg | 1998 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7580489779060633 | 29.93419245007874 | 1843.1 | 28rhc9jh | 1 | https://waterforpeople.s3.amazonaws.com/images/f260b6df-92f6-48cf-b3e8-ef200b40632e.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | ee5ad135c0878ec3768f8723bd6eb361
15bm-040x-991c | 1 |  | J7 Rw8 | 1195650812 | 07-03-2017 10:31:03 CET | Amani Desire | 00:29:03 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 911 |  | 118 | 21 | 97 | Yes | Piped Network -- Gravity Only |  | 1997 | No |  | Governement (District, WASAC) and Water For People | Network have been totally rehabilitated in 2016 | 2 | Spring | -1.740882760889992 | 29.933869978471744 | 1846.2 | 27z3ofgq |  | Yes | 30 | Yes | 2 |  | start and collection chamber | 2016 | Normal | 30 | Yes | 1 |  | 2016 | Normal | 700 | Yes | 1 | -1.7398552316859899 | 29.93657178593082 | 1752.3 | 27xecs6d |  | 2016 | Normal | Yes | 2 | washout and Valve chamber |  | 2016 | Normal | Yes | 2 |  | 2016 | Normal | 800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7387900805335443 | 29.93765421175512 | 1769.2 | 27vn8u28 | 5 | https://waterforpeople.s3.amazonaws.com/images/5a53537b-9d02-472e-b937-b27d2e923e15.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | In the rain season the water point is not used due to that water from the source contains soil and it changes the color | 862b7f7efa929efeea1c17e5e96e9cc
9hp4-rme9-7f5q | 1 |  | J7 Rw7 | 1246480097 | 23-03-2017 12:05:56 CET | Safari Bosco | 00:43:51 | 2017 | Rwanda | Rulindo | Murambi | Gatwa | Gatare |  |  | rwiseke | 9536 |  | 179 | 179 | 0 | Yes | Piped Network -- Gravity Only |  | 2001 | Yes | kingarama na gatare | Governement (District, WASAC) and Water For People | This system has issues in the dry season | 3 | Spring | -1.8081127252820783 | 30.019302406005654 | 1889.4 | 2b2ado4h |  | Yes | 55 | No | [5 empty] | 55 | Yes | 1 |  | 2001 | Normal | 1200 | Yes | 7 | -1.8083188633668612 | 30.018599981640595 | 1825.6 | 2b2mac7t |  | 2001 | Normal | No | [5 empty] | Yes | 1 |  | 2001 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.836326993528728 | 30.035793148924856 | 1756.9 | 2ccxxhs5 | 1 | https://waterforpeople.s3.amazonaws.com/images/e251880c-0e0a-4cdf-a773-80fb14884f27.jpg | 2001 | Normal | No |  |  |  | Yes |  | Normal |  | 7979bbe111e58489f64be42292ed758
gkkd-jx0t-6wj3 | 1 |  | J7 Rw8 | 1217440157 | 10-03-2017 10:24:35 CET | Amani Desire | 02:45:38 | 2017 | Rwanda | Rulindo | Ngoma | Kabuga | Kirambo |  |  | Kabarore-Ngoma-Nyabuko network | 8284 |  | 131 | 48 | 83 | Yes | Piped Network with Pump |  | 2014 | Yes | nyabuko,kagwa,kiruri,busizi,ngaru,kirungu,kiboha and kigina | Governement (District, WASAC) and Water For People | -The network has 17 water points and it serves 8 villages | 4 | Spring | -1.8123357076877171 | 29.96790053996267 | 1783.9 | 2b99ml0f | https://waterforpeople.s3.amazonaws.com/images/86346d6f-6fb2-4498-baa4-465e909eab39.jpg | Yes | 4 | Yes | 5 | https://waterforpeople.s3.amazonaws.com/images/5c34373d-0a9b-4503-b143-882e36735f22.jpg | "Springbox" --Intake Structure at a Spring¦collection chamber | 2014 | Normal | 4 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/171244fb-2cf1-4747-b177-0b6f3ae67201.jpg | 2014 | Normal | 8000 | Yes | 13 | -1.808716485895084 | 29.973362007273437 | 2001 | 2b3a3o2d | https://waterforpeople.s3.amazonaws.com/images/89c07166-50d8-46c5-97f2-4fcbeeb2b081.jpg | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/8a44cbdf-2c74-467b-bd11-9d1b822dfe54.jpg | 2014 | Poor | Yes | https://waterforpeople.s3.amazonaws.com/images/875b4895-4e32-47bc-85d9-507bafa68360.jpg | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.812458162235845 | 29.967670539637012 | 1818.2 | 2b9grs9o | 17 | https://waterforpeople.s3.amazonaws.com/images/b244db61-a806-4b0a-a52d-26585073a803.jpg | 2014 | Normal | Yes | 1 | 10 | it was due to the road construction | Yes |  | Normal | - The network has 17 water points -water points are in good operation conditions expect the water point at the source that is damaged - 4 water points don't have water today -the Pipes are in good conditions - The pump is not working properly as it was expected during Design, Today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy -the transformer at the pumping station does'nt offer the required energy for the pump - the anti hammers of pump are not functioning because of bad installation of pumping house - the system has 4 pumps units with two units pumping in one direction towards Nyabuko and other two in an other direction towards Ngoma Sector office - The suction Tank is in bad physical condition | 6b37f2a195f42052179924d37fe64cb
ffsw-m9ev-25k4 | 1 |  | J7 Rw26 | 1201010608 | 11-03-2017 10:12:28 CET | Byukusenge Elie | 00:09:58 | 2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 20456 |  | 50 | 45 | 5 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank | This network serves four sectors Cyungo,Rukozo, Base,Base and Kinihira, It has some problems in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible because it serves many populations and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2011 | Normal | 5 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6387442453989225 | 29.942185132885616 | 1902.2 | 23a6iyot | 29 | https://waterforpeople.s3.amazonaws.com/images/a50300ca-2d4a-4625-ad57-aed30445041f.jpg | 2011 | Normal | Yes | 10 | 25 | Bad tee connections and the types of pipeline needs rehabilitation | No | No water in distribution reservoir | Poor | No water available in this village due to water doesn't reach distribution reservoir in Gahwazi Village. | a9ecf581f43532459d02bca38c35a1
9x47-fbkt-7n2f | 1 |  | J7 Rw26 | 1212130068 | 11-03-2017 10:06:20 CET | Byukusenge Elie | 00:07:30 | 2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 20456 |  | 450 | 450 | 0 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank | This network serves four sectors Cyungo,Rukozo, Base,Base and Kinihira, It has some problems in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible because it serves many populations and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2011 | Normal | 5 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6246256445926717 | 29.947609527173515 | 1872.1 | 22mtuwk4 | 29 | https://waterforpeople.s3.amazonaws.com/images/f1d6941a-f2c2-44f7-aeff-c017120c5315.jpg | 2011 | Normal | Yes | 10 | 22 | Bad tee connections and the types of pipeline needs rehabilitation | Yes |  | Poor | Water tap in E.S.RUKOZO in good condition | 539764544abc57844595ac4bf1f57a40
8aqj-6jdn-gmvd | 1 |  | J7 Rw19 | 1216780216 | 13-03-2017 06:49:46 CET | Kayinamura Innocent | 00:34:04 | 2017 | Rwanda | Rulindo | Ngoma | Munyarwanda | Busizi |  |  | Kabarore-Ngoma-Nyabuko network | 8284 |  | 100 | 21 | 79 | Yes | Piped Network with Pump |  | 2014 | Yes | Nyabuko, Kagwa, Kiruri, Busizi, Ngaru, Kirungu, Kiboha and Kigina | Governement (District, WASAC) and Water For People | The network has 17 water points and it serves 8 villages | 4 | Spring | -1.8123357076877171 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦Collection Chamber | 2014 | Normal | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.8118879629206273 | 30.003478805087482 | 2031 | 2b8iu32a |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 4 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8240520982489739 | 30.006126961834365 | 1913.7 | 2bsnemal | 17 | https://waterforpeople.s3.amazonaws.com/images/7710a979-7e7a-4c08-9014-c8eb2fc1cef6.jpg | 2014 | Does Not Function | Yes | 1 | 10 | it was due to the road construction | Yes |  | Poor | -the network has 17 water points - water points are in good operation conditions except the water point at the source that is damaged - 4 water points don't have water toady - the pipe are in good conditions - the pump is not working properly as it was expected during Design, today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy - transformer at the pumping station doesn't offer the required energy for the pump - the anti-hammers of pumps are not functioning because of bad installation of pumping house - the system has 4 pump units with two units pumping in one direction towards Nyabuko, towards Ngoma sector office - the suction tank is in bad physical condition | 4f8f243f53e14ee6beaf22ed74914e
3tss-vcj9-db8a | 1 |  | J7 Rw24 | 1250560217 | 28-03-2017 08:51:12 CEST | Kabalisa Manzi Christella | 00:04:26 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Bikamba |  |  | Rwamugaza network | 14106 |  | 205 | 205 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8003377703611498 | 30.123521655372826 | 1570.8 | 2apf6gab | 1 | https://waterforpeople.s3.amazonaws.com/images/f358ec0e-626a-4ee5-ac7a-7069282edf83.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | f627e22f22349766bad35cc283ca3b7
p5yb-y2a5-uf1t | 1 |  | J7 Rw23 | 1218860184 | 15-03-2017 05:14:09 CET | Rugirangoga Augustin | 00:19:11 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 1789 |  | 192 | 180 | 12 | Yes | Piped Network -- Gravity Only |  | 2012 | Yes | karambi gitovu | Padiri |  | 3 | Spring¦Groundwater (well, etc.) | -1.6128815953757245 | 29.874655017548616 | 1956.1 | 223evzsq |  | Yes | 30 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 30 | Yes | 1 |  | 2016 | Normal | 6450 | Yes | 2 | -1.6111677762752643 | 29.88391135826884 | 1852 | 220khftj |  | 2012 | Normal | Yes | 2 | Distribution Chamber |  | 2012 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6131159820169751 | 29.88645508095031 | 1823 | 223skysw | 1 | https://waterforpeople.s3.amazonaws.com/images/50a08bf7-5eb4-496d-8e01-ccf32e76d6f1.jpg | 2012 | Poor | No |  |  |  | No | water is cut off | Normal | this network requires another storage tank in Gitovu community to serve the two last water tap and some possible extensions that will be designed as the community expands.another thing is that we have two intake tank,two . one was built in 2012 the other in 2016.three(3) sources. one in 2012, two others in 2016 | c93bb1fdb6e441e8a5ed3e97dc8fe2
ppag-a55x-xux3 | 1 |  | J7 Rw19 | 1254870065 | 25-03-2017 11:21:50 CET | Kayinamura Innocent | 00:15:55 | 2017 | Rwanda | Rulindo | Masoro | Shengampuri | Umubuga |  |  | Mutagata Gravity network | 26296 |  | 175 | 63 | 112 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | Ruri, Musenga, Rukurazo, Umubuga, Amataba, Rusine, Marenge |  |  | 1 | Spring | -1.8023389079852206 | 30.042447389592418 | 1691.2 | 2asq94nc |  | Yes | 8 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2004 | Poor | 8 | Yes | 1 |  | 2004 | Poor | 3500 | Yes | 6 | -1.8078446763653504 | 30.06649761552014 | 1669.8 | 2b1uaz5k |  | 2004 | Poor | Yes | 4 | Distribution Chamber¦Washout and Air release |  | 2004 | Poor | Yes | 2 |  | 2004 | Poor | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.807528822970007 | 30.06993964768306 | 1637.5 | 2b1b93tn | 12 | https://waterforpeople.s3.amazonaws.com/images/c1b80949-c652-4a23-b4e7-ec4f7f932254.jpg | 2016 | Normal | No |  |  |  | Yes |  | Poor | 1. the Extension to Nyabinyana village has 2 reservoirs and two water points which is under construction 2. this system have been constructed in 2004 3. it serve a party of Masoro Sector and other party is located in Gasabo District 4. 2 water points and one reservoir have been constructed in 2016. 5. in general, this network has 27 water points in which 12 are in Rulindo District and the remaining are in Gasabo District. | ca2845413e9a0b9672c47a4d292d4c8
s5ab-mgdj-cyf3 | 1 |  | J7 Rw10 | 1215161027 | 13-03-2017 21:09:46 CET | Tuyisenge Vianney | 00:06:41 | 2017 | Rwanda | Rulindo | Base | Gitare | Gihora |  |  | Gihora2 water point/Rutomvu gravity | 3015 |  | 101 | 101 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | The water point operates normally | 1 | Spring | -1.677891751247546 | 29.90118126071259 | 1802.6 | 252xezpf |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | Yes | 1 | -1.6692708920983566 | 29.89583514368797 | 1725.2 | 24oo7c7i | https://waterforpeople.s3.amazonaws.com/images/072266c1-bff3-49b3-982e-31b14e34060c.jpg | 2013 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6691736026729647 | 29.89561083661684 | 1713.3 | 24oi905o | 1 | https://waterforpeople.s3.amazonaws.com/images/6fb8f950-5cc9-4c48-941d-2b83b04c72e7.jpg | 2013 | Poor | No |  |  |  | Yes |  | Normal | The water point does no longer operate | 15b85928fb1883918ea619ce65bb491
1tyx-2jq3-wxfj | 1 |  | J7 Rw10 | 1229840204 | 03-01-2015 01:22:57 CET | Tuyisenge Vianney | 00:07:41 | 2017 | Rwanda | Rulindo | Tumba | Gahabwa | Kagusa |  |  | Kagusa water point/Nyirambuga pumping | 30604 |  | 146 | 146 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | The water point located at Kagusa operates normally and its water storage tank R100m3 serves the line to Mbogo and Gahabwa.One of the tank valve chamber has nolonger a cover.One tap stand valve has been closed | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.716469247268329 | 29.95476357073929 | 2147 | 26uprwd7 | https://waterforpeople.s3.amazonaws.com/images/e69318db-a7bd-478c-98fd-6d67f2bdce44.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7164263542115792 | 29.95512498991975 | 2152.8 | 26une5y7 | 2 | https://waterforpeople.s3.amazonaws.com/images/9d996724-8e7e-4abc-a82c-ed3540d2bc30.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The water point located at Kagusa operates normally and its water storage tank R100m3 serves the line to Mbogo and Gahabwa.One of the tank valve chamber has nolonger a cover.One tap stand valve has been closed | 58c2f293de76bc9e70296b2199ebce90
mbec-22k3-0dru | 1 |  | J7 Rw15 | 1239570475 | 21-03-2017 14:01:28 CET | Mukakarangwa Assoumpta | 00:20:06 | 2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Buhita |  |  | Miyove-Kinihira | 10452 |  | 131 | 60 | 71 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.648087716840147 | 29.97889704214982 | 1887.7 | 23pmltzg | 2 | https://waterforpeople.s3.amazonaws.com/images/896f8c2e-2d2b-4567-8ebd-66904ea5a3c6.jpg | 2015 | Normal | No |  |  |  | Yes |  | Poor | Other concrete structures they are some constructed in 1989 and other constructed by world vision in 2015 | a4335dd1627213f52b2ad09061223
vcmf-47r6-swbd | 1 |  | J7 Rw15 | 1223400173 | 12-03-2017 13:19:37 CET | Mukakarangwa Assoumpta | 00:10:49 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Muvumu |  |  | Muvumu- Taba |  |  | 400 | 400 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.8242130164596562 | 29.931083430301516 | 1700.7 | 2bswxje6 |  | Yes | 25 | No | [5 empty] | 25 | Yes | 1 |  | 2013 | Normal | 800 | Yes | 3 | 1.828985219687556 | 29.926634523104315 |  | 2c0sxawy |  | 2013 | Poor | Yes | 9 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 7500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.851508335547793 | 29.91780859198214 | 1623.9 | 2d21ph62 | 1 | https://waterforpeople.s3.amazonaws.com/images/e733b2e5-35d4-4bec-8a86-e885399b7570.jpg | 2013 | Normal | Yes | 1 | 3 | Those rehabilitating Rushinya source had strayed it | Yes |  | Poor | Water point is for school of Muvumu primary. | c8ff549e129eaaf9ff16c3f1d8e2b69
a4v9-yxc8-nceg | 1 |  | J7 Rw10 | 1214530281 | 10-03-2017 13:13:09 CET | Tuyisenge Vianney | 00:05:32 | 2017 | Rwanda | Rulindo | Bushoki | Mukoto | Marembo |  |  | Water point at Marembo school/Tare-Rusiga pumping | 9577 |  | 90 | 90 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point located at Marembo school operates normally | 10 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 4000 | No | [8 empty] | No | [5 empty] | Yes | 1 |  | 2015 | Normal | 8000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.719280136073788 | 29.90005435978609 | 2112.1 | 26zdo4jc | 2 | https://waterforpeople.s3.amazonaws.com/images/0f2183d3-9b29-46e4-a222-5116aa8257e9.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The Marembo school water point operates normally | 516cbcd7f116b7ef1fc29134d9ffd5
p3jf-kjkg-kesy | 1 |  | J7 Rw10 | 1207271232 | 10-03-2017 14:37:25 CET | Tuyisenge Vianney | 00:04:19 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Ruhanga |  |  | Ruhanga center Water point/Tare-Rusiga pumping | 9577 |  | 147 | 147 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This is Rugaha center point also serving Gakenke people | 10 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 4000 | No | [8 empty] | No | [5 empty] | Yes | 3 |  | 2015 | Normal | 8000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7394875585022915 | 29.90395031691508 | 2124.8 | 27wsbqjj | 2015 | https://waterforpeople.s3.amazonaws.com/images/d6c7547b-243e-41fa-b387-85faae73296e.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Ruhanga water point operates normally | 578c9d1f28587031f47176ae3343e2
ttnh-gusb-n4pn | 1 |  | J7 Rw10 | 1220451011 | 13-03-2017 21:12:55 CET | Tuyisenge Vianney | 00:06:23 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Rugote |  |  | Rugote water point/Rutomvu gravity system | 3015 |  | 147 | 147 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | The source is well captured. And the water point operates normally | 1 | Spring | -1.677891751247546 | 29.90118126071259 | 1802.6 | 252xezpf |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | Yes | 1 | -1.6745472927200253 | 29.89679022983813 | 1749.7 | 24xdys0n | https://waterforpeople.s3.amazonaws.com/images/eacbd87c-bd67-42f5-99e7-3a3d6107e3aa.jpg | 2013 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6744953931238238 | 29.896645075497855 | 1745.8 | 24xazlzq | 1 | https://waterforpeople.s3.amazonaws.com/images/a7730357-4327-434f-9103-78b01493e215.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | The water point operates normally | 2ca4f0992d37a4731a3631765f1cbfbe
wd3a-5wh9-h89v | 1 |  | J7 Rw19 | 1331751984 | 24-04-2017 07:11:34 CEST | Kayinamura Innocent | 00:19:17 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Gashinge |  |  | Mutagata motorised network | 26296 |  | 229 | 149 | 80 | Yes | Piped Network with Pump |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release chamber |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7840194483165286 | 30.04007336894776 | 1904.3 | 29yfj0ds | 64 | https://waterforpeople.s3.amazonaws.com/images/dd850672-a10f-48c5-9ef1-ffb2985f1017.jpg | 2016 | Poor | No |  |  |  | Yes |  | Normal | The System is new, in General it is in good conditions | 30b04390e081a59decc15587d7915676
7x9k-eyau-4b2a | 1 |  | J7 Rw23 | 1320210070 | 23-04-2017 14:42:46 CEST | Rugirangoga Augustin | 00:26:51 | 2017 | Rwanda | Rulindo | Buyoga | Gitumba | Rutabo | [5 empty] | 128 | 80 | 48 | Yes | Piped Network with Pump |  | 2014 | Yes | gatare gatenderi shagasha |  |  | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 11 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2014 | Normal | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 9000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6724430220826076 | 30.043354536375723 | 2013.1 | 24twxs41 | 1 | https://waterforpeople.s3.amazonaws.com/images/f9e28cf0-0832-437e-827f-fbcb21c7e11f.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | 912d2395fdcc3635f54544f7195e58c
sbvv-u9ac-m4ef | 1 |  | J7 Rw24 | 1223931202 | 16-03-2017 08:45:32 CET | Kabalisa Manzi Christella | 00:07:12 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Gihinga |  |  | 0 | 6572 |  | 850 | 850 | 0 | Yes | Piped Network with Pump |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8024532450946713 | 30.042616473975034 | 1748.3 | 2asxebwq |  | Yes | 3 | Yes | 1 |  |  | 2016 | Normal | 3 | Yes | 1 |  | 2016 | Normal | 35000 | Yes | 2 | -1.7575350016834248 | 30.02449548695202 | 1874.2 | 28qmz6dw | https://waterforpeople.s3.amazonaws.com/images/49bd2091-1b7e-4b06-93bc-b1e84eb13d23.jpg | 2016 | Normal | Yes | 6 |  |  | 2016 | Poor | Yes | 1 |  | 2016 | Normal | 1000 | Yes | 3 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7575206631146125 | 30.024687350390252 | 1884.1 | 28qmdqs6 | 1 | https://waterforpeople.s3.amazonaws.com/images/fb2883a2-4683-4b37-8ef1-ee265f6808dc.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 46203a54cfee269c1afcd6414c9d9
axnt-7t7f-ww1d | 1 |  | J7 Rw19 | 1195120568 | 07-03-2017 12:26:49 CET | Kayinamura Innocent | 00:14:34 | 2017 | Rwanda | Rulindo | Mbogo | Mushali | Nyakabuye |  |  | Matyazo network |  |  | 147 | 147 | 0 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | Buyanja, Buraro, Nyakabuye | Governement (District, WASAC) and Water For People |  | 3 | Spring | -1.7856001537024087 | 29.978428885393118 | 1894.3 | 2a126x3c |  | Yes | 17 | Yes | 4 |  | "Springbox" --Intake Structure at a Spring¦Collection Chamber | 2016 | Normal | 17 | Yes | 1 |  | 2016 | Normal | 4300 | Yes | 1 | -1.7705795933776213 | 29.968679108343068 | 1834.4 | 29c7cesm |  | 2016 | Normal | Yes | 2 | Air release chamber, Washout chamber |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 1800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7836981801444904 | 29.973921507906166 | 1852.4 | 29xwh4ij | 4 | https://waterforpeople.s3.amazonaws.com/images/cc8fc540-bbda-4f4c-95bb-c301c490aad1.jpg | 2016 | Does Not Function | Yes | 1 | 30 | Taps were damaged | No | Broken parts | Poor | People rather use water from sources other than this water point because the springs are near by. | 69bcc1d37b64eeef344921aff665cad7
rafe-se9d-mue7 | 1 |  | J7 Rw26 | 1216490605 | 12-03-2017 07:19:35 CET | Byukusenge Elie | 00:10:55 | 2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Nyamagana | 20456 |  | 100 | 95 | 5 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank | This network serves four sectors Cyungo,Rukozo, Base,Base and Kinihira, It has some problems in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible because it serves many populations and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2011 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 1 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6499541768028827 | 29.936405538862207 | 1813.4 | 23spxvs4 | 29 | https://waterforpeople.s3.amazonaws.com/images/e9dc74e5-04e7-4a8c-8c96-8089c4b3a74f.jpg | 2011 | Normal | Yes | 7 | 25 | Bad tee connections and the types of pipeline needs rehabilitation | Yes |  | Poor | Water available in Centre Marembo | 8788399772e9256cf24b3af56f85f39d
r0mc-pndk-yps | 1 |  | J7 Rw23 | 1214290344 | 15-03-2017 05:14:18 CET | Rugirangoga Augustin | 00:50:52 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 1789 |  | 192 | 180 | 12 | Yes | Piped Network -- Gravity Only |  | 2012 | Yes | karambi gitovu | Padiri | this network is not mmm | 1 | Spring¦Groundwater (well, etc.) | -1.6128815953757245 | 29.874655017548616 | 1956.1 | 223evzsq |  | No | 30 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring¦Well | 2016 | Normal | 30 | Yes | 1 |  | 2016 | Normal | 6450 | Yes | 3 | -1.6111677762752643 | 29.8839135826884 | 1852 | 220khftj | https://waterforpeople.s3.amazonaws.com/images/04d09ba0-1dee-4e26-a00c-f574d9b17f8a.jpg | 2012 | Normal | Yes | 2 | Distribution Chamber |  | 2016 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6111224814505243 | 29.883911859642673 | 1830.6 | 220i3pef | 1 | https://waterforpeople.s3.amazonaws.com/images/86a03212-dec4-4b40-a269-9c36bef855e1.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | no many problems to this network | 8de95086eacac3efd7bc93b5fac1f55
h8uq-1yre-hvct | 1 |  | J7 Rw15 | 1210760249 | 09-03-2017 04:51:27 CET | Mukakarangwa Assoumpta | 00:07:25 | 2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Kabagabaga |  |  | kirikumuryango network |  |  | 181 | 75 | 106 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦Ventouse,washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.894361905159083 | 29.962872286450388 | 1352.2 | 2f0xhca4 | 1 | https://waterforpeople.s3.amazonaws.com/images/9b59582a-133c-4d58-9cb5-051e83614bee.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | d8dc693998a851222df5b6722ccf6163
38m6-30ue-5pyp | 1 |  | J7 Rw15 | 1210760244 | 08-03-2017 22:55:11 CET | Mukakarangwa Assoumpta | 00:05:43 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Rutonde |  |  | kirikumuryango network |  |  | 241 | 98 | 143 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 11 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8944151824826687 | 29.972088124921026 | 1446.5 | 2f10gidk | 1 | https://waterforpeople.s3.amazonaws.com/images/c8ca8496-d323-4f41-bf5b-ece49cfb4a62.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 343d81ac2c173da85efae5ab698597f
56qv-jjr2-tcxt | 1 |  | J7 Rw10 | 1305650071 | 16-04-2017 22:04:20 CEST | Tuyisenge Vianney | 00:05:43 | 2017 | Rwanda | Rulindo | Base | Gitare | Mugenda I |  |  | Gitare center water point/Nyirambuga pumping system | 30604 |  | 117 | 117 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Local government | The water point is operational however they last saw water yesterday.This is a collection of 2 catchment area of Nyirambuga1 and Nyirambuga2 with almost 8 sources | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.6671416223971065 | 29.9034225593216 | 2033.8 | 24l5e0ey | https://waterforpeople.s3.amazonaws.com/images/ca55f353-06aa-47ff-8579-7b5399a8efb2.jpg | 2012 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6649563913692509 | 29.902071345166085 | 2005 | 24hj02x8 | 2 | https://waterforpeople.s3.amazonaws.com/images/f47ee31e-16d3-486d-954d-529f56ffaeaf.jpg | 2012 | Normal | No |  |  |  | No | The water point is operational however they last saw water yesterday.This is a collection of 2 catchment area of Nyirambuga1 and Nyirambuga2 with almost 8 sources | Normal | The water point is operational however they last saw water yesterday.This is a collection of 2 catchment area of Nyirambuga1 and Nyirambuga2 with almost 8 sources | ac48543ac77cca41e24154aa3a5f692
4xw7-4gga-cak4 | 1 |  | J7 Rw10 | 1207380139 | 09-03-2017 11:06:38 CET | Tuyisenge Vianney | 00:12:29 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Gasiza center water point served by gravity before Tare pumping | 9577 |  | 228 | 228 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Gvt and water for people | This water point at Gasiza center above the road nearby Caritas storage,hasn't operated since inauguration of the Tare-Rusiga water pumping system | 8 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 4000 | Yes | 1 | -1.7304290449564053 | 29.91775279527241 | 1818.8 | 27hsx0kp | https://waterforpeople.s3.amazonaws.com/images/648da7e8-09b9-4b6f-b721-ddd2227b032d.jpg | 2015 | Normal | No | [5 empty] | Yes | 1 |  | 2015 | Normal | 2000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7304904469243736 | 29.917866759264747 | 1803.2 | 27hx31t6 | 1 | https://waterforpeople.s3.amazonaws.com/images/472e7ea0-f030-4c49-a83a-cd5b14552093.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The water point doesn't deliver water to the people however its storage tank has water. The problem is the water point water cannot be paid due to lack of clients who consume water from Nyagahondo water system constructed in 2010 by Caritas. | b5cbdc9ab49148adb634a7c95ba552dc
32rw-hy94-qbwy | 1 |  | J7 Rw19 | 1203832263 | 17-03-2017 05:22:57 CET | Kayinamura Innocent | 00:20:57 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 6074 |  | 135 | 67 | 68 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma, Karehe, Rutonde, Gitaba, Kiruri, Buhera, Ruhanya, Kibamba and karindi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.93859037216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7800353621166856 | 29.956941933853315 | 2213.4 | 29rukgz5 | https://waterforpeople.s3.amazonaws.com/images/658a3145-f6af-4fff-9b16-0f6122c96e8e.jpg | 2014 | Normal | Yes | 8 | Washout and Air release chamber | https://waterforpeople.s3.amazonaws.com/images/c54b99ee-ddfb-43de-ba1e-24d9b217c507.jpg | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7777704154866751 | 29.95591343073154 | 2204.7 | 29o40i93 | 28 | https://waterforpeople.s3.amazonaws.com/images/5726a620-55ef-4e79-b854-2b5124c90d87.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | 1. the system has two Pumps but one is damaged and is not working, only one pump is used to pump water 2. Eleven (11) water points served by the distribution reservoir R 50m3 located at Kibamba village do not have water today because water don't reach this reservoir, there is not water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5. one water point doesn't Function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water and reservoir being under construction | 346599d1cc2fd493c2e8cc491baec12
qdwp-9ry3-qhf | 1 |  | J7 Rw15 | 1210770169 | 08-03-2017 20:29:26 CET | Mukakarangwa Assoumpta | 00:09:01 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyarunyinya |  |  | kinywamagana pumping network | 6436 |  | 132 | 92 | 40 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8418331346075192 | 29.94208485121125 | 1733.2 | 2cm1zbdo | 1 | https://waterforpeople.s3.amazonaws.com/images/969ae971-74fd-42e3-afc5-654188fd2451.jpg | 2013 | Does Not Function | No |  |  |  | Yes |  | Does Not Function | this water point does not function because water can not reach to the water point | 86b8cd986b41e5d8b393908c1d628d7d
jmpj-4fq1-bvhv | 1 |  | J7 Rw15 | 1200310658 | 08-03-2017 23:02:18 CET | Mukakarangwa Assoumpta | 00:07:40 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Rutonde |  |  | kirikumuryango network |  |  | 1350 | 1350 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8945586414373776 | 29.971608993676146 | 1423.1 | 2f18skuc | 1 | https://waterforpeople.s3.amazonaws.com/images/e033903a-d6aa-4217-8cf0-5fb139b2446e.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | -water point is for EP Rutonde | 323677e0fe44d965e2f1545166b99025
76bp-dvwd-wevh | 1 |  | J7 Rw10 | 1306630060 | 16-04-2017 21:50:47 CEST | Tuyisenge Vianney | 00:05:34 | 2017 | Rwanda | Rulindo | Base | Gitare | Mugenda I |  |  | Gitare cell water point/Nyirambuga pumping system | 30604 |  | 117 | 117 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | The water point does not operate.All taps stands removed | 1 | Spring | -1.7265024345182751 | 29.95608995799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6591754170880912 | 29.89613597269885 | 2015.2 | 247yvj81 | 6 | https://waterforpeople.s3.amazonaws.com/images/7bc3d069-d5c3-4b72-a9cc-3bd1835493f5.jpg | 2012 | Does Not Function | No |  |  |  | No | The water point does not operate.All taps stands removed | Does Not Function | The water point does not operate.All taps stands removed | 455b955b2ded23158e59c53ec5a5174c
htw1-yv85-pmv5 | 1 |  | J7 Rw24 | 1254810720 | 28-03-2017 10:25:40 CEST | Kabalisa Manzi Christella | 00:05:26 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza network | 14106 |  | 229 | 229 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8103252124666829 | 30.113151299505382 | 1621.3 | 2b5xyhjf | 1 | https://waterforpeople.s3.amazonaws.com/images/9a22f7aa-8e7b-417e-a332-3f4740222e7c.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | 5ec1a0da353eb4ea322cad64be77c89
8vem-ymkj-qkkn | 1 |  | J7 Rw26 | 1214090087 | 11-03-2017 09:24:23 CET | Byukusenge Elie | 00:15:53 | 2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Nyamagana | 20456 |  | 850 | 850 | 0 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo village in Base Sector | Government and African Development Bank |  | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6503469284404462 | 29.936577918855278 | 1784.5 | 23td5sdh | 29 | https://waterforpeople.s3.amazonaws.com/images/07401600-e3d6-41c4-8a51-7319fc082b71.jpg | 2011 | Normal | Yes | 10 | 22 | Bad tee connections and the types of pipeline needs to be replaced | Yes |  | Poor | This is the second water tap used by the students and staff in G.S.Murambo | e795d125739bf1967b1d702ba9e6e8
41p1-9dtj-erqu | 1 |  | J7 Rw23 | 1246450343 | 24-03-2017 15:49:45 CET | Rugirangoga Augustin | 00:32:45 | 2017 | Rwanda | Rulindo | Buyoga | Butare | Ryanyirakayobe |  |  | Nyagahera |  |  | 96 | 80 | 16 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | karambi kankanga ryanyirakayobe | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6992109477296 | 30.0140024994200 | 1901.3 | 2626r6b0 |  | No | 16 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 16 | Yes | 1 |  | 2014 | Normal | 6800 | Yes | 3 | -1.7036674554172262 | 30.018283044778862 | 1811.3 | 269jp2ja | https://waterforpeople.s3.amazonaws.com/images/9ba4fca2-712f-46dc-9846-e153f9423408.jpg | 2014 | Normal | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7046728299542815 | 30.018388837980453 | 1691.9 | 26b7tumv | 2 | https://waterforpeople.s3.amazonaws.com/images/3d54221d-2cec-42fa-98dc-36d917707ee3.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal |  | c24bd4d3a2626d64969b0d1d5cb559
c03n-fpjp-hj7m | 1 |  | J7 Rw24 | 1252010185 | 28-03-2017 09:17:43 CEST | Kabalisa Manzi Christella | 00:14:16 | 2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Amahoro |  |  | Gicumbi Mutete network |  |  | 109 | 109 | 0 | Yes | Piped Network with Pump |  | 2009 | No |  | Government | The saorce of the system is in Gicumbi | 3 | Spring | -1.606505683129936 | 30.035988434546855 | 2024.6 | 21sv1h3b |  | Yes | 3 | Yes | 1 |  |  | 2009 | Normal | 30 | Yes | 2 |  | 2009 | Normal | 30000 | Yes | 5 | -1.6066092774364567 | 30.036029953620556 | 2040 | 21t0zt54 | https://waterforpeople.s3.amazonaws.com/images/eeb8d0b1-2730-4943-a094-6f69a9de95dd.jpg | 2009 | Normal | Yes | 10 |  |  | 2009 | Normal | Yes | 2 |  | 2009 | Normal | 30000 | Yes | 1 |  | 2009 | Poor | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6074161607210917 | 30.038211996325053 | 2007.1 | 21ud7x5q | 1 | https://waterforpeople.s3.amazonaws.com/images/c2ab7a14-78fd-47f5-ba63-a52c65422901.jpg | 2009 | Normal | No |  |  |  | Yes |  | Normal |  | b141201fdc3b5bec0493817ce99c27
2pp7-wtaq-32uc | 1 |  | J7 Rw10 | 1215161030 | 13-03-2017 21:20:14 CET | Tuyisenge Vianney | 00:11:03 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Cyili |  |  | Rutomvu source catchment area and intake structures | 3015 |  | 169 | 169 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | The water source functions well and operates well | 1 | Spring | -1.677891751247546 | 29.90118126071259 | 1772.8 | 252xezpf | https://waterforpeople.s3.amazonaws.com/images/b1d5cac1-2075-4d7a-85cc-78d840caa46c.jpg | No | 40 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/b9a7b172-0663-4799-bc6a-3e8b50f8b2d2.jpg | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 40 | Yes | 1 |  | 2013 | Normal | 100 | Yes | 1 | -1.677932928981033 | 29.90106573272952 | 1758.2 | 252zsq4i | https://waterforpeople.s3.amazonaws.com/images/c18e3302-7193-426b-857c-8450a9f64a8e.jpg | 2013 | Normal | No | [5 empty] | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/beb92f3c-dffe-4d3e-bb69-66ca7371066d.jpg | 2013 | Normal | 2000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.678059474812574 | 29.90114711031225 | 1772.8 | 2536xxdv | 1 | https://waterforpeople.s3.amazonaws.com/images/be6512f6-32e7-4318-8ef3-cff0ac48c5ba.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | The water point at source capturing is not well constructed neither protected | e4dc1cca8152ec88db2b08d2f6a47c2
5qyd-wrdg-cc57 | 1 |  | J7 Rw10 | 1316780077 | 20-04-2017 10:21:55 CEST | Tuyisenge Vianney | 00:04:10 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Gihanga |  |  | Water point at Rusura Primary school/Nyirambuga pumping | 30604 |  | 152 | 152 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | Operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | Yes | 1 | -1.6774662429578722 | 29.941063784105186 | 1795.4 | 2527td02 | https://waterforpeople.s3.amazonaws.com/images/b2e4ffec-ac79-4390-b24e-1cbe01acf546.jpg | 2017 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6774037766550376 | 29.940891234518883 | 1798.2 | 25248rdc | 2 | https://waterforpeople.s3.amazonaws.com/images/e8c7dbe9-45f2-4fda-851b-61bb69708c24.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | Operational | cb44f6a86670bf2b4bfcdb2baf2692d
cca0-np3r-d0jp | 1 |  | J7 Rw8 | 1224840115 | 16-03-2017 08:50:19 CET | Amani Desire | 00:14:22 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kalindi |  |  | Musenge Network | 6074 |  | 120 | 65 | 55 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi | WFP |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber¦washout and Air release |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7574491460132338 | 29.939210307192432 | 2076.1 | 28qhm9a8 | 28 | https://waterforpeople.s3.amazonaws.com/images/2be17e67-ac9f-45a6-a03b-a6ffebd45ae8.jpg | 2014 | Does Not Function | Yes | 8 | 30 | Water doesnt reach distribution reservoir R50m3 located at Ruhanya village that serves the water points in Ruhanya | No | water dont reach the distribution reservoir that serves this water point | Does Not Function | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | e02d156b1012542e4a7a6b675c8a242
xd5a-4fvf-kb0m | 1 |  | J7 Rw15 | 1242860079 | 21-03-2017 15:02:15 CET | Mukakarangwa Assoumpta | 00:12:16 | 2017 | Rwanda | Rulindo | Kinihira | Rebero | Ndusu |  |  | Miyove-Kinihira | 10452 |  | 146 | 60 | 86 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6598981682588185 | 29.99691264539973 | 1846.1 | 2495qrk1 | 2 | https://waterforpeople.s3.amazonaws.com/images/b993c4d2-c649-4c06-b731-79ab41815672.jpg | 2015 | Normal | No |  |  |  | Yes |  | Poor | Water point is in condition because is contructed in 2015 by world vision | fec243f8314f92fc4937d24ac42d54c
w59j-dre4-pv8u | 1 |  | J7 Rw15 | 1210760232 | 08-03-2017 22:16:46 CET | Mukakarangwa Assoumpta | 00:08:33 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Mwagiro |  |  | Kirikumuryango network |  |  | 139 | 50 | 89 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8759908849668039 | 29.972854394070215 | 1514.2 | 2e6js234 | 1 | https://waterforpeople.s3.amazonaws.com/images/fb47aa94-bc41-40db-afcb-a14c2bafd64f.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 2bc0e58dfefa4afda228bb111a7938d0
k0nk-tub6-7axp | 1 |  | J7 Rw19 | 1240960263 | 23-03-2017 07:41:57 CET | Kayinamura Innocent | 00:09:10 | 2017 | Rwanda | Rulindo | Masoro | Kabuga | Karambi |  |  | Mutagata motorised network | 26296 |  | 127 | 127 | 0 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.776497088980154 | 30.04852521867399 | 1811.8 | 29lzt1j9 | 64 | https://waterforpeople.s3.amazonaws.com/images/ab7926b8-19bd-449d-8af3-489d881d4346.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 86dd657e35581d40ef98e883d3c9d277
ujm1-gx5j-pyp | 1 |  | J7 Rw10 | 1220120431 | 13-03-2017 22:16:58 CET | Tuyisenge Vianney | 00:04:22 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Buramira water point/Buramira gravity | 1255 |  | 104 | 104 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | GoR | The water point operates well | 2 | Spring | -1.6776639816373493 | 29.911131429480132 | 2061.4 | 252jq0vb |  | Yes | 30 | No | [5 empty] | 30 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6772728432116262 | 29.911172527389688 | 1940.4 | 251wi49z | 1 | https://waterforpeople.s3.amazonaws.com/images/52e8bbe1-3881-49c7-8f45-9b43572e26c5.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The water point operates well | 4b33e979acfe4d022ba2dadab19150
15hx-5aqa-f12g | 1 |  | J7 Rw15 | 1208010142 | 08-03-2017 20:43:19 CET | Mukakarangwa Assoumpta | 00:06:56 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | kinywamagana pumping network | 6436 |  | 281 | 80 | 201 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.846340431881709 | 29.956459958425977 | 1937.7 | 2ctihtbg | 1 | https://waterforpeople.s3.amazonaws.com/images/a3ec432d-7c93-4eb0-8480-62c3ad45805d.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | 1787a2d7cc467c9710d0d2dddd58da3
8sfh-818c-sfsw | 1 |  | J7 Rw15 | 1208010152 | 08-03-2017 19:50:43 CET | Mukakarangwa Assoumpta | 00:06:17 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kigarama |  |  | kinywamagana pumping network | 6436 |  | 233 | 69 | 164 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8498680878749738 | 29.97389259517619 | 1897.4 | 2czc2ee2 | 1 | https://waterforpeople.s3.amazonaws.com/images/ef754520-cbf0-44af-a6e7-b513180bbe9c.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | ad87f64c49684cbd7fa1bd8031abbccb
rk3c-h63c-p81p | 1 |  | J7 Rw8 | 1197880596 | 07-03-2017 12:05:42 CET | Amani Desire | 00:17:48 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 911 |  | 118 | 31 | 87 | Yes | Piped Network -- Gravity Only |  | 1997 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.740882760889992 | 29.93386997871744 | 1846.2 | 27z3ofgq |  | Yes | 30 | Yes | 2 |  | start and collection chamber | 2016 | Normal | 30 | Yes | 1 |  | 2016 | Normal | 700 | Yes | 1 | -1.7398552316859899 | 29.93657178593082 | 1752.3 | 27xecs6d |  | 2016 | Normal | Yes | 2 | washout and Air release chamber |  | 2016 | Normal | Yes | 2 |  | 2016 | Normal | 800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7402438709445491 | 29.934969608884014 | 1793.7 | 27y1kor9 | 5 | https://waterforpeople.s3.amazonaws.com/images/77e7ca5b-118c-43ef-a884-14ba98c4ac51.jpg | 2016 | Normal | No |  |  |  | No | the Valve towards the water point is closed and no water reaches the water point, it has been closed because the water point is near the sources around and people don't buy water they prefer to take water from springs | Poor |  | 8d32587c16bb14b2f4f05dc39a6db08c
3gwk-awdq-j8an | 1 |  | J7 Rw24 | 1219520899 | 16-03-2017 07:34:17 CET | Kabalisa Manzi Christella | 00:07:05 | 2017 | Rwanda | Rulindo | Burega | Karengeli | Kiziba |  |  | Rwamugaza | 14106 |  | 400 | 400 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government | no problem | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3.5 | Yes | 2 |  |  | 2003 | Normal | 3.5 | Yes | 1 |  | 2003 | Normal | 8000 | Yes | 20 | -1.7416188180333267 | 29.988511802248155 | 1861.3 | 280b531p |  | 2003 | Normal | Yes | 16 |  |  | 2003 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7251508052939244 | 30.044363508198177 | 1788.9 | 27935lqz | 1 | https://waterforpeople.s3.amazonaws.com/images/6d7c848e-1d01-44b9-aca7-39700022170b.jpg | 2003 | Poor | No |  |  |  | No | Broken parts | Poor | System needs rehabilitation | 4fe67f6d44dbc55153f68b7e5691dd8
1etg-r73q-a0u6 | 1 |  | J7 Rw23 | 1317360111 | 23-04-2017 14:44:03 CEST | Rugirangoga Augustin | 00:13:03 | 2017 | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | nyiragahera | 0 |  | 151 | 105 | 46 | Yes | Piped Network with Pump |  | 2014 | Yes | gatare gatenderi shagasha rutabo | Governement (District, WASAC) and Water For People | This Systems Functions well | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 11 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2014 | Normal | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7039253954554892 | 30.026301252006245 | 1628.7 | 269z6cbr | 2 | https://waterforpeople.s3.amazonaws.com/images/24c05d3c-9533-4f2f-b73f-f68e6f728e43.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | 1264f8c7c4598b3ad1ae54a6ddbf354
xxf3-6n0x-6vh | 1 |  | J7 Rw23 | 1204770092 | 08-03-2017 18:52:55 CET | Rugirangoga Augustin | 00:32:24 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Mutima |  |  | Rutare I | 345 |  | 169 | 140 | 29 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | mutima |  |  | 1 | Spring | -1.6301829505751766 | 29.875821766632345 | 1956.8 | 22w0vwcm |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.630274494338843 | 29.875693911321243 | 1887.6 | 22w68ssk | 2 |  | 2016 | Normal | No |  |  |  | Yes |  | Normal | Public Tap has two taps but people use one on this tap stand one is closed | 3d17174fc6798d6fb2e08657dce5949
eke5-u2tk-dmud | 1 |  | J7 Rw23 | 1203040308 | 09-03-2017 11:25:37 CET | Rugirangoga Augustin | 00:15:07 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Buramba |  |  | Gihanga | 2456 |  | 163 | 120 | 43 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | gitwa buramba | Governement (District, WASAC) and Water For People |  | 1 | Groundwater (well, etc.) | -1.6358367374763643 | 29.9135277934778 | 1996.9 | 235d9tfj |  | Yes | 15 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/19208388-4297-4c38-a246-b95d8a16811c.jpg | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 15 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6359367366282058 | 29.913209249247846 | 1989.3 | 235j85h8 | 1 | https://waterforpeople.s3.amazonaws.com/images/31a86f4b-0f55-4659-9e5f-87444f0d7176.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | 8b3c17fae1ae9a45a026a5a3631e9ac
gf3j-t24r-0mkg | 1 |  | J7 Rw19 | 1242890355 | 23-03-2017 07:29:27 CET | Kayinamura Innocent | 00:14:18 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Kigarama |  |  | Mutagata motorised network | 26296 |  | 169 | 47 | 122 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.801522287450358 | 30.042875565044753 | 1708.3 | 2are10ng |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7873771391601223 | 30.048943302048592 | 1876.4 | 2a3zknpl | 64 | https://waterforpeople.s3.amazonaws.com/images/04d9d3fc-239a-4cf0-81b9-bccd79cdee35.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 8190421dfe0dbb6bd3b456dabd42fc2
6js9-btcw-x4w1 | 1 |  | J7 Rw23 | 1197960193 | 07-03-2017 11:01:57 CET | Rugirangoga Augustin | 00:35:12 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 1789 |  | 192 | 100 | 92 | Yes | Piped Network -- Gravity Only |  | 2012 | Yes | karambi gitovu | Padiri | This system was built by the Catholic church and rehabiliteted by Water For People | 3 | Spring | -1.6106435741386236 | 29.881109348905262 | 1842.1 | 21zpiwcb |  | No | 60 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 50 | Yes | 1 |  | 2012 | Normal | 6450 | Yes | 1 | -1.6111524033357627 | 29.883905051379898 | 1828.5 | 220jw07r |  | 2 | Normal | Yes | 3 | Distribution Chamber |  | 2017 | Normal | Yes | 2 |  | 2012 | Normal | 6800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6110345641155963 | 29.883777128988903 | 1821 | 220cqsyd | 1 |  | 2012 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | d62b40fed2da905952fa15bfafc88716
2x8p-qftk-9s6h | 1 |  | J7 Rw23 | 1320200105 | 23-04-2017 14:42:39 CEST | Rugirangoga Augustin | 00:41:04 | 2017 | Rwanda | Rulindo | Buyoga | Gahororo | Gitabura |  |  | kiruruma | 8295 |  | 129 | 96 | 33 | Yes | Piped Network with Pump |  | 2014 | Yes | gatenderi gatare gitabura | Governement (District, WASAC) and Water For People | This Water Point works well | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 4 |  | 2014 | Normal | 9000 | Yes | 4 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 20147 | Normal | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.9429785421740646 | 30.035387755458895 | 1375.8 | 2h9blgg1 | 1 | https://waterforpeople.s3.amazonaws.com/images/5d4d24ee-6aa5-4483-81b8-bfd2148649ed.jpg | 9633 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | 9cd87246b1161b6ae2cde2fdd9f23b4
vp64-3kmm-h0c9 | 1 |  | J7 Rw10 | 1302660085 | 14-04-2017 22:18:55 CEST | Tuyisenge Vianney | 00:10:47 | 2017 | Rwanda | Rulindo | Bushoki | Mukoto | Gatare |  |  | Nkombe gravity system catchment area |  |  | 129 | 129 | 0 | Yes | Piped Network -- Gravity Only |  | 2002 | Yes | Gitwa,Gatare and Budaha | COFORWA | This is a representative of 4sources making Nkome gravity system catchment | 4 | Spring¦Lake/Reservoir | -1.726263209282846 | 29.90351686333194 | 2121.4 | 27ax8ot7 | https://waterforpeople.s3.amazonaws.com/images/e7573cec-b659-49e6-baef-85aca57c6e40.jpg | Yes | 18 | Yes |  | https://waterforpeople.s3.amazonaws.com/images/2503a999-c255-416b-b0ce-eaec78a92585.jpg | "Springbox" --Intake Structure at a Spring | 2002 | Normal | 18 | Yes | 3 | https://waterforpeople.s3.amazonaws.com/images/3bce2b7a-1ec8-45e6-98fc-d162af2de1bf.jpg | 2002 | Normal | 100 | Yes | 1 | -1.7260141905430018 | 29.9039721775314 | 2115.6 | 27aicuov | https://waterforpeople.s3.amazonaws.com/images/c08cfa70-4686-4dbc-af85-2811a7d2ebda.jpg | 2002 | Normal | No | [5 empty] | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/36e658c4-feef-4dbe-898e-e2dfef85537f.jpg | 2002 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7259545840285198 | 29.90409683391642 | 2069.9 | 27aes928 | 1 | https://waterforpeople.s3.amazonaws.com/images/29a1bb3d-835a-4b8d-bc11-fc27862d07cb.jpg | 2002 | Normal | No |  |  |  | Yes |  | Normal | This is a representative of 4sources making Nkome gravity system catchment | 14c9dc31eaeba4c48a9c7a15c33eb58
48ed-20u8-24q9 | 1 |  | J7 Rw23 | 1218330112 | 15-03-2017 06:10:52 CET | Rugirangoga Augustin | 00:24:47 | 2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatiba |  |  | Gihanga II |  |  | 151 | 151 | 0 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | gatiba gatwa | Governement (District, WASAC) and Water For People | Gihanga and Gihanga II have the common source and the common intake | 1 | Groundwater (well, etc.) | -1.6358367374763643 | 29.917613599705728 | 1996.9 | 235d9tgo |  | Yes | 15 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 15 | Yes | 1 |  | 2016 | Normal | 7000 | Yes | 3 | -1.6358367374763643 | 29.9113527793477 |  | 235d9tex |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6460127050522646 | 29.926842708083004 | 1777.9 | 23m7d3d0 | 2 | https://waterforpeople.s3.amazonaws.com/images/01bc2c94-9a79-4496-aee5-8d35d528b93a.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | gihanga and gihanga 2 they have the common source and the common intake tank | 30ad1674b1b2d77ac8e698df88e62dc
9vhe-8949-433k | 1 |  | J7 Rw10 | 1216750591 | 13-03-2017 21:44:00 CET | Tuyisenge Vianney | 00:06:35 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Water point at GS Ngarama/Rutumvo gravity |  |  | 172 | 172 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | Water point has 2 stands at GS Ngarama | 1 | Spring | -1.677891751247546 | 29.90118126071259 | 1802.6 | 252xezpf |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.699286001679674 | 29.909363587167046 | 1746.9 | 262ax6qd | 2 | https://waterforpeople.s3.amazonaws.com/images/f0339029-aa3a-4750-99ee-2967395328e8.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | The water point at the school operates very well | d6267646c0e7fadf7916c25153b8c0ce
pf9p-d1rs-dxgx | 1 |  | J7 Rw10 | 1218190181 | 13-03-2017 21:22:46 CET | Tuyisenge Vianney | 00:05:49 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Cyili |  |  | Cyili2 water point/Rutomvu gravity | 3015 |  | 169 | 169 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | This water point at Cyili was closed | 1 | Spring | -1.677891751247546 | 29.90118126071259 | 1802.6 | 252xezpf |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | Yes | 1 | -1.6825138179236236 | 29.901875141339215 | 1791.1 | 25akh96y | https://waterforpeople.s3.amazonaws.com/images/c0049724-6f8f-4de1-91e9-265dd07edb7d.jpg | 2013 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6823978339581336 | 29.90176499472782 | 1750.8 | 25adc1xl | 1 | https://waterforpeople.s3.amazonaws.com/images/076d6c3d-0965-4cd9-a5c9-1fd329b8e173.jpg | 2013 | Does Not Function | No |  |  |  | Yes |  | Does Not Function | The water point was closed | aee5f1fa4548f225a1d7994afdcbeba4
2772-kuk4-qq9y | 1 |  | J7 Rw24 | 1222090649 | 16-03-2017 06:29:08 CET | Kabalisa Manzi Christella | 00:09:06 | 2017 | Rwanda | Rulindo | Burega | Taba | Nyagisozi |  |  | Rwamugaza | 14106 |  | 505 | 505 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | no problem | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 2 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  | https://waterforpeople.s3.amazonaws.com/images/c54c7212-78d0-4a71-ab2e-6f8f7de754d5.jpg | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7319276300617568 | 30.015296934895872 | 2071.9 | 27ka822g | 1 | https://waterforpeople.s3.amazonaws.com/images/bfb7af8d-3006-40cf-bf35-087d86cfdc4b.jpg | 2012 | Normal | No |  |  |  | No | Water seller was not around | Normal | no problem | 6b18161fc9da2727a18eb2772842eb
bcny-fqma-95ab | 1 |  | J7 Rw24 | 1247990163 | 28-03-2017 08:58:31 CEST | Kabalisa Manzi Christella | 00:07:45 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Gatobotobo |  |  | Rwamugaza network | 14106 |  | 103 | 103 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7633039627353264 | 30.058411073145404 | 1581.3 | 2906iap4 | 1 | https://waterforpeople.s3.amazonaws.com/images/2110c12d-40bd-4e45-a6ba-9281c8fbad37.jpg | 2003 | Normal | No |  |  |  | No | Road construction destroyed some pipes | Poor |  | 26490559491144ea836d2a18c18ac49
3h2s-2hw2-vgfe | 1 |  | J7 Rw24 | 1251700113 | 28-03-2017 08:45:12 CEST | Kabalisa Manzi Christella | 00:05:51 | 2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Rugogwe |  |  | Rwamugaza network | 14106 |  | 192 | 192 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234245 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7975468819355958 | 30.099695771320274 | 1664.7 | 2akt2ibo | 1 | https://waterforpeople.s3.amazonaws.com/images/fab53e03-3fe3-48fe-b2af-54c78a23c822.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | be146de54a97c98d53f3ff283f886e9
8f3b-bww7-v6f3 | 1 |  | J7 Rw10 | 1215880813 | 15-03-2017 16:52:08 CET | Tuyisenge Vianney | 00:07:44 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Kabunigu |  |  | Gako-Kabunigo water point/Tare-Rusiga pumping | 9577 |  | 219 | 219 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This Gako water point near Gako Military base.It operates well and normally | 10 | Spring | -1.7379838326200818 | 29.906994158112184 | 2017.8 | 27ub0ptp |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.812299355862946 | 29.93806995284934 | 2156.1 | 2b978ud0 | 2 | https://waterforpeople.s3.amazonaws.com/images/b09798c3-97f1-4dad-99e1-27523bffa710.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water point operates very well | 7e33a7e8c88ecf873947d939de4d1658
fc50-28my-5s0k | 1 |  | J7 Rw10 | 1235970050 | 02-01-2015 23:21:15 CET | Tuyisenge Vianney | 00:07:24 | 2017 | Rwanda | Rulindo | Tumba | Gahabwa | Rushaki |  |  | Water point at Marembo center/Nyirambuga pumping | 30604 |  | 152 | 152 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This water tap at Marembo center of Tumba operates well with two taps stands | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.709679459384019 | 29.96796227605311 | 2060.9 | 26jhikpr | https://waterforpeople.s3.amazonaws.com/images/2b1ab932-994a-4767-b046-f1db688bced3.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7097108692401204 | 29.968824946649793 | 2041.3 | 26jjwb54 | 2 | https://waterforpeople.s3.amazonaws.com/images/ef27d603-3b18-4825-b036-768ac4b0476c.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap at Marembo center of Tumba operates well with two taps stands | 8a99a91d815be3361a12e58fb274a1
sduc-ba3a-bqcb | 1 |  | J7 Rw10 | 1236020068 | 02-01-2015 12:48:41 CET | Tuyisenge Vianney | 00:06:20 | 2017 | Rwanda | Rulindo | Buyoga | Karama | Cyasenga |  |  | Water point at Cyasenga/Nyirambuga pumping | 30604 |  | 165 | 165 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point at Cyasenga.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water. | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.713045916393161 | 29.98500402832229 | 2097.6 | 26p25npm | https://waterforpeople.s3.amazonaws.com/images/19cb9c3f-7360-426b-9981-cc52a7060abc.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7144983553281643 | 29.9903461634498 | 2032.7 | 26rghigv | 2 | https://waterforpeople.s3.amazonaws.com/images/ec8dde48-09f0-4ba3-8d33-43b1a3b1e9c0.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point at Cyasenga.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water. | b9ca537b5e287d48fbd627d9394f4b
qsdp-j8m4-ucq8 | 1 |  | J7 Rw15 | 1238730182 | 21-03-2017 17:08:53 CET | Mukakarangwa Assoumpta | 00:08:25 | 2017 | Rwanda | Rulindo | Kinihira | Rebero | Kirwa |  |  | Miyove-Kinihira | 10452 |  | 187 | 80 | 107 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6794334664926354 | 29.987908470968677 | 1933 | 255h3rjb | 2 | https://waterforpeople.s3.amazonaws.com/images/2154c623-57d9-4fe5-9409-25ad2186fed3.jpg | 2015 | Normal | No |  |  |  | Yes |  | Poor |  | f0058a3de68b71fde5a51f43e9b4f2
kx4n-6m64-puvr | 1 |  | J7 Rw8 | 1241620104 | 22-03-2017 20:16:33 CET | Amani Desire | 00:13:22 | 2017 | Rwanda | Rulindo | Murambi | Mvuzo | Rurama |  |  | Mutagata Motorised Network | 26296 |  | 155 | 52 | 103 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7962067904738814 | 30.014905757171416 | 1978.7 | 2ailaelx | 64 | https://waterforpeople.s3.amazonaws.com/images/3d9258d1-7e39-4841-aedf-2063cd2a1a18.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | 33b0ff49a728ec2a99547805fa05b6
mh6a-4jdj-dxby | 1 |  | J7 Rw10 | 1237650156 | 03-01-2015 00:23:34 CET | Tuyisenge Vianney | 00:08:13 | 2017 | Rwanda | Rulindo | Tumba | Taba | Nyirataba |  |  | Water point at Nyirataba/Nyirambuga pumping | 30604 |  | 169 | 169 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point at Nyirataba doesnt have any problem.However the storage tank serving Mwili and Nyirataba its structure has started cracking and its valve chamber cover nolonger in place | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.7315018256178305 | 29.966339176682236 | 2137 | 27jl7ua7 | https://waterforpeople.s3.amazonaws.com/images/9dccf5d9-8bae-43e2-81aa-3ccb97514a53.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7316746860487238 | 29.96645328559915 | 2127.4 | 27jvc7kg | 2 | https://waterforpeople.s3.amazonaws.com/images/337c75fa-f52d-4e3a-a478-a9cc2157bb62.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point at Nyirataba doesnt have any problem.However the storage tank serving Mwili and Nyirataba its structure has started cracking and its valve chamber cover nolonger in place | 77aad4fb8109518af4d58ec6af23bd7
k4fq-ykav-wqky | 1 |  | J7 Rw24 | 1248610157 | 28-03-2017 10:46:06 CEST | Kabalisa Manzi Christella | 00:09:01 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Rwamugaza network | 14106 |  | 193 | 193 | 0 | Yes | Piped Network with Pump |  | 2003 | Yes | Nyarurama | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695880900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7589684669004633 | 30.070823301599418 | 1795.1 | 28t04690 | 1 | https://waterforpeople.s3.amazonaws.com/images/9a3d482b-b721-4b1e-9cb7-c0961ddf93f3.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | 83316de152244539e5a21d1567875c4c
mdf8-r4xn-jgun | 1 |  | J7 Rw26 | 1215510161 | 11-03-2017 10:18:28 CET | Byukusenge Elie | 00:10:56 | 2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 20456 |  | 45 | 30 | 15 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank | This network serves four sectors Cyungo,Rukozo, Base,Base and Kinihira, It has some problems in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible because it serves many populations and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6364251639944525 | 29.938175723475066 | 1868.2 | 236ceeb9 | 29 | https://waterforpeople.s3.amazonaws.com/images/f769ed6b-85f9-4804-b8ec-2edef57fde8c.jpg | 2011 | Poor | Yes | 10 | 22 | Bad tee connections and the types of pipeline needs rehabilitation | No | no water available in the distribution reservoir im Gahwazi Village | Poor | water not available in this transmission line of Gahwazi | 40ff6b2eb4184f842a7a2b2a2536c
ctj7-4wv8-egp7 | 1 |  | J7 Rw23 | 1203700084 | 07-03-2017 12:27:42 CET | Rugirangoga Augustin | 00:39:56 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 1789 |  | 192 | 100 | 92 | Yes | Piped Network -- Gravity Only |  | 2012 | Yes | Gitovu | Padiri | Water Tanks (reservoirs) built in 2017, it doesn’t have water yet | 3 | Spring | 1.613001918870488 | 29.87535077266787 | 1921.6 | 223m1729 |  | Yes | 20 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 20 | Yes | 2 |  | 2012 | Normal | 6450 | Yes | 3 | -1.6100731207000338 | 29.88548582583426 | 1812.8 | 21yrl6w6 |  | 2012 | Normal | Yes | 2 | Distribution Chamber |  | 2012 | Normal | Yes | 2 |  | 2017 | Poor | 1500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6096929412154701 | 29.8858304054849 | 1795.8 | 21y4ypwq | 2 |  | 2017 | Does Not Function | Yes | 365 | 0 | not yet start working.it is new | No | Water point under construction | Does Not Function | System under construction | c01365f4da5f3b54c37f107f643436b
uc87-y6yf-2d5u | 1 |  | J7 Rw19 | 1236870952 | 23-03-2017 08:03:05 CET | Kayinamura Innocent | 00:09:58 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Amahoro |  |  | Mutagata motorised network | 26296 |  | 120 | 120 | 0 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044153 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7772960034332368 | 30.047155121220314 | 1867 | 29nbfpx3 | 64 | https://waterforpeople.s3.amazonaws.com/images/b0d98ecd-7bb2-4e01-b6f0-ba57f3a9fd2e.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 6c61f7b0ae8d79aaeea7d0f339fac8ef
ue2s-6av4-fvmc | 1 |  | J7 Rw23 | 1249440061 | 25-03-2017 20:47:52 CET | Rugirangoga Augustin | 00:26:42 | 2017 | Rwanda | Rulindo | Buyoga | Butare | Gasave |  |  | KIDUHA | 0 |  | 114 | 100 | 14 | Yes | Piped Network -- Gravity Only |  | 2007 | Yes | gasave giko kankanga | Italians(LAKE ANGELS) | Rehabilitation irakenewe kuberako ibigega by'umuyoboro birava. | 1 | Groundwater (well, etc.) | -1.692136727874054 | 30.02146392212493 | 1866.9 | 25qh8a2e |  | No | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Poor | 20 | Yes | 1 |  | 2007 | Poor | 2200 | Yes | 3 | -1.6932117321635163 | 30.026191374639453 | 1765.8 | 25s9j3fp | https://waterforpeople.s3.amazonaws.com/images/178a6bf6-9fd6-4782-874d-89928b5b2390.jpg | 2007 | Normal | No | [5 empty] | Yes | 1 |  | 2007 | Poor | 2200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.699901220308483 | 30.014659085284347 | 1862.4 | 263bu31u | 1 | https://waterforpeople.s3.amazonaws.com/images/2d0cdcbb-ba7b-41e7-a6c6-acf19d8274ec.jpg | 2014 | Poor | No |  |  |  | Yes |  | Poor | System is working but needs rehabilitation, Reservoirs are leaking, Water doesnt reach enough to satisfy the need at the health center. | c8aa166e7c84439d9d452bf2db783d
shnq-pk09-16fw | 1 |  | J7 Rw15 | 1239840699 | 23-03-2017 06:39:19 CET | Mukakarangwa Assoumpta | 00:06:02 | 2017 | Rwanda | Rulindo | Kinihira | Marembo | Kigali |  |  | Nyamagana-Kinihira |  |  | 189 | 60 | 129 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6656741432835351 | 29.933065445552003 | 1871.1 | 24ipvapu | 2 | https://waterforpeople.s3.amazonaws.com/images/daeeced1-41ec-4cea-87f6-f7aee44f324c.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | 1b9b933d30a881971b8de87933b6a7c
50tv-ax1n-k08r | 1 |  | J7 Rw15 | 1244750101 | 23-03-2017 06:47:46 CET | Mukakarangwa Assoumpta | 00:07:58 | 2017 | Rwanda | Rulindo | Kinihira | Marembo | Kigali |  |  | Nyamagana- Kinihira |  |  | 189 | 70 | 119 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦Ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6651244558565585 | 29.932167449720993 | 1894.1 | 24ht4gft | 2 | https://waterforpeople.s3.amazonaws.com/images/7fbd5b5f-a1bb-412a-9d39-1581bfcaa15e.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | 9ef82b3b92a862f6772847af38562f97
uy77-mxra-k4bn | 1 |  | J7 Rw7 | 1240630602 | 24-03-2017 11:06:26 CET | Safari Bosco | 00:12:31 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo |  |  | marenge | 5544 |  | 203 | 203 | 0 | Yes | Piped Network with Pump |  | 1998 | No |  |  |  | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 1 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 1 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.82688285907943 | 30.06110681219943 | 1719.5 | 2bxbwawz | 1 | https://waterforpeople.s3.amazonaws.com/images/ae12a376-64d7-4b66-b369-ec22e8a72292.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 2e176b97b7c965e9fd19daf209bae33
dhv2-bq5w-066u | 1 |  | J7 Rw15 | 1232080683 | 21-03-2017 17:37:11 CET | Mukakarangwa Assoumpta | 00:14:32 | 2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Bwishya |  |  | Miyove-Kinihira | 10452 |  | 181 | 60 | 121 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2027.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.663381399335895 | 29.982826753001927 | 1949.4 | 24exj1kk | 1 | https://waterforpeople.s3.amazonaws.com/images/98cb6159-9967-4f96-a3eb-af906204a272.jpg | 1989 | Does Not Function | No |  |  |  | Yes |  | Poor | water point does not function they access water to Gatembe and Kirwa villages | 9d5ac673d59ecd1c73d8a384aa13848
ccqq-yg2b-9kh2 | 1 |  | J7 Rw8 | 1196110880 | 07-03-2017 14:13:53 CET | Amani Desire | 00:46:00 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Ruhanya |  |  | Mutungo | 510 |  | 102 | 50 | 52 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | kibaya ,Ruhanya |  | the network is not in good condition it is old ,water points are damaged and valve at reservoirs are damaged | 1 | Spring | -1.769488583676096 | 29.9450760030861 | 1922.1 | 29aeg5oa | https://waterforpeople.s3.amazonaws.com/images/5a6b4842-93fe-4254-ab3b-2ad366b00418.jpg | No | 24 | No | [5 empty] | 24 | Yes | 1 |  | 2004 | Normal | 500 | Yes | 2 | -1.7685825306926122 | 29.944785701134276 | 1910.6 | 298wv587 | https://waterforpeople.s3.amazonaws.com/images/8dce1737-2d21-425a-b695-edd771070b68.jpg | 2004 | Poor | No | [5 empty] | Yes | 1 |  | 2004 | Poor | 2000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7558062929993428 | 29.94311833414845 | 1855.3 | 28nrz63r | 3 | https://waterforpeople.s3.amazonaws.com/images/1ce1e4c0-3706-4477-b378-b7b8e6a809d5.jpg | 2004 | Poor | No |  |  |  | Yes |  | Poor | -the network is damaged ,it is not in good operational condition -The water point is damaged as it is seen on the picture -water is flowing the whole day because there is no water tap | 8795849c12faa1a5d5446acce6844e2
19nk-fbhn-rttj | 1 |  | J7 Rw26 | 1308720081 | 15-04-2017 16:33:48 CEST | Byukusenge Elie | 00:08:59 | 2017 | Rwanda | Rulindo | Cyungo | Burehe | Gitandi |  |  | Nyamagana | 20456 |  | 40 | 35 | 5 | Yes | Piped Network -- Gravity Only |  | 2011 | No |  | Government and African Development Bank |  | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 120 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 120 | Yes | 1 |  | 2011 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.92216532428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 1 |  | 2011 | Normal | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6220962695435488 | 29.941595895491297 | 1838.7 | 22in88gn | 29 | https://waterforpeople.s3.amazonaws.com/images/7e8b1c80-3681-4886-927d-a121f6f7e4b0.jpg | 2011 | Poor | Yes | 15 | 30 | problem of pipeline and bad connection | No | no water valve | Poor | This water tap needs to be rehabilitated | 9c137c2d8b6c29aeb2b926e03574875c
2nqv-uha4-5ffr | 1 |  | J7 Rw24 | 1223931237 | 16-03-2017 08:34:25 CET | Kabalisa Manzi Christella | 00:06:12 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kanyoni |  |  | 0 | 6572 |  | 640 | 640 | 0 | Yes | Piped Network with Pump |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8024532750946713 | 30.042616473975034 | 1748.3 | 2asxebwq |  | Yes | 3 | Yes | 1 |  |  | 2016 | Normal | 3 | Yes | 1 |  | 2016 | Normal | 35000 | Yes | 10 | -1.767486275024945 | 30.035974538149265 | 1988.5 | 2973dhdz |  | 2016 | Normal | Yes | 8 |  |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 35000 | Yes | 3 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7717478807227132 | 30.033257208765676 | 2008.2 | 29e5052k | 1 | https://waterforpeople.s3.amazonaws.com/images/bf5f4e00-3ba0-46c7-8752-50734b4fe1b9.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 244a7e2fa7222410c0cbb6f965d36d1
k1je-q31k-c9wq | 1 |  | J7 Rw10 | 1318980075 | 21-04-2017 16:26:12 CEST | Tuyisenge Vianney | 00:05:12 | 2017 | Rwanda | Rulindo | Rusiga | Taba | Gahondo |  |  | Gahondo water point chez Safari/Bitare-Gahondo gravity | 9577 |  | 83 | 83 | 0 | Yes | Piped Network -- Gravity Only |  | 1989 | No |  | Catholic Church | Not operational | 2 | Spring | -1.8240400967512485 | 29.93064274686712 | 1670 | 2bsmt63u | https://waterforpeople.s3.amazonaws.com/images/25ddada5-f7d2-4b1d-bf71-891978bdb02e.jpg | Yes | 10 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/d8a4437c-9939-4aa3-8955-1bfa79d9263d.jpg | "Springbox" --Intake Structure at a Spring | 2017 | Normal | 10 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/4a279064-cebd-4ac4-bfaf-54b9d2488906.jpg | 2017 | Normal | 400 | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.821282595354738 | 29.92759522431068 | 1651.9 | 2bo2hj4b | 1 | https://waterforpeople.s3.amazonaws.com/images/67b1a1e1-6dfb-4643-a2dd-6bf9dddca8b8.jpg | 1989 | Does Not Function | No |  |  |  | No | not operational.sources being recaptured for making it pumping system | Does Not Function | Currently at water sources there are two conductions lines with big quantity of water.However,the previous gravity network is not operating at all for the works of recapturing being under progress.The sources are being recaptured to make it pumping system that will also be supplying the Gako(Rusiga) Military Base | 21eef144d52efc2afd90a64695faeb7
ydfh-15pd-ccf9 | 1 |  | J7 Rw19 | 1190991126 | 07-03-2017 11:45:45 CET | Kayinamura Innocent | 00:21:19 | 2017 | Rwanda | Rulindo | Mbogo | Mushali | Buraro |  |  | Matyazo network |  |  | 155 | 55 | 100 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | Buyanja, Nyakabuya, Buraro | Governement (District, WASAC) and Water For People |  | 3 | Spring | -1.7856001537024087 | 29.978428885393118 | 1894.3 | 2a126x3c |  | Yes | 17 | Yes | 4 |  | "Springbox" --Intake Structure at a Spring¦Collection chamber | 2016 | Normal | 17 | Yes | 1 |  | 2016 | Normal | 4300 | Yes | 1 | -1.77057095933776213 | 29.968679108343068 | 1834.4 | 29c7cesm |  | 2016 | Normal | Yes | 2 | Air release chamber, Washout chamber |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 1800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7706723719846356 | 29.968179693500556 | 1826.8 | 29cdaqu9 | 4 | https://waterforpeople.s3.amazonaws.com/images/0b8b6db7-8754-498e-bf33-0baca5db5f7b.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | People choose rather to fetch water from Springs which is near by | d15e6b7a8237fb204e4c3e4f5fe3b5f6
cm1n-c8md-bmes | 1 |  | J7 Rw26 | 1201100080 | 02-01-2015 05:51:32 CET | Byukusenge Elie | 00:09:46 | 2017 | Rwanda | Rulindo | Cyungo | Burehe | Sove |  |  | Nyamagana | 20456 |  | 30 | 15 | 15 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Poor | 2100 | Yes | 29 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.627481346013367 | 29.941905897269496 | 1795.2 | 22rk4viz | 29 | https://waterforpeople.s3.amazonaws.com/images/32c57678-fc1f-475f-9a06-a321007eb7dd.jpg | 2011 | Poor | Yes | 10 | 30 | The distribution reservoir does not supply water in this transmission towards G.S.Urumuli | No | The water tap was damaged and bad connection of tee junctions towards Burehe cell | Poor | This water tap doesn't used by the community ,They use the spring sources and it is located near G.G.S Urumuli | 9df1361b6ed74e4e30d96443c644bf
3kx9-thfk-ycdn | 1 |  | J7 Rw7 | 1243590420 | 24-03-2017 12:47:07 CET | Safari Bosco | 00:54:37 | 2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Kigomwa |  |  | marenge | 5544 |  | 118 | 118 | 0 | Yes | Piped Network with Pump |  | 1998 | No |  | Governement (District, WASAC) and Water For People | Water points is functioning well | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 500 | Yes | 15 | -1.8228065710007637 | 30.055376173807932 | 1827.2 | 2bqkzg21 | https://waterforpeople.s3.amazonaws.com/images/240fbb89-4622-496a-a844-0f8e4b38b127.jpg | 2016 | Normal | Yes | 0 | Sedimentation Tank |  | 2016 | Normal | Yes | 2 |  | 2016 | Normal | 500 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | Yes |  | Filtration | 2016 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8203207263751617 | 30.052657495490102 | 1884.6 | 2bmhby0e | 3 |  | 2016 | Normal | No |  |  |  | Yes |  | Normal | This water point was built in 1998 | 97ba707dca3e2bb2c78caf1ed4d110d6
cand-qxsa-tukj | 1 |  | J7 Rw15 | 1206960494 | 09-03-2017 19:44:51 CET | Mukakarangwa Assoumpta | 00:07:33 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Kigali |  |  | Gisoro- Nyundo network | 2297 |  | 220 | 110 | 110 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.840451151026817 | 29.948165560771624 | 1795.9 | 2cjrthy1 |  | Yes | 13 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 13 | Yes | 1 |  | 2013 | Normal | 30 | Yes | 6 | 1.8406374522240199 | 29.94836287627501 | 1783.7 | 2ck2jau3 |  | 2013 | Poor | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 7000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8703513484484746 | 29.94146128876709 | 1440.6 | 2dx7zknq | 1 | https://waterforpeople.s3.amazonaws.com/images/57086f90-e772-485a-a238-1770f3b10242.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 7c8af0d0f62d7a3cd47f030d71dfb82
s065-b3dj-fmb6 | 1 |  | J7 Rw24 | 1220310368 | 16-03-2017 08:41:47 CET | Kabalisa Manzi Christella | 00:05:31 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Gatagara |  |  | 0 | 6572 |  | 725 | 725 | 0 | Yes | Piped Network with Pump |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.802453270946713 | 30.042616473975034 | 1748.3 | 2asxebwq |  | Yes | 3 | Yes | 1 |  |  | 2016 | Normal | 3 | Yes | 1 |  | 2016 | Normal | 35000 | Yes | 10 | -1.767486275024945 | 30.035974538149265 | 1988.5 | 2973dhdz |  | 2016 | Normal | Yes | 6 |  |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 35000 | Yes | 3 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7697913645295664 | 30.033620249860302 | 1989.9 | 29awwm40 | 1 | https://waterforpeople.s3.amazonaws.com/images/69fe4c25-247c-4170-a08c-7a63207ef8e2.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | b0b1e19bbe9bed6dd52daf87976b97bf
kqs6-b4a1-whmk | 1 |  | J7 Rw10 | 1208830586 | 10-03-2017 11:58:22 CET | Tuyisenge Vianney | 00:06:50 | 2017 | Rwanda | Rulindo | Bushoki | Mukoto | Rusave |  |  | Rusave water point/Tare-Rusiga pumping | 567 |  | 101 | 101 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This water point operates normally | 8 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 4000 | No | [8 empty] | No | [5 empty] | Yes | 1 |  | 2015 | Normal | 8000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7112141880966345 | 29.897933421545954 | 2127.4 | 26m17bc3 | 2 | https://waterforpeople.s3.amazonaws.com/images/144e3653-d3ea-42e2-97d3-ff8b7d3102ab.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Rusave water points operates normally. | 82880248203da532a73df5a5e5d694
kpu7-20m9-qxkg | 1 |  | J7 Rw15 | 1212190058 | 12-03-2017 10:34:23 CET | Mukakarangwa Assoumpta | 00:13:32 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Mukumba |  |  | Bitete-Muvumu | 1316 |  | 92 | 0 | 92 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 3 | Spring | 1.8337482672601935 | 29.943433443706404 | 1749 | 2c8obmzu |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Poor | 1000 | Yes | 4 | 1.8368127107947887 | 29.93457412501046 | 1635 | 2cdr3pn5 |  | 2013 | Normal | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Poor | Yes | 1 |  | 2013 | Normal | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8369288312896663 | 29.932717484807938 | 1537 | 2cdxnha7 | 1 | https://waterforpeople.s3.amazonaws.com/images/b7c3ab92-6260-4578-92f5-3a89f128a583.jpg | 2013 | Does Not Function | No |  |  |  | Yes |  | Poor | People choose rather to fetch water from Springs which is near by | f6a6d56e86d83bf1971565fe71df61ed
3ann-41vu-qe7f | 1 |  | J7 Rw8 | 1199670548 | 07-03-2017 09:42:53 CET | Amani Desire | 00:40:40 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 911 |  | 118 | 25 | 93 | Yes | Piped Network -- Gravity Only |  | 1997 | No |  | Governement (District, WASAC) and Water For People | Network have been totally rehabilitatated in 2016 | 2 | Spring | -1.740882760889992 | 29.933869978471744 | 1846.2 | 27z3ofgq |  | Yes | 30 | Yes | 2 |  | start chamber and collection chamber | 2016 | Normal | 30 | Yes | 1 |  | 2016 | Normal | 700 | Yes | 1 | -1.7398552316859899 | 29.93657178593082 | 1752.3 | 27xecs6d |  | 2016 | Normal | Yes | 2 | washout and Valve chamber |  | 2016 | Normal | Yes | 2 |  | 2016 | Normal | 800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7388288956156897 | 29.939373576308554 | 1765.4 | 27vp14w1 | 5 | https://waterforpeople.s3.amazonaws.com/images/4578caf3-38d6-476a-bd46-0044cd16ef77.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | All other water structures and pipeline have been totally rehabilitated in 2016 except one water point at the source | 54a9c28e2bc6d6879a95433dd62189d
vned-2d2f-jqa4 | 1 |  | J7 Rw7 | 1239890533 | 24-03-2017 14:09:05 CET | Safari Bosco | 00:22:46 | 2017 | Rwanda | Rulindo | Murambi | Mvuzo | Kabuga | [5 empty] | 199 | 199 | 0 | Yes | Piped Network -- Gravity Only |  | 2001 | Yes | kabunga,gatare,taba,karwa hamwe na kigarama | Governement (District, WASAC) and Water For People | System is functional but in Dry season water not enough has schools connected to the system, has three sources, filling 20 liters in 14 seconds has 17 water points including one at the source, has 12,000 meters | 3 | Spring | -1.8081127252820783 | 30.019302406005654 | 1889.4 | 2b2ado4h |  | Yes | 14 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 14 | Yes | 1 |  | 2001 | Normal | 12000 | Yes | 7 | -1.8083188633668612 | 30.018599981640595 | 1825.6 | 2b2mac7t |  | 2001 | Normal | No | [5 empty] | Yes | 1 |  | 2001 | Normal | 12000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8083673788125414 | 30.018576770492718 | 1798.1 | 2b2p9i8p | 7 |  | 2001 | Normal | No |  |  |  | Yes |  | Normal |  | f855bc7f2a0a2b86e56bd1a8da52cf3
t2n8-su6h-2yt7 | 1 |  | J7 Rw24 | 1255380101 | 28-03-2017 08:54:33 CEST | Kabalisa Manzi Christella | 00:06:28 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Gatobotobo |  |  | Rwamugaza network | 14106 |  | 103 | 103 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7649613139419935 | 30.064983393871657 | 1611.1 | 292xc961 | 1 | https://waterforpeople.s3.amazonaws.com/images/5f83314c-6ada-420e-b978-6552fb9b66a3.jpg | 2003 | Normal | No |  |  |  | No | Road construction destroyed some pipes | Poor |  | 73c8974490a1cd11c3b7e94198e61cd7
9m93-qcmg-tw1f | 1 |  | J7 Rw19 | 1242010100 | 23-03-2017 07:35:26 CET | Kayinamura Innocent | 00:13:32 | 2017 | Rwanda | Rulindo | Masoro | Kabuga | Kanunga |  |  | Mutagata motorised network | 26296 |  | 143 | 68 | 75 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.25 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7904123516937525 | 30.051864103339597 | 1822.3 | 2a90kfmu | 64 | https://waterforpeople.s3.amazonaws.com/images/f1916b80-82c6-43c2-a270-9ce5f1579f37.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 7d8ec8aa2de255886adf5b3361faed2
u9tr-ks6x-10x1 | 1 |  | J7 Rw15 | 1215360071 | 12-03-2017 10:54:02 CET | Mukakarangwa Assoumpta | 00:07:32 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Karama |  |  | Bitete-Muvumu | 1316 |  | 121 | 45 | 76 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 3 | Spring | 1.8337482672601935 | 29.943433443706404 | 1749 | 2c8obmzu |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Poor | 1000 | Yes | 4 | 1.8368127107947887 | 29.93457412501046 | 1635 | 2cdr3pn5 |  | 2013 | Normal | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Poor | Yes | 1 |  | 2013 | Normal | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8500548699235562 | 29.927443058131963 | 1450.8 | 2czndmiy | 1 | https://waterforpeople.s3.amazonaws.com/images/d4323717-876f-48cb-9199-4fe5a4bb0316.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | df938b8a2b59ef9bd52d7682cd55cf27
bn63-38hy-r1jx | 1 |  | J7 Rw8 | 1209110887 | 10-03-2017 10:24:13 CET | Amani Desire | 00:34:19 | 2017 | Rwanda | Rulindo | Ngoma | Kabuga | Nyabuko |  |  | Kabarore-Ngoma-Nyabuko network | 8284 |  | 122 | 35 | 87 | Yes | Piped Network with Pump |  | 2014 | Yes | Nyabuko ,kagwa,kiruli,busizi,ngaru,kirungu,kiboha,kigina | Governement (District, WASAC) and Water For People | The network has 17 water points | 4 | Spring | -1.8123357076877171 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦collection chamber | 2014 | Poor | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 14 | -1.808716485895084 | 29.973362007273437 | 2001 | 2b3a3o2d |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.815732653875976 | 29.974778657011672 | 1951.4 | 2bew1yqr | 17 | https://waterforpeople.s3.amazonaws.com/images/34c67376-e3f7-48f6-88e7-1a59f4431656.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | - the network has 17 water points -water points are in good operational conditions except the water at the source that is damaged -4 water points don't have water today -the pipes are in good condition -the pump is not working properly as it was expected during Design due to the lack of sufficient energy -the transformer at the pumping station doesnt offer the required energy to the pump -the anti hammers of the pump are not functioning because of bad installation of pumping house -the system has two pumps with four units with two units pumping in one direction towards Nyabuko and other two in an other direction towards ngoma sector office - The suction tank is bad physical condition | 73d99649c3bfc68f714e20f3c265baf0
8ype-6bs4-gmqf | 1 |  | J7 Rw19 | 1204660972 | 07-03-2017 11:04:05 CET | Kayinamura Innocent | 00:59:42 | 2017 | Rwanda | Rulindo | Mbogo | Mushali | Gitaba |  |  | Matyazo network |  |  | 118 | 100 | 18 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | Buyanja, nyakabuye,Buraro | Governement (District, WASAC) and Water For People |  | 3 | Spring | -1.7856001537024087 | 29.978428885393118 | 1894.3 | 2a126x3c | https://waterforpeople.s3.amazonaws.com/images/9acb718a-67a4-40be-8156-22b8fe1ce672.jpg | Yes | 17 | Yes | 4 | https://waterforpeople.s3.amazonaws.com/images/560811fa-bb0b-411f-8335-df939ad7bc99.jpg | "Springbox" --Intake Structure at a Spring¦Collection chamber | 2016 | Normal | 17 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/c9151e0b-819f-4b6d-83cc-27ec714f1546.jpg | 2016 | Normal | 4300 | Yes | 1 | -1.7705709593776213 | 29.968679108343068 | 1834.4 | 29c7cesm | https://waterforpeople.s3.amazonaws.com/images/d07b4c41-b1f4-4f3e-bdaa-36106c89b539.jpg | 2016 | Normal | Yes | 2 | Air release chamber, Washout chamber | https://waterforpeople.s3.amazonaws.com/images/69a6894a-fa22-4845-949a-e4f32a60e4c8.jpg | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 1800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7857343842315625 | 29.978352439147873 | 1918.4 | 2a19xjyf | 4 | https://waterforpeople.s3.amazonaws.com/images/cf202aed-60ab-4472-b716-3cc1d644d1a2.jpg | 2016 | Poor | No |  |  |  | Yes |  | Normal |  | 5b4a44471781192893398529c3e23dd
e0k9-6f4p-qnhs | 1 |  | J7 Rw10 | 1303450109 | 14-04-2017 21:14:54 CEST | Tuyisenge Vianney | 00:09:06 | 2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Gitaba |  |  | Rutembe catchment area | 673 |  | 118 | 118 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | Gitaba and Muko | Rulindo district | Rutembe spring catchment has been benefited to capture water to supply the Rulindo districg headquarters jointly with Mpango spring catchment area | 1 | Spring | -1.7022323649660753 | 29.916292315373823 | 1834.3 | 2676k28q | https://waterforpeople.s3.amazonaws.com/images/1be72b67-8c0a-4d60-bdeb-d9faf9a0b105.jpg | Yes | 20 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/ac860f2a-b0d3-41ab-943b-70702191c154.jpg | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 20 | Yes | 1 |  | 2015 | Normal | 100 | Yes | 1 | -1.7022525180255077 | 29.916181811817076 | 1810.4 | 2677qxg9 | https://waterforpeople.s3.amazonaws.com/images/312c3271-3533-4319-8c04-b311e6c73cb9.jpg | 2015 | Normal | Yes | 1 | Overflow where people are currently fetching due to water point that has no sufficient water | https://waterforpeople.s3.amazonaws.com/images/f2de9e9c-e79b-41b4-bf7f-200483392f27.jpg | 2015 | Normal | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/0df5f10d-5fec-4d49-86ae-7769818e9e2b.jpg | 2015 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7022416503451199 | 29.91622363057006 | 2045.2 | 26775hui | 1 | https://waterforpeople.s3.amazonaws.com/images/f17b8179-70bf-4b7b-b6c7-d0854be7e153.jpg | 2015 | Poor | No |  |  |  | Yes |  | Normal | Water deviated and people are fetching from overflow. Rutembe spring catchment has been benefited to capture water to supply the Rulindo districg headquarters jointly with Mpango spring catchment area | 4dc2f1cfb8ee9d6da8c74d46e8285643
vm48-pe5p-872u | 1 |  | J7 Rw15 | 1207570667 | 09-03-2017 04:40:01 CET | Mukakarangwa Assoumpta | 00:07:08 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Rutonde |  |  | kirikumuryango network |  |  | 241 | 150 | 91 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8960671030551557 | 29.969811851357687 | 1412.5 | 2f3qp16a | 1 | https://waterforpeople.s3.amazonaws.com/images/6db058ac-022f-4e01-a35e-2af8675fe4e1.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 2516d6f2aff86aa44e148fcb353a433
utjs-tv7h-q9ja | 1 |  | J7 Rw23 | 1243880143 | 23-03-2017 06:25:11 CET | Rugirangoga Augustin | 00:23:06 | 2017 | Rwanda | Rulindo | Buyoga | Gitumba | Munini |  |  | Kiruruma | 8295 |  | 158 | 153 | 5 | Yes | Piped Network with Pump |  | 2014 | Yes | rutabo gitabo nyarubuye remera rusongati rugarama cyasuli munini | Governement (District, WASAC) and Water For People | this network is working well | 1 | Groundwater (well, etc.) | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 15 | -1.6111677762752643 | 30.047381335897573 | 1775.8 | 220khh2x |  | 2014 | Normal | Yes | 5 | Pressure Break Tank |  | 2014 | Normal | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.683480271329771 | 30.049155094563368 | 2033.3 | 25c68c0b | 1 | https://waterforpeople.s3.amazonaws.com/images/c7960762-4aff-4e95-b869-a83e09f5dd6f.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | the pumping network has no problem | 79866be9250fc3ecebee35c48629a5
348h-rsug-14uy | 1 |  | J7 Rw8 | 1193310633 | 07-03-2017 20:42:08 CET | Amani Desire | 00:38:14 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kibaya |  |  | Mutungo | 510 |  | 133 | 60 | 73 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | kibaya,Ruhanya |  | The network is not in good cindition , water points are damaged and some of them are not operational and the valves at reservoirs are damaged | 1 | Spring | -1.769488583676096 | 29.9450760030861 | 1922.1 | 29aeg5oa |  | No | 24 | No | [5 empty] | 24 | Yes | 1 |  | 2004 | Poor | 2000 | Yes | 2 | -1.7685825306926122 | 29.944785701134276 | 1910.6 | 298wv587 |  | 2004 | Poor | No | [5 empty] | Yes | 1 |  | 2004 | Poor | 2000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7414359494875786 | 29.942370905107868 | 1766 | 2800f9sv | 1 | https://waterforpeople.s3.amazonaws.com/images/14e44697-29a1-40c3-9273-c7123c309771.jpg | 2004 | Does Not Function | Yes | 5 | 15 | sometimes there is not enough water and water from the Reservoir doesnt reach this water point due to that the pipeline is damaged | No | due to the problems of the pipeline which is damaged | Does Not Function |  | 1bb6b387dcd6fdfd3830c612b5106184
8k5j-8pns-xfd9 | 1 |  | J7 Rw24 | 1224840156 | 15-03-2017 14:20:10 CET | Kabalisa Manzi Christella | 00:17:45 | 2017 | Rwanda | Rulindo | Cyinzuzi | Migendezo | Gitabage |  |  | 0 | 14106 |  | 735 | 735 | 0 | Yes | Piped Network with Pump |  | 2009 | No |  | umushinga witwa Ema | No Problem with the Water Point | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2009 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 16 | -1.7543004341479447 | 29.99197561543003 | 2178 | 28lao5qn |  | 2009 | Normal | Yes | 23 | vantouse | https://waterforpeople.s3.amazonaws.com/images/d4ab9b54-4c06-4181-b42f-166871ccf16e.jpg | 2009 | Normal | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.765119964043886 | 29.99589560140937 | 2152 | 29369qpi | 1 | https://waterforpeople.s3.amazonaws.com/images/345f7065-a5e1-43b3-bf06-b91be10e292d.jpg | 2009 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | 60973535cc9b9ec24a297d872279c5d3
6ugs-u7xp-ebfn | 1 |  | J7 Rw10 | 1212450108 | 09-03-2017 11:57:50 CET | Tuyisenge Vianney | 00:08:27 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Budaha |  |  | Water point at Budaha nearby pumping station/Tare pumping | 9577 |  | 205 | 205 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Gvt and Water for people | Water point at Budaha | 8 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte | https://waterforpeople.s3.amazonaws.com/images/af3c58e8-b40c-4635-aa28-51e31f046110.jpg | Yes | 40 | No | [5 empty] | 40 | Yes | 1 |  | 2015 | Normal | 4000 | Yes | 1 | -1.7193854981836107 | 29.918058951124646 | 1794.3 | 26zjmgq4 |  | 2015 | Normal | No | [5 empty] | Yes | 1 |  | 2015 | Normal | 2000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7186078301980896 | 29.91851971138519 | 1778.7 | 26y96njl | 1 | https://waterforpeople.s3.amazonaws.com/images/305f3947-f28f-4617-ada8-c16dd753611f.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This Budaha water points operates normally | 5eaae8b4d623111e4b572cb3f54b8
8qsr-x9sb-e0v9 | 1 |  | J7 Rw26 | 1204810181 | 02-01-2015 05:53:47 CET | Byukusenge Elie | 00:09:07 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Kabingo |  |  | Nyamagana | 20456 |  | 70 | 60 | 10 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6481591735157544 | 29.91789362165804 | 1779.1 | 23pqruqy | 29 | https://waterforpeople.s3.amazonaws.com/images/2703fea2-6d6d-47a0-ac38-e3f97611bc0a.jpg | 2011 | Normal | No |  |  |  | Yes |  | Normal | Water are available at this water point and this transmission line towards Base was in good condition but will be affected by the new road2 construction. | c1be8889d9624c01645e0614899b3
bh16-4avn-w30f | 1 |  | J7 Rw23 | 1203080207 | 09-03-2017 07:35:30 CET | Rugirangoga Augustin | 00:56:40 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Kiruli |  |  | Migogo | 558 |  | 129 | 120 | 9 | Yes | Piped Network -- Gravity Only |  | 2009 | Yes | kiruli bukangano kabahama Rubanda | Italians(LAKE ANGELS) | System needs rehabilitation | 1 | Spring | -1.632311918504939 | 29.90125938622725 | 1810.2 | 22zjp8ec |  | No | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2009 | Normal | 20 | No | [5 empty] | Yes | 3 | -1.6350822337877793 | 29.89531663121816 | 1775.7 | 2344max5 |  | 2009 | Poor | No | [5 empty] | Yes | 2 |  | 2009 | Poor | 3000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.637767975874519 | 29.895748240187057 | 1750.2 | 238k6h1p | 1 |  | 2009 | Poor | No |  |  |  | Yes |  | Poor | System needs rehabilitation | db7ebc738e33f9a64abb94842b805a98
1eck-0qmg-nr5m | 1 |  | J7 Rw19 | 1252140256 | 28-03-2017 11:46:09 CEST | Kayinamura Innocent | 00:20:06 | 2017 | Rwanda | Rulindo | Ngoma | Mugote | Sakara |  |  | Kararama pumping network | 6572 |  | 99 | 99 | 0 | Yes | Piped Network with Pump |  | 2007 | Yes | Riryi,nyakibyeyi,marembo,ngabitsinze, musenyi,munoga,remera,nyagisozi,rwamiko,kiziba,kisigiro,gacyamo,muhondo | Government |  | 4 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | No | 6 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring¦Collection chamber | 2007 | Poor | 6 | Yes | 1 |  | 2007 | Normal | 1500 | Yes | 25 | -1.7543004341479447 | 29.99197561543003 | 2178 | 28lao5qn |  | 2007 | Normal | Yes | 20 | Distribution Chamber¦Washout and Air release chamber |  | 2007 | Normal | Yes | 4 |  | 2007 | Normal | 30000 | Yes | 2 |  | 2007 | Poor | Yes |  | 2007 | Poor | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.800204799834038 | 30.0032756790772 | 2086.5 | 2ap7fshs | 47 | https://waterforpeople.s3.amazonaws.com/images/a28211c2-9db1-409a-89f8-4c3e11a841e5.jpg | 2007 | Does Not Function | No |  |  |  | No | water do not reach this water point | Does Not Function | 1.the system has two pumps but only one is functioning 2.The source and the pumping station are under total rehabilitation 3. Water points located in Ngoma sector do not have water 4.this network serves Ngoma, cyinzuzi and Ntarabana sectors | 2285fc74121e9a9f316366116fe55a57
g6h8-dum8-c6c1 | 1 |  | J7 Rw24 | 1253520461 | 28-03-2017 08:38:13 CEST | Kabalisa Manzi Christella | 00:06:21 | 2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Karera |  |  | Rwamugaza network | 14106 |  | 182 | 182 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.792103123537687 | 30.09620140999927 | 1717.4 | 2abt6p7m | 1 | https://waterforpeople.s3.amazonaws.com/images/d47fc24e-1218-4475-b7b3-691af4a0f612.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | 355b51fb3da762a790fa12e4ed26a98
4djh-wbp3-0js4 | 1 |  | J7 Rw23 | 1242600193 | 23-03-2017 06:27:42 CET | Rugirangoga Augustin | 00:31:20 | 2017 | Rwanda | Rulindo | Buyoga | Gitumba | Nyarubuye |  |  | Kiruruma | 8295 |  | 146 | 140 | 6 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | rutabo gitaba cyasuli nyarubuye remera rusongati munini rugarama | Governement (District, WASAC) and Water For People | this network has no problem | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 15 | -1.6684773741137722 | 30.047381335897573 | 1775.8 | 24nckozd |  | 2014 | Normal | Yes | 5 | Pressure Break Tank |  | 2014 | Normal | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6822110346478416 | 30.053853619414415 | 1846.1 | 25a2ma7u | 2 | https://waterforpeople.s3.amazonaws.com/images/c0e6340a-5bb1-46d1-aeb0-c970025a9fd0.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | this network is ok | bc308ba3b08149f81a9689d9c48cfcb6
p391-7bgt-842f | 1 |  | J7 Rw24 | 1246240085 | 27-03-2017 08:20:58 CEST | Kabalisa Manzi Christella | 00:22:50 | 2017 | Rwanda | Rulindo | Kisaro | Mubuga | Rutabo |  |  | Gahama Kisaro network | 10234 |  | 740 | 740 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | This system has pump problem it needs to be rehabilitated | 1 | Spring | -1.6671501074688961 | 30.041830412153367 | 1945.4 | 24l5zh36 | https://waterforpeople.s3.amazonaws.com/images/6bc46dbc-d10e-4907-86c1-14a2284b0cbe.jpg | Yes | 3 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/e4685d98-8576-49df-9695-c610c0696784.jpg |  | 2012 | Normal | 3 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/0b131d22-beaf-4a4c-9920-7144ee892480.jpg | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a | https://waterforpeople.s3.amazonaws.com/images/c38613e9-5159-484a-889b-7a7e07cd5db0.jpg | 2012 | Normal | Yes | 14 |  |  | 2012 | Normal | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/f3496b2d-df94-4d9f-b0b0-7518d8f676b6.jpg | 2012 | Poor | Yes | https://waterforpeople.s3.amazonaws.com/images/4f1af7ad-2087-4975-a065-dbda8d56d521.jpg | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6199595800199647 | 30.027459194222658 | 2245.2 | 22f3tho2 | 1 | https://waterforpeople.s3.amazonaws.com/images/0c5148c9-aaf9-4d19-a477-7074728e2646.jpg | 2012 | Normal | No |  |  |  | No | Water was not Pumped | Poor |  | 822729a8255504297e1f25ae36e7145
a4b3-59y0-u4td | 1 |  | J7 Rw23 | 1231900462 | 23-03-2017 06:28:33 CET | Rugirangoga Augustin | 01:24:56 | 2017 | Rwanda | Rulindo | Buyoga | Gitumba | Munini |  |  | Kiruruma | 8295 |  | 158 | 150 | 8 | Yes | Piped Network with Pump |  | 2014 | Yes | rutabo gitaba nyarubuye remera rusongati rugarama munini cyasuli | Governement (District, WASAC) and Water For People | this network has no problem | 1 | Spring | -1.6681514332446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 2 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 15 | -1.6684773741137722 | 30.047381335897573 | 1775.8 | 24nckozd |  | 2014 | Normal | Yes | 5 | Pressure Break Tank |  | 2014 | Normal | Yes | 3 |  | 2014 | Normal | 9000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6800218880266584 | 30.05654517887784 | 1949.3 | 256g8cr9 | 2 | https://waterforpeople.s3.amazonaws.com/images/3214cc53-f75e-495b-ac46-de4ce835d08b.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | this network has no problem | 2fbf91e53fc585d528a31ad0b9d7a7d6
bfqa-sn81-aunk | 1 |  | J7 Rw24 | 1251100059 | 27-03-2017 08:43:53 CEST | Kabalisa Manzi Christella | 00:09:54 | 2017 | Rwanda | Rulindo | Kisaro | Mubuga | Gako |  |  | Gahama Kisaro network | 10234 |  | 955 | 955 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6671501074688961 | 30.041830412153367 | 1945.4 | 24l5zh36 |  | Yes | 3 | Yes | 1 |  |  | 2012 | Normal | 3 | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 |  |  | 2012 | Normal | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Poor | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.639416515835831 | 30.022274814001918 | 2215.7 | 23baf0u6 | 1 | https://waterforpeople.s3.amazonaws.com/images/40edfc03-aa39-425a-befe-d98471a1ac9c.jpg | 2012 | Poor | No |  |  |  | No | System under rehabilitation | Poor | System needs rehabilitation | f561f18f37f05e88655e90a29a632bdb
62s7-tqx2-4fva | 1 |  | J7 Rw10 | 1221960395 | 13-03-2017 22:13:55 CET | Tuyisenge Vianney | 00:12:07 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Kivure source/Buramira gravity system | 1255 |  | 134 | 134 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | GoR | The water point operates well and the source is well captured | 2 | Spring | -1.6776639816373493 | 29.911131429480132 | 2061.4 | 252jq0vb | https://waterforpeople.s3.amazonaws.com/images/c59c862b-bd40-4b6e-9d20-0ebc5bc6043b.jpg | Yes | 30 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/f49a7198-9926-4eff-bbb2-78f7223748d0.jpg | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 30 | Yes | 1 |  | 2015 | Normal | 100 | Yes | 2 | -1.6776970382145038 | 29.91108363159739 | 1905.9 | 252libom | https://waterforpeople.s3.amazonaws.com/images/be7c36dc-7d88-4184-bb4e-5d3e811c1df0.jpg | 2015 | Normal | Yes | 2 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/3b836203-ae24-4ac2-a02c-f16fe771d335.jpg | 2015 | Normal | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/883560f8-6e3f-4044-be56-e01f54384919.jpg | 2015 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.677436728919955 | 29.911288457251604 | 1967.1 | 252611yg | 1 | https://waterforpeople.s3.amazonaws.com/images/c03bda9a-ba28-458b-ab26-e0e7bd27ada0.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The protected springs needs repairs | 437aa8849bfe30a97acf56ff7a64fce7
gqcy-6ma2-41vq | 1 |  | J7 Rw24 | 1223911308 | 16-03-2017 08:50:19 CET | Kabalisa Manzi Christella | 00:07:01 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Rugaragara |  |  | charity water 203.033 | 6572 |  | 815 | 815 | 0 | Yes | Piped Network with Pump |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8024532750946713 | 30.042616473975034 | 1748.3 | 2asxebwq |  | Yes | 3 | Yes | 1 |  |  | 2016 | Normal | 3 | Yes | 1 |  | 2016 | Normal | 35000 | Yes | 10 | -1.7575350016834248 | 30.02449548695202 | 1874.2 | 28qmz6dw |  | 2016 | Normal | Yes | 6 |  |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 1000 | Yes | 3 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7717579606659892 | 30.029869548529824 | 1966.9 | 29e5lkne | 1 | https://waterforpeople.s3.amazonaws.com/images/54cf3c35-3223-45c4-944b-4026ccbc63cf.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | f53a619a12e348d8c2d2d660b864a95d
fryj-24sm-k0rm | 1 |  | J7 Rw19 | 1242890311 | 23-03-2017 03:26:09 CET | Kayinamura Innocent | 01:01:56 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Ruri |  |  | Mutagata Gravity network | 26296 |  | 189 | 40 | 149 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | Ruri, Musenga, Rukurazo, Umubuga, Amataba, Rusine, Marenge |  |  | 1 | Spring | -1.8023389079852206 | 30.042447389592418 | 1691.2 | 2asq94nc | https://waterforpeople.s3.amazonaws.com/images/3ade1118-6a78-4dd1-a45f-9065637349ec.jpg | Yes | 8 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/ace40a9d-6d82-42a9-a5d4-ec058a07f34d.jpg | "Springbox" --Intake Structure at a Spring | 2004 | Poor | 8 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/6670b137-1dad-42fe-87af-b036746afc79.jpg | 2004 | Poor | 3500 | Yes | 6 | -1.8078446763653504 | 30.066649761552014 | 1669.8 | 2b1uaz5m | https://waterforpeople.s3.amazonaws.com/images/a204273f-8d63-46f6-92a6-a74355e2c715.jpg | 2004 | Poor | Yes | 4 | Distribution Chamber¦Washout, Air release chamber |  | 2004 | Poor | Yes | 2 |  | 2004 | Poor | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8025238426219097 | 30.04270428949008 | 1749.1 | 2at1kd57 | 12 | https://waterforpeople.s3.amazonaws.com/images/05ae9c39-8cc9-4afa-8e4e-75fa81fe8ece.jpg | 2004 | Poor | No |  |  |  | Yes |  | Poor | 1. the Extension to Nyabinyana village has 2 reservoirs and two water points which is under construction 2. this system have been constructed in 2004 3. it serve a party of Masoro Sector and other party is located in Gasabo District 4. 2 water points and one reservoir have been constructed in 2016. 5. in general, this network has 27 water points in which 12 are in Rulindo District and the remaining are in Gasabo District. | e84087ac3e5b4fe3c37325db68a2311b
tx91-tnj1-kgg8 | 1 |  | J7 Rw24 | 1217930854 | 16-03-2017 07:15:57 CET | Kabalisa Manzi Christella | 00:06:09 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Kigabiro |  |  | Rwamugaza | 14106 |  | 565 | 565 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | 2 | no problem | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7475657260833042 | 30.05411904060127 | 1861.9 | 28a5e0hp | 1 | https://waterforpeople.s3.amazonaws.com/images/54953240-670d-43c2-ac8f-dd1a7ebc85c6.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | no problem | 371e1337c5f3f776ddbcf362ea624b3b
qfw4-f6x6-c5qb | 1 |  | J7 Rw10 | 1220450960 | 13-03-2017 08:20:24 CET | Tuyisenge Vianney | 00:14:31 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Karambi |  |  | Nyabishengeshi source/Nyabishengeshi gravity system | 893 |  | 79 | 79 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Government | This water source named Nyabishengeshi for gravity system,operates very well. | 2 | Spring | -1.6778517470929726 | 29.880934967401814 | 2032.3 | 252v194p | https://waterforpeople.s3.amazonaws.com/images/d2f5a6a6-e54c-4e3f-b9f1-545c6f7de997.jpg | Yes | 50 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/2a09787f-fe08-4f89-b4eb-3583e1306bc9.jpg | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 50 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/4d832c29-3c21-46fc-8dc1-0c970e2a6fd7.jpg | 2013 | Normal | 1000 | Yes | 1 | -1.6772837603096855 | 29.8817639879645 | 2022.1 | 251x3jnl | https://waterforpeople.s3.amazonaws.com/images/6ad2daf7-9d1c-41e4-8653-0f80ca71a266.jpg | 2013 | Normal | No | [5 empty] | Yes | 4 | https://waterforpeople.s3.amazonaws.com/images/ea83f9eb-f2c6-4469-b301-3a408629e655.jpg | 2013 | Normal | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6770909664344702 | 29.881803989351255 | 1991.1 | 251lsb5u | 1 | https://waterforpeople.s3.amazonaws.com/images/ef8d94c3-96fa-4688-b90f-e913485fe775.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | This water has water points operating very | 6a27fbacd589aed6b9d7b816e6533d97
7hu9-j8wg-ys0v | 1 |  | J7 Rw7 | 1247570193 | 24-03-2017 12:27:43 CET | Safari Bosco | 00:17:36 | 2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Rusenyi |  |  | marenge | 5544 |  | 156 | 156 | 0 | Yes | Piped Network with Pump |  | 1998 | Yes | marembo,rusenyi | Governement (District, WASAC) and Water For People | mumfura nibwo riba rifite amazi | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | No | [5 empty] | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.831856902066767 | 30.05375436388424 | 1765.2 | 2c5jsqih | 2 | https://waterforpeople.s3.amazonaws.com/images/7e1c8f42-1574-4b96-923e-294366cd7000.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | b22feaa0196dc17b7bece9d625a11dc
vhqr-ac0w-qgxr | 1 |  | J7 Rw15 | 1201290278 | 08-03-2017 07:19:52 CET | Mukakarangwa Assoumpta | 00:39:58 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatimba |  |  | kinywamagana pumping network | 6436 |  | 217 | 10 | 207 | Yes | Piped Network with Pump |  | 2013 | Yes | Kigarama | Governement (District, WASAC) and Water For People | The water tap does not function properly | 7 | Spring | -1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 | https://waterforpeople.s3.amazonaws.com/images/8aaa8509-fddf-45b0-8d9c-7428d32f44eb.jpg | Yes | 10 | Yes | 3 | https://waterforpeople.s3.amazonaws.com/images/b60dcc6f-8a26-48c9-9429-f17a5ae068fb.jpg | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/b9d10521-78c8-4582-ac0b-fa1d42070d41.jpg | 2013 | Normal | 1500 | Yes | 20 | -1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 | https://waterforpeople.s3.amazonaws.com/images/a6573ecc-4fc8-4cc2-b0b5-95cfe2cefaf5.jpg | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout | https://waterforpeople.s3.amazonaws.com/images/b694f52d-c228-47b6-9e93-7598c87952d2.jpg | 2013 | Normal | Yes | 4 | https://waterforpeople.s3.amazonaws.com/images/07e1953e-ab0a-4678-9cf2-9f9c67ddd925.jpg | 2013 | Normal | 11000 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/affc714f-3cb7-4a00-ae4d-770eee98a9f0.jpg | 2013 | Poor | Yes | https://waterforpeople.s3.amazonaws.com/images/320ee8af-f8aa-48dc-95ce-5ad84e9571f6.jpg | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8476627251150932 | 29.971217585140035 | 1765.9 | 2cvp31a8 | 1 | https://waterforpeople.s3.amazonaws.com/images/60611209-38a6-448f-a046-533f1a7be345.jpg | 2013 | Poor | No |  |  |  | Yes |  | Poor | -This network has 7 sources,3 of them does not function because of the destruction of pipes from sources to pumping station and power management of catchment sources. -There are some parts of pumps which do not function properly like pressure gauge, voltmeter, water hammer and crapier. | e3d07cecd99ca9e6b1bd0182f344de
f7pe-d39h-3te6 | 1 |  | J7 Rw24 | 1220870417 | 16-03-2017 09:02:23 CET | Kabalisa Manzi Christella | 00:14:35 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kanyoni |  |  | charity water 203.037 | 6572 |  | 640 | 640 | 0 | Yes | Piped Network with Pump |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8024532750946713 | 30.042616473975034 | 1748.3 | 2asxebwq |  | Yes | 3 | Yes | 1 |  |  | 2016 | Normal | 3 | Yes | 1 |  | 2016 | Normal | 2000 | Yes | 3 | -1.7575350016834248 | 30.02449548695202 | 1874.2 | 28qmz6dw |  | 2016 | Normal | Yes | 6 |  |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 2000 | Yes | 3 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7808728324913405 | 30.027407432295764 | 2003.1 | 29t8kwc2 | 1 | https://waterforpeople.s3.amazonaws.com/images/71366ea9-fbd2-4555-b38a-8dd3d1ae8a04.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 1c4157f68b5d4a204ea8928e2816432
mg7u-jffj-m90t | 1 |  | J7 Rw26 | 1241060219 | 03-01-2015 04:54:41 CET | Byukusenge Elie | 00:05:04 | 2017 | Rwanda | Rulindo | Rukozo | Mberuka | Mataba |  |  | Kabonanyoni | 7894 |  | 75 | 70 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare, Kabera,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe, Kabyayi, Kabingo, Kamiyove, Murwa, Nyenyeri, Rukingu and Kivomo | Governement (District, WASAC) and Water For People | This is the New pumping system which serves the community located at the uphill, it has 5 sources, one source which is located in Miyove sector, Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro,This network has one reservoir which is not functioning, This network serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6197019944239157 | 29.956033960278273 | 2084.1 | 22eoxmzs | 31 | https://waterforpeople.s3.amazonaws.com/images/d3a5ea69-6738-46fb-a543-6d7748fd06df.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | 5c6ab099c8fc58cda2c75fc141ffbd9
gnms-286n-0807 | 1 |  | J7 Rw24 | 1324950232 | 24-04-2017 23:17:04 CEST | Kabalisa Manzi Christella | 00:11:34 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Kabirizi |  |  | Rwamugaza network | 14106 |  | 148 | 148 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7374173333138418 | 30.06563288387298 | 1723.9 | 27td31kg |  | 2003 | Normal | Yes | 14 |  |  | 2003 | Normal | Yes | 1 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.769042553438832 | 30.073308624203612 | 1654.8 | 299o941p | 1 | https://waterforpeople.s3.amazonaws.com/images/0675db11-d17d-4557-bc9e-d83d07b2851e.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 7942cfdd3c639dfa671c36903a630cf
njsf-0tsw-afwe | 1 |  | J7 Rw8 | 1238780175 | 23-03-2017 10:10:42 CET | Amani Desire | 00:11:29 | 2017 | Rwanda | Rulindo | Murambi | Bubangu | Ruhunga |  |  | Mutagata Motorised Network | 26296 |  | 112 | 112 | 0 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.04275565044753 | 1708.3 | 2arxobm3 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.79689424299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8308159517353995 | 30.02397561980076 | 1917.1 | 2c3tvndb | 6 | https://waterforpeople.s3.amazonaws.com/images/0c878870-1700-460b-a6cb-e77c708df23d.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | 4cfcfabaf2add4a8442afdbcfb04afe
y6u0-cf2c-1gdu | 1 |  | J7 Rw8 | 1221330206 | 16-03-2017 08:53:24 CET | Amani Desire | 00:10:50 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  | Musenge Network | 6074 |  | 186 | 41 | 145 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi |  |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7378732349103467 | 29.92809884886626 | 2000.3 | 27u4gyc0 | 28 | https://waterforpeople.s3.amazonaws.com/images/09daea9e-93c7-4e27-8873-7b3eac3fd5b2.jpg | 2014 | Does Not Function | Yes | 8 | 30 | all water served by R50m3 located at kibamba village do not have water today | No | water points served by R50m3 located at kibamba village do not have water | Does Not Function | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | ed4b922d768243c92d6cbc234d7eb8a
u0tq-498b-4fda | 1 |  | J7 Rw24 | 1328800050 | 24-04-2017 23:36:24 CEST | Kabalisa Manzi Christella | 00:19:15 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyagasozi |  |  | Rwamugaza network | 14106 |  | 197 | 197 | 0 | Yes | Piped Network with Pump |  | 2014 | Yes | nyagisozi,gacyamo | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  | null | 2014 | Normal | 3 | Yes | 2 |  | 2014 | Normal | 35000 | Yes | 7 | -1.7374173333138418 | 30.006563288387298 | 1723.9 | 27td3141 |  | 2014 | Normal | Yes | 14 |  |  | 2014 | Normal | Yes | 1 |  | 2014 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7548332727858367 | 30.057301410270863 | 1868.9 | 28m685b1 | 1 | https://waterforpeople.s3.amazonaws.com/images/92178cac-3031-47b2-8b71-249f79eaeff5.jpg | 2014 | Poor | Yes | 2 | 120 | Water is not enough and doesn’t reach well the tap | No | Irregular Supply | Poor | Irregular supply on the system | 14584c9030b5cece9eaa112678e72f75
re4h-13fr-t4bk | 1 |  | J7 Rw26 | 1217400116 | 11-03-2017 09:10:48 CET | Byukusenge Elie | 00:12:16 | 2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatwa |  |  | Nyamagana | 20456 |  | 850 | 850 | 0 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and some population in Kabingo Village im Base Sector | Government and African Development Bank |  | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.650363504142119 | 29.936084296808996 | 1792.3 | 23tecnkw | 29 | https://waterforpeople.s3.amazonaws.com/images/afa009a7-dd02-4d64-ac3b-54cc71621de1.jpg | 2011 | Normal | Yes | 10 | 32 | Bad tee connection and the types of pipeline needs partial rehabilitation | Yes |  | Poor | This water tap is used by students and staff of G.S.Murambo | 5ba4cf6c622bd7deaa5dcc0138fe65
3pwr-c8je-sbed | 1 |  | J7 Rw23 | 1217610106 | 12-03-2017 18:41:14 CET | Rugirangoga Augustin | 00:09:57 | 2017 | Rwanda | Rulindo | Base | Gitare | Gisiza |  |  | Rwicanyoni | 698 |  | 116 | 110 | 6 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | gisiza kirwa gatete | Governement (District, WASAC) and Water For People | the network works properly | 2 | Spring | -1.6644377224987001 | 29.903649586570488 | 1928 | 24go1jh8 |  | Yes | 10 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 10 | Yes | 1 |  | 2016 | Normal | 8600 | Yes | 3 | -1.6605194594779042 | 29.90927074216649 | 1808.8 | 24a6nmdw |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6503503299295477 | 29.90156529604597 | 1775.3 | 23tdr7pj | 2 | https://waterforpeople.s3.amazonaws.com/images/46647e2c-aaa9-4cfd-a84f-95639fd74f92.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | 31488941cdfc8cac3562508ec121c77b
u8tr-29b2-6bbb | 1 |  | J7 Rw15 | 1211680230 | 08-03-2017 22:37:09 CET | Mukakarangwa Assoumpta | 00:06:23 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Bugarura |  |  | kirikumuryango network |  |  | 119 | 61 | 58 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8883216455946839 | 29.97346943254691 | 1445.8 | 2eqxviza | 1 | https://waterforpeople.s3.amazonaws.com/images/53ef4eed-b2a7-4787-a94a-c361dc6d6bf8.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | fc50f56ba233e9dd39e84e5e1619ced
t3hu-a6u3-hh6j | 1 |  | J7 Rw8 | 1221220716 | 16-03-2017 08:48:35 CET | Amani Desire | 00:11:29 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gicumbi |  |  | Musenge Network | 6074 |  | 141 | 30 | 111 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi |  |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.777983528964204 | 29.944776372326473 | 1906.7 | 29ogilvb | 28 |  | 2014 | Normal | No |  |  |  | Yes |  | Normal | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | 49db3f12608abe1687fa8a539e523017
mu4j-kr4k-tb78 | 1 |  | J7 Rw19 | 1228330619 | 23-03-2017 05:08:15 CET | Kayinamura Innocent | 00:15:59 | 2017 | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 26296 |  | 325 | 70 | 255 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7952032286038397 | 30.043999486060134 | 1923.5 | 2agxr2c7 | 64 | https://waterforpeople.s3.amazonaws.com/images/fa1907a1-66c0-4a8c-8263-cf9f85879052.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | da75afc6d14c3ad468e53df547252c2f
j702-c0hx-4twu | 1 |  | J7 Rw26 | 1185481511 | 07-03-2017 12:58:05 CET | Byukusenge Elie | 00:13:37 | 2017 | Rwanda | Rulindo | Cyungo | Marembo | Murambo |  |  | Mugomero Marembo | 3456 |  | 161 | 150 | 11 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | Gahinga, Nganzo,Rusango, Buyaga and Murambo | Governement (District, WASAC) and Water For People | The source of this network is located in Burera District and this network serves three villages in Burera and it has eight water taps, one starting chamber and reservoirs im Burera and This network end in Marembo Center and it needs some extentions to serves two villages (Kidomo, Kibuye) which have not the network | 1 | Spring | -1.5777496463341437 | 29.93714072556937 | 2147.8 | 20haqsiz |  | Yes | 120 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 120 | Yes | 2 |  | 2015 | Normal | 10000 | Yes | 10 | -1.5961706844323926 | 29.9125708534345822 | 2085.4 | 21bs0o8l |  | 2015 | Normal | Yes | 3 | Distribution Chamber |  | 2015 | Normal | Yes | 2 |  | 2015 | Normal | 10000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6214856650884248 | 29.90951708504146 | 1998.1 | 22hmwsbb | 1 | https://waterforpeople.s3.amazonaws.com/images/1e0d8de8-dd7a-4392-b4c4-5585576a05d8.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This watee tap is located near Marembo Cell office and the community does not use it ,they prefer to use the local springs | c0bd5ffc841a2b7ac2aac855e3c239f
46x1-sndw-pucn | 1 |  | J7 Rw26 | 1240570251 | 21-03-2017 14:08:20 CET | Byukusenge Elie | 00:07:15 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Murwa |  |  | Kabonanyoni | 7894 |  | 800 | 800 | 0 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6524950674869425 | 29.9699706256412 | 1780.6 | 23wx5zoz | 31 | https://waterforpeople.s3.amazonaws.com/images/0417d8ef-4d18-45ab-a7b4-58f373b57d3b.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is used by the students and staff of E.P.Murwa. | 8fb96cc4a054ee75ea81b767e139a9
pe5h-hxrk-2sxe | 1 |  | J7 Rw10 | 1235970214 | 03-01-2015 02:18:26 CET | Tuyisenge Vianney | 00:04:26 | 2017 | Rwanda | Rulindo | Tumba | Barari | Gaseke |  |  | Water point at Rukore Primary School/Nyirambuga pumping | 30604 |  | 149 | 149 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | Everything operates normally the water is available everyday.But taps valves have not yet been fixed | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7153669393819335 | 29.930398042369774 | 1808.3 | 26swa7mv | 2 | https://waterforpeople.s3.amazonaws.com/images/45891b8d-dc8b-4d97-b8d8-8de9695af326.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | Everything operates normally the water is available everyday.But taps valves have not yet been fixed | 6c606d73d6bb734ba0a816f92a81d24
mk9k-pt7e-vk62 | 1 |  | J7 Rw10 | 1234520195 | 02-01-2015 12:51:35 CET | Tuyisenge Vianney | 00:06:34 | 2017 | Rwanda | Rulindo | Buyoga | Karama | Cyasenga |  |  | Water point at GS Kadendegere/Nyirambuga pumping | 30604 |  | 165 | 165 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point at GS Kadendegere.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water. | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.7148013764276964 | 29.98285919009786 | 2087.5 | 26ryxy5w | https://waterforpeople.s3.amazonaws.com/images/e0fbcdde-b71c-4428-b119-267c9aa837d8.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7151673180129632 | 29.982110397231704 | 2104.7 | 26skdjxp | 4 | https://waterforpeople.s3.amazonaws.com/images/2f80b753-4d12-4c5c-8229-3f77606c32bc.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point at GS Kadendegere.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water. | 9c25ae3d773c462eeb6c32c7851f466
ngb0-59q0-xvfd | 1 |  | J7 Rw23 | 1225560265 | 15-03-2017 07:40:10 CET | Rugirangoga Augustin | 00:18:49 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutembe | 1012 |  | 229 | 200 | 29 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | this network works partialy | 2 | Spring | -1.6452293607002955 | 29.88940159790624 | 1774.8 | 23kwbua6 |  | No | 50 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Poor | 50 | Yes | 1 |  | 2016 | Poor | 4000 | Yes | 2 | -1.6350822337877793 | 29.89531663121816 | 1775.1 | 2344max5 |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6514228986763058 | 29.88436971608385 | 1718.7 | 23v5glaz | 2 | https://waterforpeople.s3.amazonaws.com/images/1d2ce04f-15bf-40ce-a15f-50d7da462399.jpg | 2016 | Does Not Function | No |  |  |  | No | water does not reach the water tap bacause of the high elevation of the source compared to the tank | Poor | this water tap does not have water | 5c7cd66326ab1c92cc55bbe7b5f7d3b9
7m38-7u24-r2y3 | 1 |  | J7 Rw8 | 1247400104 | 23-03-2017 08:07:07 CET | Amani Desire | 00:11:19 | 2017 | Rwanda | Rulindo | Murambi | Mvuzo | Iraro |  |  | Mutagata Motorised Network | 26296 |  | 147 | 147 | 0 | Yes | Piped Network with Pump |  | 2016 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7836450281086484 | 30.019508909198894 | 1970.2 | 29xthyub | 64 | https://waterforpeople.s3.amazonaws.com/images/a667a2c6-15f4-4f63-9f56-1b059fbf528a.jpg | 2016 | Poor | No |  |  |  | Yes |  | Poor | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | 2b23ed033673c92e2e4493436d46d81
wsc8-hfax-ejcp | 1 |  | J7 Rw10 | 1314160056 | 20-04-2017 07:56:11 CEST | Tuyisenge Vianney | 00:06:55 | 2017 | Rwanda | Rulindo | Tumba | Misezero | Taba |  |  | Water point chez Nsekanabo/Nyirambuga pumping | 30604 |  | 100 | 100 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | People fetch from the washout | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | Yes | 1 | -1.6912437217100402 | 29.956331646808437 | 2019 | 25p08oq3 | https://waterforpeople.s3.amazonaws.com/images/b5c6578f-0870-4cf6-9ea0-f06781eed47d.jpg | 2017 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6910869237346702 | 29.956280353314483 | 2030.9 | 25oqpr1m | 1 | https://waterforpeople.s3.amazonaws.com/images/18b313c2-4b54-43ee-a0f3-db5e731f0ef2.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | operational | dede4df04ba2e84d46c0d7dbdaa6f5a1
dej8-r7at-gbu7 | 1 |  | J7 Rw23 | 1198760261 | 08-03-2017 16:43:06 CET | Rugirangoga Augustin | 01:05:09 | 2017 | Rwanda | Rulindo | Base | Gitare | Nyamugali |  |  | Rutembe | 1012 |  | 121 | 65 | 56 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | Base Nyamugali | Governement (District, WASAC) and Water For People | This systems doent function well due to some broken piepes and water doesn’t reach the reservior | 2 | Groundwater (well, etc.) | -1.6451884854420848 | 29.88948901942251 | 1747.3 | 23kty3v2 |  | Yes | 60 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Poor | 60 | Yes | 1 |  | 2017 | Poor | 2500 | Yes | 2 | -1.6508199697188073 | 29.884369144843145 | 1716 | 23u555ej |  | 2016 | Does Not Function | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6546077559400407 | 29.882232774277984 | 653.1 | 240esfnq | 2 |  | 2016 | Does Not Function | Yes | 1 | 300 | Low Pressure and many users | No | Water doesn’t reach Water Tap | Does Not Function | System needs rehabilitation | c830b6546d53a85564e7047ea976961
2xd2-9krs-8k2r | 1 |  | J7 Rw15 | 1205030313 | 08-03-2017 22:08:43 CET | Mukakarangwa Assoumpta | 00:08:00 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Mwagiro |  |  | Kirikumuryango network |  |  | 139 | 22 | 117 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦Ventouse,Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8731546786834028 | 29.974998052780794 | 1594.1 | 2e1uoyat | 1 | https://waterforpeople.s3.amazonaws.com/images/33258c22-19d9-41ad-af24-fea36376b41c.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | d788198f6d31d84d89c5093e476786d
98e2-7nvg-0dkw | 1 |  | J7 Rw10 | 1238430336 | 03-01-2015 01:57:17 CET | Tuyisenge Vianney | 00:04:23 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Water point at EP Murambi Publique/Nyirambuga pumping | 30604 |  | 174 | 174 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Storage tank valve chamber nolonger have cover.All taps are closed.Water point not used | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.6935011067923973 | 29.91963503568733 | 2134.5 | 25sqsn5o | https://waterforpeople.s3.amazonaws.com/images/fb2ee290-04f2-4225-89a5-d0229f5e6969.jpg | 2012 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6935027110371177 | 29.919570992972112 | 2121.9 | 25sqsn5n | 2 | https://waterforpeople.s3.amazonaws.com/images/2fe58a0f-eca9-48b2-947e-8d97bbf1d2c5.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Storage tank valve chamber nolonger have cover.All taps are closed.Water point not used | 2ad19a2e54d0c933a4875e754facfe8d
45q7-dus0-8mn1 | 1 |  | J7 Rw23 | 1220470535 | 15-03-2017 08:04:09 CET | Rugirangoga Augustin | 00:38:59 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 2456 |  | 214 | 200 | 14 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | buramba mushongi | Governement (District, WASAC) and Water For People | Water system has no problem | 1 | Spring | -1.6358367374763643 | 29.9135277934778 | 1996.9 | 235d9tfj |  | Yes | 15 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 15 | Yes | 1 |  | 2016 | Normal | 7200 | Yes | 6 | -1.6498521069502532 | 29.917613599705728 | 1996.9 | 23sjzjl4 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6514902823238626 | 29.918754184005493 | 1751.9 | 23v9mmsz | 2 | https://waterforpeople.s3.amazonaws.com/images/1edcc74c-28c6-4101-9901-13076f996d39.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | df9e57c9a8545e4a82c9f8d6faf2e5c
93dg-9ykw-b59q | 1 |  | J7 Rw10 | 1307430070 | 16-04-2017 21:55:56 CEST | Tuyisenge Vianney | 00:06:29 | 2017 | Rwanda | Rulindo | Base | Gitare | Mugenda I |  |  | Water point near Gitare school/Nyirambuga pumping system | 30604 |  | 117 | 117 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | The water point operates normally though its tap stands got disturbed and not well functioning.The opening towards water meter box got damaged and it exposes the water meter to theft.The beneficiaries last saw last July of 2016 and they fetches once. | 1 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6596596378457802 | 29.896647298003096 | 2009.4 | 248rgc9i | 2 | https://waterforpeople.s3.amazonaws.com/images/919fc0c9-7b66-49d9-a34c-30a87cdb3e12.jpg | 2012 | Poor | No |  |  |  | No | The water point operates normally though its tap stands got disturbed and not well functioning.The opening towards water meter box got damaged and it exposes the water meter to theft.The beneficiaries last saw last July of 2016 and they fetches once. | Poor | The water point operates normally though its tap stands got disturbed and not well functioning.The opening towards water meter box got damaged and it exposes the water meter to theft.The beneficiaries last saw last July of 2016 and they fetches once. | 6684a6ef1557039a4b7add3cb3789c
mb40-7fcc-kd10 | 1 |  | J7 Rw10 | 1289334452 | 15-04-2017 22:12:54 CEST | Tuyisenge Vianney | 00:05:20 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Water point2 at Gasiza market/Nyagahondo gravity system | 844 |  | 228 | 228 | 0 | Yes | Piped Network -- Gravity Only |  | 2010 | No |  | Caritas | The water tap stand got damaged.It does nolonger function.People have the habit of damaging the taps.However,water reaches the system.People have denied to pay the water cost and prefered to damage it | 1 | Spring | -1.7298781428197503 | 29.909858739201194 | 2099.2 | 27gw668q |  | Yes | 30 | No | [5 empty] | 30 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7305043580200132 | 29.920536323739245 | 1783.6 | 27hxohfp | 1 | https://waterforpeople.s3.amazonaws.com/images/c40cd160-94f5-4194-86de-dc2232b97bc6.jpg | 2010 | Does Not Function | No |  |  |  | No | The water tap stand got damaged.It does nolonger function.People have the habit of damaging the taps.However,water reaches the system.People have denied to pay the water cost and prefered to damage it | Does Not Function | The water tap stand got damaged.It does nolonger function.People have the habit of damaging the taps.However,water reaches the system.People have denied to pay the water cost and prefered to damage it | bd624b4af91a19b13cd9affe7b77cfd
3ms6-7yn9-t8a8 | 1 |  | J7 Rw24 | 1251080086 | 27-03-2017 08:31:58 CEST | Kabalisa Manzi Christella | 00:07:50 | 2017 | Rwanda | Rulindo | Kisaro | Murama | Ryarubuguza |  |  | Gahama Kisaro network | 10234 |  | 495 | 495 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6671501074688961 | 30.041830412153367 | 1945.4 | 24l5zh36 |  | Yes | 3 | Yes | 1 |  |  | 2012 | Normal | 3 | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 |  |  | 2012 | Normal | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6218943822060037 | 30.027841831103952 | 2245.8 | 22ibbl12 | 1 | https://waterforpeople.s3.amazonaws.com/images/1eaa00ca-7f6f-4e8a-9b78-e01c8cc564f7.jpg | 2012 | Normal | No |  |  |  | No | Water seller was not around | Poor | System is under rehabilitation | 3b18291ac12b523523555e34e8dc6714
etpa-gres-3gj1 | 1 |  | J7 Rw26 | 1232820611 | 21-03-2017 14:18:22 CET | Byukusenge Elie | 00:05:30 | 2017 | Rwanda | Rulindo | Rukozo | Mbuye | Kibare |  |  | Kabonanyoni | 7894 |  | 90 | 85 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.9534263452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.95850379141477 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6230942128852763 | 29.965152059088016 | 1842.4 | 22karl4z | 31 | https://waterforpeople.s3.amazonaws.com/images/d52ff047-6d2e-45a7-b729-150ecd1e3e5c.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water tap located near ADEPR church | 76dfb446c03e80e34a4845d6fa818cab
c6ph-y57w-7t03 | 1 |  | J7 Rw10 | 1245400342 | 22-03-2017 14:26:02 CET | Tuyisenge Vianney | 00:06:16 | 2017 | Rwanda | Rulindo | Rusiga | Taba | Nyakarama |  |  | Nyakarama water point/Nyakabizi gravity | 1259 |  | 101 | 101 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People | This water point is sole operational in Gitanda.It has got 3 water points it serves in Taba cell(Gitanda) | 2 | Spring | -1.803447729664134 | 29.930708856826865 | 1927.1 | 2aukc7xn |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | Yes | 1 | -1.8195626482318565 | 29.921340573409292 | 1731.1 | 2bl82z0t | https://waterforpeople.s3.amazonaws.com/images/1a168869-dfbc-4140-80b7-4bc01aeb4f48.jpg | 2013 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8194666819901903 | 29.921435030115436 | 1743.2 | 2bl24mz2 | 2 | https://waterforpeople.s3.amazonaws.com/images/6b5d71da-ec5f-4ebe-a62f-246ded5d2009.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | This water point is sole operational in Gitanda.It has got 3 water points it serves in Taba cell(Gitanda).However the water storage tank external walls has started cracking and eventually leaking | aa42578d1f11755d234717e8498d6b99
nk5v-qmbr-xj5 | 1 |  | J7 Rw15 | 1237120291 | 21-03-2017 14:50:42 CET | Mukakarangwa Assoumpta | 00:21:38 | 2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Magezi |  |  | Miyove-Kinihira | 10452 |  | 141 | 70 | 71 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦Ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6567950978852406 | 29.987859119397267 | 1944.4 | 24416dye | 1 | https://waterforpeople.s3.amazonaws.com/images/668da65c-3fa4-4224-9887-a9d493ba8b0a.jpg | 1989 | Poor | No |  |  |  | Yes |  | Poor | water point is poor because is not in good condition. | ceba43ebd5ce53427e1b0393d573dfa
gap4-gsfv-cwq1 | 1 |  | J7 Rw8 | 1238780152 | 23-03-2017 09:52:59 CET | Amani Desire | 00:17:28 | 2017 | Rwanda | Rulindo | Murambi | Gatwa | Amataba |  |  | Mutagata Motorised Network | 26296 |  | 134 | 134 | 0 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2017 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.81241563131564 | 30.03548901876885 | 1883.1 | 2b9ee2de | 64 | https://waterforpeople.s3.amazonaws.com/images/9f5f29e5-0032-4909-b2ba-54bddd17f56f.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | c329ac2a9bacab48eb5ce4b02d38b25
6pk5-7nxu-3ect | 1 |  | J7 Rw10 | 1304460107 | 14-04-2017 22:21:42 CEST | Tuyisenge Vianney | 00:04:54 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Budaha |  |  | Nkombe water point/Nkombe gravity |  |  | 205 | 205 | 0 | Yes | Piped Network -- Gravity Only |  | 2002 | No |  | COFORWA | This is water point located in Nkombe nearby catchment area.It functions well | 1 | Spring | -1.726263209282846 | 29.90351686333194 | 2121.4 | 27ax8ot7 |  | Yes | 18 | No | [5 empty] | 18 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7260117074409786 | 29.90404220657206 | 2091.2 | 27aicuow | 1 | https://waterforpeople.s3.amazonaws.com/images/45359718-ceae-4daf-9131-e135f987d37c.jpg | 2002 | Normal | No |  |  |  | Yes |  | Normal | This is water point located in Nkombe nearby catchment area.It functions well | 3fe8abb689ff3a8e6898c579e4662a2
89vr-hmhb-hw9f | 1 |  | J7 Rw10 | 1232070317 | 03-01-2015 01:17:13 CET | Tuyisenge Vianney | 00:15:39 | 2017 | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point at EP Tumba Public/Nyirambuga pumping | 30604 |  | 115 | 115 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water scarcity at water point of EP Tumba Public is same problem with Buyoga area.To be tackled together.Its R25m3 doesnt have cover on valve chamber.It serves the school | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 2 | -1.7083403262571588 | 29.952389532361302 | 2207.4 | 26habx4z | https://waterforpeople.s3.amazonaws.com/images/20f99b35-22c7-47d1-b264-71455523160e.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7092686466338194 | 29.95088549711994 | 2193.2 | 26it3ss4 | 3 | https://waterforpeople.s3.amazonaws.com/images/1c65e8dc-c538-4044-92cb-67829a53ff26.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water scarcity at water point of EP Tumba Public is same problem with Buyoga area.To be tackled together.Its R25m3 doesnt have cover on valve chamber.It serves the school.It is near to the main reservoir of R300m3 constructed on July22,1983.This main reservoir serves the whole Nyirambuga pumping system distributions of Buyoga,Tumba,Bushoki and Mbogo | f69c480773025a59c4c15afa025203
td5v-cb97-mq3q | 1 |  | J7 Rw26 | 1195270868 | 07-03-2017 11:20:18 CET | Byukusenge Elie | 00:10:07 | 2017 | Rwanda | Rulindo | Cyungo | Marembo | Gahinga |  |  | Mugomero Marembo | 3456 |  | 652 | 602 | 50 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | Kidomo, Gahinga, Nganzo, Rusayo and Murambo | Governement (District, WASAC) and Water For People | The source is located in Burera District and this network serbes three villages in Burera and it has eight water taps on Burera2 and starting chamber even one reservoir | 1 | Spring | -1.5777496463341437 | 29.93714072556937 | 2147.8 | 20haqsiz |  | Yes | 120 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 120 | Yes | 2 |  | 2015 | Normal | 10000 | Yes | 10 | -1.5961706844323926 | 29.91257085345822 | 2085.4 | 21bs0o8l |  | 2015 | Normal | Yes | 3 | Distribution Chamber |  | 2015 | Normal | Yes | 2 |  | 2015 | Normal | 10000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.611583381851107 | 29.91299865059559 | 2059.8 | 2219hng9 | 8 | https://waterforpeople.s3.amazonaws.com/images/f38aadaa-f80a-470f-bcb6-f752cc3e9de4.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | this water is not used because it is located near improved spring that2 most of people use it. | 74677aa1aa4a17e699836e77da364f
udd2-v436-ueqg | 1 |  | J7 Rw19 | 1197872323 | 07-03-2017 15:50:56 CET | Kayinamura Innocent | 00:11:15 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Ruhondo |  |  | Kishwi network | 1309 |  | 184 | 41 | 143 | Yes | Piped Network -- Gravity Only |  | 2003 | Yes | Buraro and Ruhondo | Goverment | One Part of the system was Rehabilitated By the Government (District, WASAC) and Water For People | 1 | Spring | -1.772207769769515 | 29.962926865497884 | 1849 | 29ewe2ct |  | Yes | 25 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2003 | Normal | 25 | Yes | 2 |  | 2016 | Normal | 700 | Yes | 2 | -1.7714946380440713 | 29.963728274178695 | 1845.6 | 29dq4aet |  | 2003 | Normal | No | [5 empty] | Yes | 2 |  | 2003 | Normal | 680 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7702627843739063 | 29.965143407014022 | 1823.2 | 29bovz0j | 4 | https://waterforpeople.s3.amazonaws.com/images/a7f131a2-f033-45ec-857d-44fdfee0b8f1.jpg | 2003 | Poor | No |  |  |  | Yes |  | Normal | Source gets dirty in the rainy season, part of the system was destroyed, one water point is not functional | 3a6c33ead935514b966871744917c4
vffj-rc75-kjta | 1 |  | J7 Rw7 | 1447960466 | 06-06-2017 21:15:01 CEST | Rugirangoga Augustin | 00:25:49 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Gihemba |  |  | kazabazana |  |  | 163 | 140 | 23 | Yes | Piped Network with Pump |  | 1998 | Yes | kirenge gatete |  |  | 2 | Spring | -16675834297797398 | 30.0428712210569 | 1965.7 | l57wd97uj0 |  | Yes | 65 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 65 | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 7 | -1.619758842045289 | 30.0245213756495 | 1796.5 | 22erwtjp |  | 2012 | Normal | Yes | 14 | Pressure Break Tank¦Distribution Chamber¦washout,air release |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6662163702427564 | 30.001570076715723 | 1783.4 | 24jm0pwv | 2 |  | 2012 | Does Not Function | No |  |  |  | Yes |  | Poor | uyu muyoboro ntamazi ufite | 35e7e606ab3b19d4d4284fab3d827
6vkk-746f-gtmr | 1 |  | J7 Rw15 | 1202040534 | 12-03-2017 10:21:00 CET | Mukakarangwa Assoumpta | 00:16:06 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Mukumba |  |  | Bitete-Muvumu | 1316 |  | 92 | 20 | 72 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 3 | Spring | 1.8337482627601935 | 29.943433443706404 | 1749 | 2c8obmzu |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Poor | 1000 | Yes | 4 | 1.8368127107947887 | 29.93457412501046 | 1635 | 2cdr3pn5 |  | 2013 | Normal | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Poor | Yes | 4 |  | 2013 | Normal | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.836937632237202 | 29.934437399136876 | 1633 | 2cdy8wwg | 1 | https://waterforpeople.s3.amazonaws.com/images/556ee541-0bc3-4dbe-aa1f-0dd6ac3da08d.jpg | 2013 | Does Not Function | No |  |  |  | Yes |  | Does Not Function | -Ntabwo rikora kubera ntabantu barivoma ho company yakuyeho compter. | ecb4cfe85d72d7f9ee4dd896ed84ac3
knxx-mmv0-wmb1 | 1 |  | J7 Rw7 | 1244490917 | 19-03-2017 19:57:54 CET | Safari Bosco | 00:20:42 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo |  |  | Cyaruzinge |  |  | 120 | 80 | 40 | Yes | Piped Network -- Gravity Only |  | 1998 | Yes | kabeza gitwa gatiba | Governement (District, WASAC) and Water For People | Partially the system was destroyed by road cosntrcution | 1 | Groundwater (well, etc.) | -1.9608329887916556 | 30.108313748470525 | 1437.1 | 2i2uxnff | https://waterforpeople.s3.amazonaws.com/images/7862f3ca-5791-404c-8cc6-e65cd3644ae5.jpg | Yes | 60 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Does Not Function | 60 | No | [5 empty] | Yes | 5 | -1.9607478453374956 | 30.108194518684037 | 1495.5 | 2i2pkqzd |  | 2017 | Normal | Yes | 8 | Distribution Chamber |  | 2017 | Poor | No | [5 empty] | Yes | 2 |  | 2017 | Normal | No |  |  |  | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.9610126856660148 | 30.10817890049864 | 1487.6 | 2i35ngbd | 2 | https://waterforpeople.s3.amazonaws.com/images/bfcaff21-fed2-4407-bcb2-a298bc67a9e1.jpg | 2017 | Poor | No |  |  |  | Yes |  | Poor | System needs rehabilitation | eae7d2b7d021317666749b1df9af1178
2u3m-5sjr-eaqf | 1 |  | J7 Rw7 | 1438131183 | 06-06-2017 15:34:42 CEST | Rugirangoga Augustin | 00:20:45 | 2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Gatete |  |  | gahama | 10234 |  | 163 | 140 | 23 | Yes | Piped Network with Pump |  | 2012 | Yes | ruberano gishinge akamanama ryarubuguza |  |  | 2 | Spring | -1.6675834297797398 | 30.0428712210569 | 1965.7 | 24lvl43w |  | Yes | 0 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 65 | Yes | 2 |  | 2012 | Normal | 12000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 | Pressure Break Tank¦Distribution Chamber¦washout,air release |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 12000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6189420351033565 | 30.03585365582292 | 1935.3 | 22dfopmu | 1 | https://waterforpeople.s3.amazonaws.com/images/3a711fdd-614d-48f6-8ce0-997ee0a5768c.jpg | 2012 | Does Not Function | No |  |  |  | No | ivomo ryarangiritse | Does Not Function | iri vomo ntabwo rikora .ryarangiritse | cb7044b7527427771ae4cfe814399ce
mxaf-f4be-xg26 | 1 |  | J7 Rw10 | 1224900474 | 16-03-2017 17:46:48 CET | Tuyisenge Vianney | 00:04:16 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | Rwintare2 water point/Tare-Rusiga pumping | 9577 |  | 281 | 281 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This water point is also located in Rwintare village of Gako/Rusiga.It operates very well and normally | 1 | Spring | -1.69919116767908 | 29.937233740854015 | 1848.2 | 2625kai4 |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.835997002880581 | 29.955502837955834 | 2031.1 | 2ccea677 | 1 | https://waterforpeople.s3.amazonaws.com/images/ba03d86e-5bf9-446c-8f11-388c2b3d175a.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water point is also located in Rwintare village of Gako/Rusiga.It operates very well and normally | aa46dda7856fdf106369d8f12e0f6d7
1f8m-m1vc-sttg | 1 |  | J7 Rw19 | 1216842375 | 17-03-2017 05:23:31 CET | Kayinamura Innocent | 00:17:09 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Munini |  |  | Musenge network | 6074 |  | 111 | 62 | 49 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma, Karehe, Rutonde, Gitaba, Kiruri, Buhera, Ruhanya, Kibamba and Karindi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Washout and Air release chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7940501170376564 | 29.952318295912054 | 2031.8 | 2af1a72b | 28 | https://waterforpeople.s3.amazonaws.com/images/13007b45-36fa-44bc-9230-dcfb2a486c3a.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | 1. The system has two Pumps but one is damaged and is not working, only one pump is used to pump water 2. Eleven (11) water points served by the distribution reservoir R 50m3 located at Kibamba village do not have water today because water don't reach this reservoir, there is not water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5. one water point doesn't Function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water points and reservoir being under construction | 694f57c032262bee4e2c339b463ca891
ubmc-dt3s-r1b5 | 1 |  | J7 Rw24 | 1252810216 | 28-03-2017 10:41:02 CEST | Kabalisa Manzi Christella | 00:21:50 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Kararama network | 6572 |  | 193 | 193 | 0 | Yes | Piped Network with Pump |  | 2009 | No |  | umushinga witwa Ema |  | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 1 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 7 | -1.7558238738774876 | 30.05848449136532 | 1855.1 | 28nt627c |  | 2003 | Normal | Yes | 14 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7607032986882079 | 30.065943246225913 | 1845.8 | 28vvplgz | 1 | https://waterforpeople.s3.amazonaws.com/images/9739b48b-d514-472f-9f5d-252904647bf3.jpg | 2012 | Normal | No |  |  |  | No | Broken Water Point | Poor |  | 68d4d452cbc53d687df0f23bcb396bbe
xbqq-h79e-522e | 1 |  | J7 Rw15 | 1200180299 | 09-03-2017 07:15:41 CET | Mukakarangwa Assoumpta | 00:08:43 | 2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Kabakene |  |  | kirikumuryango network |  |  | 99 | 99 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | Yes | kabagabaga | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.890964101428984 | 29.96253245751114 | 1431.2 | 2evb1yll | 1 | https://waterforpeople.s3.amazonaws.com/images/ead2cdcf-a7a2-405a-b49d-81fcfdc6d92e.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 70fa31511a3aa7737ce09dd66c27
qhts-w6ut-agbx | 1 |  | J7 Rw10 | 1245400350 | 22-03-2017 14:35:13 CET | Tuyisenge Vianney | 00:02:52 | 2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point/AEP Kigarama gravity | 2621 |  | 243 | 243 | 0 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | This is one of water points located in grouped area Kigarama village.It is normally operational and functional | 1 | Spring | -1.7875070118422336 | 29.92431620181639 | 2051.7 | 2a47b9m3 |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7751605390222898 | 29.931869045120123 | 1785.9 | 29jsmd6e | 2 | https://waterforpeople.s3.amazonaws.com/images/00987daf-abf1-4214-8b48-c50185d390f5.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | This is one of water points located in grouped area Kigarama village.It is normally operational and functional | 6d6729e664cdc2ca09e45912fbf7647
un5j-va76-cqyd | 1 |  | J7 Rw10 | 1314550454 | 20-04-2017 08:25:40 CEST | Tuyisenge Vianney | 00:06:45 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Rusura |  |  | Water point chez Senzoga/Nyirambuga pumping | 30604 |  | 157 | 157 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | Yes | 1 | -1.6843876360100896 | 29.94527936356322 | 1934.1 | 25dntbng | https://waterforpeople.s3.amazonaws.com/images/7385163a-f974-43cd-8899-a99dc5c95d7c.jpg | 2017 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6819748370716483 | 29.945844331139284 | 1852.7 | 259obuv6 | 2 | https://waterforpeople.s3.amazonaws.com/images/92012f35-a25e-40a7-97a4-2f1cbb9c6957.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | operational | a0a2aed2abda7ca66e8c3eac8f9654
dftw-t5ru-9fuc | 1 |  | J7 Rw23 | 1202340683 | 09-03-2017 08:43:37 CET | Rugirangoga Augustin | 00:27:59 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 1458 |  | 77 | 70 | 7 | Yes | Piped Network -- Gravity Only |  | 2005 | No |  |  | This Systems Functions well | 1 | Spring | -1.6426625760859115 | 29.882931577022582 | 1948.1 | 23gnwvd9 |  | Yes | 60 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2005 | Normal | 60 | Yes | 1 |  | 2005 | Normal | 4500 | Yes | 1 | -1.6504806794707938 | 29.88290457979722 | 1745.4 | 23tlhufh |  | 2005 | Normal | Yes | 2 | Pressure Break Tank |  | 2016 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.650395144365332 | 29.882824355326047 | 626.3 | 23tg4xzg | 2 |  | 2017 | Normal | No |  |  |  | Yes |  | Poor | System is working but some parts were destroyed when the people are digging in their farms | 1b1d5e99525d882d227d3d40b0bff7e5
mtc6-0v7j-17us | 1 |  | J7 Rw7 | 1445940113 | 04-06-2017 13:33:21 CEST | Rugirangoga Augustin | 00:19:10 | 2017 | Rwanda | Rulindo | Kisaro | Murama | Mugomero |  |  | gahama | 10234 |  | 129 | 100 | 29 | Yes | Piped Network with Pump |  | 2012 | Yes | ruberano gatete mugomero gishinge nyakarekare kibingwe | waterforpeople |  | 2 | Spring | -1.6675834297797398 | 30.0428712210569 | 1965.7 | 24lvl43w |  | Yes | 15 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 15 | Yes | 2 |  | 2012 | Normal | 12000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 | Pressure Break Tank¦Distribution Chamber¦washout,air release |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 12000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6345967571242568 | 30.04016071492577 | 2130.3 | 233bg3e9 | 1 | https://waterforpeople.s3.amazonaws.com/images/03b13cbf-29de-412b-bea5-dea76ce95c28.jpg | 2012 | Normal | No |  |  |  | No | amazi ni make kuburyo ataboneka buri munsi | Normal | ntabwo amazi akunda kuboneka. bavoma kabiri mu cyumweru | cac8722aa63368c8d252d22665ee68
835q-4udt-hw5w | 1 |  | J7 Rw26 | 1199000814 | 01-01-2015 20:07:39 CET | Byukusenge Elie | 00:10:22 | 2017 | Rwanda | Rulindo | Cyungo | Rwili | Kivumu |  |  | Sakara |  |  | 570 | 520 | 50 | Yes | Piped Network with Pump |  | 2015 | Yes | Kivumu Nturo Nyabisasa and Sakara | Governement (District, WASAC) and Water For People | it has source Nyamagana shared with Nyamagana gravity and it was constructed in 2015 and the extensions in Kivumu and Nyabisasa villages was constructed in 2016 and it is not yet used by the community and the pumping station use main distribution reservoir of Nyamagana gravity as the suction reservoir | 2 | Spring | -1.5919947371749814 | 29.923957502559304 | 2015.8 | 214v5hgn |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1200 | Yes | 2 | -1.6031327757439937 | 29.922709284118525 | 2131.4 | 21naedcr |  | 2016 | Normal | Yes | 5 | Distribution Chamber |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 2300 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.5966863773670548 | 29.928912459382538 | 2107.3 | 21cmds7t | 4 | https://waterforpeople.s3.amazonaws.com/images/ed6abb3b-c2d2-494d-aedd-97e098742414.jpg | 2016 | Normal | No |  |  |  | No | it is the new water tap and It is not yet used by the community. | Normal | This is the extensions in Kivumu village and it is not yet finished. | 465c47d9670c994a843ff79ca01afd
4mf9-60mk-ya9s | 1 |  | J7 Rw19 | 1255850076 | 28-03-2017 11:46:35 CEST | Kayinamura Innocent | 00:08:48 | 2017 | Rwanda | Rulindo | Ngoma | Mugote | Rukoma |  |  | Kararama pumping network | 6572 |  | 92 | 47 | 45 | Yes | Piped Network with Pump |  | 2007 | Yes | Riryi,nyakibyeyi,marembo,ngabitsinze, musenyi,munoga,remera,nyagisozi,rwamiko,kiziba,kisigiro,gacyamo,muhondo | Government |  | 4 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | No | 6 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring¦Collection chamber | 2007 | Normal | 6 | Yes | 1 |  | 2007 | Normal | 1500 | Yes | 25 | -1.7543004341479447 | 29.99197561543003 | 2178 | 28lao5qn |  | 2007 | Normal | Yes | 20 | Distribution Chamber¦Washout and Air release chamber |  | 2007 | Normal | Yes | 4 |  | 2007 | Poor | 30000 | Yes | 2 |  | 2007 | Poor | Yes |  | 2007 | Poor | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7960521377610468 | 30.00298249018891 | 2112.4 | 2aiccwfx | 47 | https://waterforpeople.s3.amazonaws.com/images/6cec32e8-5043-4d7a-8268-88e8896dcd8d.jpg | 2007 | Does Not Function | No |  |  |  | No | this water do not have water today because water don't reach this water point | Does Not Function | 1.the system has two pumps but only one is functioning 2.The source and the pumping station are under total rehabilitation 3. Water points located in Ngoma sector do not have water 4.this network serves Ngoma, cyinzuzi and Ntarabana sectors | da64b9ed891524aeef7c3d194f2c4
3hqh-nwh8-1kgk | 1 |  | J7 Rw10 | 1232070305 | 02-01-2015 23:58:46 CET | Tuyisenge Vianney | 00:08:11 | 2017 | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point behind Gisha center/Nyirambuga pumping | 30604 |  | 133 | 133 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | At water point behind Gisha center,water is available but the water point after being maintained people are no longer using it | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.741608354195878 | 29.966107962721438 | 2047.3 | 280ajn9p | 2 | https://waterforpeople.s3.amazonaws.com/images/92853c2b-a1d8-4337-8aa6-793c4931b800.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | At water point behind Gisha center,water is available but the water point after being maintained people are no longer using it | 5d8b3722d0d1218980db538579ce6bf
4vfy-afqu-kh0x | 1 |  | J7 Rw10 | 1240510060 | 02-01-2015 12:18:26 CET | Tuyisenge Vianney | 00:06:15 | 2017 | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at Buyoga secondary school/Nyirambuga pumping | 30604 |  | 177 | 177 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point at Buyoga secondary school.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6948660521972871 | 30.01248810081209 | 2097.2 | 25uzrm58 | 6 | https://waterforpeople.s3.amazonaws.com/images/f84a2338-b9dd-4753-8466-ecd82c5efff0.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point at Buyoga secondary school.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water | 12cd5b2698cec97e11d45a27e7c96e8
rsh6-5u0n-6jsd | 1 |  | J7 Rw10 | 1240510062 | 02-01-2015 12:06:16 CET | Tuyisenge Vianney | 00:09:11 | 2017 | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at Buyoga Health Center/Nyirambuga pumping | 30604 |  | 177 | 177 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Buyoga Health center water point operates well.However the common problem that is on Buyoga side of Nyirambuga pumping is that water reaches the system rarely | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 0 | -1.6942090317849903 | 30.012588095258174 | 2069.1 | 25twh07x | https://waterforpeople.s3.amazonaws.com/images/f1c89b0a-0f26-4046-ad28-d2de24a86854.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6942090317849903 | 30.012588095258174 | 2069.1 | 25twh07x | 6 |  | 2015 | Normal | No |  |  |  | Yes |  | Normal | Buyoga Health center water point operates well.However the common problem that is on Buyoga side of Nyirambuga pumping is that water reaches the system rarely.The water point geolocation coordinates and pboto are mistakenly put on water storage tank. | 64dbf5f4b01ccd17f656e4ccb7e0fad3
urda-cmda-h28m | 1 |  | J7 Rw23 | 1226490107 | 15-03-2017 06:05:10 CET | Rugirangoga Augustin | 00:29:29 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Bukangano |  |  | Migogo | 558 |  | 129 | 120 | 9 | Yes | Piped Network -- Gravity Only |  | 2009 | Yes | kiruli bukangano kabahama Rubanda | Padiri | this network works partialy | 1 | Groundwater (well, etc.) | -1.6327309674421784 | 29.901262305566668 | 1800.8 | 2308pft0 | https://waterforpeople.s3.amazonaws.com/images/9cd2a731-b352-45ae-8811-58a5b9adbf93.jpg | No | 50 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/47794007-714c-4c00-bc25-d8ed5362ec2f.jpg | "Springbox" --Intake Structure at a Spring | 2009 | Normal | 50 | Yes | 1 |  | 2009 | Poor | 6800 | Yes | 3 | -1.6327309674421784 | 29.901262305566668 | 1900.3 | 2308pft0 |  | 2009 | Poor | No | [5 empty] | Yes | 1 |  | 2009 | Poor | 6800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6506264011739427 | 29.930864094865832 | 1806 | 23tttx9o | 2 | https://waterforpeople.s3.amazonaws.com/images/0865daaa-41be-4ef0-8a7f-c8f650e9156f.jpg | 2016 | Normal | No |  |  |  | Yes |  | Poor | this network needs rehabilitation | 3fd51c355194331e7df39016437a8f
upde-y2cp-g4r7 | 1 |  | J7 Rw26 | 1193921160 | 07-03-2017 13:11:12 CET | Byukusenge Elie | 00:11:58 | 2017 | Rwanda | Rulindo | Cyungo | Marembo | Murambo |  |  | Mugomero Marembo | 3456 |  | 161 | 150 | 11 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | Gahinga, Nganzo, Rusayu, Buyaga and Murambo | Governement (District, WASAC) and Water For People | The source of this network is located in Burera District and This network serves three villages in Burera and iy has eight water taps ,starting chamber and reservoirs in Burera and this network needs extentions to supply two villages (Kidomo and Kibuye) which do not have network | 1 | Spring | -1.5777496463341437 | 29.93714072556937 | 2147.8 | 20haqsiz |  | Yes | 120 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 120 | Yes | 2 |  | 2015 | Normal | 10000 | Yes | 10 | -1.5961706844323926 | 29.912557085345822 | 2085.4 | 21bs0o8l |  | 2015 | Normal | Yes | 3 | Distribution Chamber |  | 2015 | Normal | Yes | 2 |  | 2015 | Normal | 10000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6229365041411323 | 29.90932725945568 | 2026.9 | 22k18n11 | 1 | https://waterforpeople.s3.amazonaws.com/images/3b3578e6-be1f-42f7-8629-fc669cf0f701.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is in good condition and it doesn't used by the community because they prefer to use the spring water and rain water from health Center reservoir. | 6dafb8b0671bf450eaf59a667bd7a29
tffc-krbk-07ty | 1 |  | J7 Rw19 | 1327061895 | 22-04-2017 12:29:35 CEST | Kayinamura Innocent | 00:10:40 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Amahoro |  |  | Nyakagezi | 26296 |  | 120 | 43 | 77 | Yes | Piped Network -- Gravity Only |  | 2017 | No |  | Governement (District, WASAC) and Water For People | This water point is under construction | 1 | Spring | -1.7765195993909377 | 30.040143936092534 | 1670.1 | 29m0zwoh | https://waterforpeople.s3.amazonaws.com/images/3a6dbb98-42e9-4fb3-95c7-b9846bf32f6e.jpg | Yes | 38 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/3bdae5d3-8555-428f-bc53-83ad510bc33b.jpg | "Springbox" --Intake Structure at a Spring | 2017 | Poor | 38 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.776302056356461 | 30.040303983660248 | 1642.5 | 29lohsz7 | 2 | https://waterforpeople.s3.amazonaws.com/images/a5663f7b-6e99-404d-90e4-531f2296d26f.jpg | 2017 | Does Not Function | No |  |  |  | No | This network is under construction | Does Not Function |  | b3f4efc7ba8b26bb99e46b929cf276e
x1m3-mv2e-yhyh | 1 |  | J7 Rw23 | 1243590253 | 23-03-2017 06:27:56 CET | Rugirangoga Augustin | 00:26:33 | 2017 | Rwanda | Rulindo | Kisaro | Sayo | Rugarama |  |  | Kiruruma | 8295 |  | 109 | 101 | 8 | Yes | Piped Network with Pump |  | 2014 | Yes | rutabo gitaba nyarubuye remera rusongati rugarama cyasuli munini | Governement (District, WASAC) and Water For People | The network is operating without problem | 1 | Groundwater (well, etc.) | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 15 | -1.6684773741137722 | 30.047381335897573 | 1775.8 | 24nckozd |  | 2014 | Normal | Yes | 5 | Pressure Break Tank |  | 2014 | Normal | Yes | 3 |  | 2014 | Normal | 4000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6696865091835438 | 30.018426230985952 | 2085.7 | 24pcm4yg | 2 | https://waterforpeople.s3.amazonaws.com/images/d3537bd0-9c57-4d2c-9905-7e728e895b71.jpg | 2014 | Does Not Function | No |  |  |  | Yes |  | Poor | the network has no problem | 4e36e9ceb240aea3c45867ea98cdf0ba
rv5x-4ef3-wu37 | 1 |  | J7 Rw23 | 1248440061 | 25-03-2017 20:47:24 CET | Rugirangoga Augustin | 00:23:43 | 2017 | Rwanda | Rulindo | Buyoga | Butare | Giko |  |  | Kiduha-muyanza | 0 |  | 115 | 100 | 15 | Yes | Piped Network -- Gravity Only |  | 2007 | No |  | Italians(LAKE ANGELS) | kubitaro bya Muyanza ntabwo bafite amazi ahagije(information given by Director of health center that pressure they get is not sufficient. | 1 | Spring | -1.692136727874054 | 30.02146392212493 | 1866.9 | 25qh8a2e | https://waterforpeople.s3.amazonaws.com/images/06cd4575-59af-400b-b586-9ed42f93808e.jpg | No | 20 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/7d20d498-f86e-4f09-811d-880afc880ebb.jpg | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 20 | Yes | 1 |  | 2014 | Normal | 2200 | Yes | 3 | -1.6932117321635163 | 30.026191374639453 | 1765.8 | 25s9j3fp |  | 2007 | Poor | No | [5 empty] | Yes | 1 |  | 2007 | Poor | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6923655969341922 | 30.022065301971406 | 1825.7 | 25qux8zg | 1 | https://waterforpeople.s3.amazonaws.com/images/93a97e00-d981-494f-a0e8-49dd935b416d.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | Ibigega by'uyu muyoboro birava | aa2c5e0aa9bd062931c247934e136d1
mbv9-h6fn-qy9p | 1 |  | J7 Rw7 | 1446800068 | 04-06-2017 13:25:17 CEST | Rugirangoga Augustin | 00:25:37 | 2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Kabeza |  |  | gahama | 10234 |  | 92 | 80 | 12 | Yes | Piped Network with Pump |  | 2012 | No |  | gouverment | iri vomo ntabwo rifite amaZi ahagije | 1 | Spring | -1.6675834297797398 | 30.0428712210569 | 1965.7 | 24lvl43w |  | Yes | 45 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 65 | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 | Pressure Break Tank¦Distribution Chamber¦washout,air release |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6148837602477844 | 30.040840082323438 | 2032.1 | 226pyq2g | 1 | https://waterforpeople.s3.amazonaws.com/images/c07831d7-4d11-4c94-8705-45f6f8cf17dd.jpg | 2012 | Poor | No |  |  |  | Yes |  | Normal | nta | 19e54e774fc8619d74c3ff9786c1ca3
a15h-q098-tepm | 1 |  | J7 Rw23 | 1208950863 | 11-03-2017 20:03:15 CET | Rugirangoga Augustin | 00:26:53 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Cyondo |  |  | Ruramba | 1564 |  | 173 | 140 | 33 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | this network is affected by the construction project of the road | 1 | Spring | -1.612504606727932 | 29.86882944818841 | 1922.4 | 222s9irk | https://waterforpeople.s3.amazonaws.com/images/089bfa7d-4335-4837-ae69-a26f657cc231.jpg | Yes | 60 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/2dfe7366-e039-40a4-855e-ad42dc7632a4.jpg | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 60 | Yes | 1 |  | 2016 | Normal | 4500 | Yes | 2 | -1.6213170406640873 | 29.869799421143036 | 1873.1 | 22hcseq1 |  | 2016 | Normal | Yes | 2 | Sedimentation Tank |  | 2016 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6126446085984363 | 29.868788932561944 | 1919.9 | 2230ll8f | 1 | https://waterforpeople.s3.amazonaws.com/images/77dea4a6-eb6e-42c7-b92a-35d5a35c4de2.jpg | 2016 | Poor | No |  |  |  | Yes |  | Poor | they have destroyed this water tap but it is not totaly destroyed.it works | c2c1de7e63e53ec14fafc68544a87073
gt12-p72s-jvx1 | 1 |  | J7 Rw7 | 1437160355 | 06-06-2017 15:05:12 CEST | Rugirangoga Augustin | 00:31:32 | 2017 | Rwanda | Rulindo | Kisaro | Gitatsa | Ndago |  |  | gahama | 10234 |  | 148 | 40 | 108 | Yes | Piped Network -- Gravity Only |  | 2012 | Yes | ruberarano gishinge kibingwe mugomero rusongati | waterfor people | uyu muyuboro ntabwo amazi yawo ahagije | 2 | Spring | -1.6675834297797398 | 30.0428712210569 | 1965.7 | 24lvl43w |  | Yes | 65 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 50 | No | [5 empty] | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 | Sedimentation Tank |  | 1998 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6631529193417967 | 30.04727443578637 | 1734.8 | 24eju35k | 1998 | https://waterforpeople.s3.amazonaws.com/images/26d3aa61-fff7-4385-a1d2-ad4737aede42.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | uyu muyoboro urakora ni mushya | 7f734c33ff293f6cc5c41fbf2b845e
6d4c-c46j-m6v | 1 |  | J7 Rw19 | 1242190053 | 24-03-2017 04:42:10 CET | Kayinamura Innocent | 00:07:22 | 2017 | Rwanda | Rulindo | Masoro | Kivugiza | Rebero |  |  | Mutagata motorised network | 26296 |  | 376 | 138 | 238 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7870592625325574 | 30.06787834580483 | 1704.9 | 2a3gishy | 64 | https://waterforpeople.s3.amazonaws.com/images/ed7dc5ba-a162-4154-8b69-7084a99e3951.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | a86966feef79ea1742510c4dc99cc49
p2gn-80n8-tj5y | 1 |  | J7 Rw10 | 1277880055 | 05-04-2017 21:11:44 CEST | Tuyisenge Vianney | 00:05:55 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Ngarama |  |  | Nyirangarama water point/Rutare-Nyirangarama gravity system | 726 |  | 89 | 89 | 0 | Yes | Piped Network -- Gravity Only |  | 1960 | No |  | Government of Rwanda | Though the water point at Nyirangarama village operates,its infrastructure needs to be reconstructed | 1 | Spring | -1.6705676828047722 | 29.878696276428556 | 2067 | 24qt0942 |  | Yes | 20 | No | [5 empty] | 20 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6662632345897406 | 29.885490477241813 | 1840.4 | 24jozv1i | 1 | https://waterforpeople.s3.amazonaws.com/images/31aec1b6-120e-4e78-800f-6b9641f349e6.jpg | 1960 | Poor | No |  |  |  | Yes |  | Poor | Though the water point at Nyirangarama village operates,its infrastructure needs to be reconstructed | fa37f0c75430d4341c4cb3b8506727
jua8-cdbb-3q9u | 1 |  | J7 Rw10 | 1218280445 | 14-03-2017 22:25:46 CET | Tuyisenge Vianney | 00:12:10 | 2017 | Rwanda | Rulindo | Rusiga | Kirenge | Rebero |  |  | Gashinge source/Gashinge gravity |  |  | 181 | 181 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Government | The water source is well captured | 1 | Spring | -1.778040825436737 | 29.922360289445436 | 2013.8 | 29ok37br | https://waterforpeople.s3.amazonaws.com/images/b033b817-85ac-419d-94d4-59ac80fb85db.jpg | No | 60 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/1b44db65-3e44-4a8e-a94c-f955c8e0d533.jpg | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 60 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/34dc745d-1f3d-4c50-98fb-d68f095611e6.jpg | 2015 | Normal | 800 | Yes | 1 | -1.7773799213895622 | 29.92560170300912 | 1894.2 | 29ng75tk | https://waterforpeople.s3.amazonaws.com/images/96f170b3-208c-4382-9705-152c941ca02d.jpg | 2013 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7781078804730488 | 29.922533869418384 | 2079.7 | 29onnsyh | 1 | https://waterforpeople.s3.amazonaws.com/images/96c2e439-3714-4ce4-8f43-5924abdcbca3.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | The water source operates well and its water points as well as storage tanks function well | aa1aa2a7160840d43e87c7693adfb9
t4ck-a6pn-cx06 | 1 |  | J7 Rw10 | 1225570122 | 15-03-2017 19:29:22 CET | Tuyisenge Vianney | 00:04:25 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Wpt at Murambi Central Catholic Church/Nyirambuga pumping | 30604 |  | 174 | 174 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | GoR | Murambi central catholic church water point/Nyirambuga pumping operates well though tap valves are not fixed | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6833514684945 | 29.928798094274256 | 1992.8 | 25byho7r | 1 | https://waterforpeople.s3.amazonaws.com/images/2117b142-32b3-4e3f-b046-de49c8cec83e.jpg | 2012 | Normal | No |  |  |  | Yes |  | Poor | Murambi central catholic church water point/Nyirambuga pumping operates well though tap valves are not fixed | 4d9e3f6d5e843cf6d9f9099982c34c
nn3y-r6kq-gvw3 | 1 |  | J7 Rw10 | 1300340103 | 16-04-2017 22:24:06 CEST | Tuyisenge Vianney | 00:10:58 | 2017 | Rwanda | Rulindo | Base | Gitare | Rugerero |  |  | Water point at Gasana/Nyirambuga pumping system | 30604 |  | 143 | 143 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Water point chez Gasana currently is not operating due to the pipeline that got broken while constructing road.They last saw water in last December.They water storage tank while having water does not store for more than 2 days.It is guessed it leakes with high intensity of infiltration | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.6683182824360163 | 29.909632188967205 | 2015.8 | 24n31q8o | https://waterforpeople.s3.amazonaws.com/images/a461f60a-d618-4388-91fc-1efc89c003eb.jpg | 2012 | Poor | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6680297890703109 | 29.909957252469262 | 2026 | 24mls5p7 | 2 | https://waterforpeople.s3.amazonaws.com/images/331dae15-5e44-4302-a78b-1e603773c76a.jpg | 2012 | Does Not Function | No |  |  |  | No | Water point chez Gasana currently is not operating due to the pipeline that got broken while constructing road.They last saw water in last December.They water storage tank while having water does not store for more than 2 days.It is guessed it leakes with high intensity of infiltration | Does Not Function | Water point chez Gasana currently is not operating due to the pipeline that got broken while constructing road.They last saw water in last December.They water storage tank while having water does not store for more than 2 days.It is guessed it leakes with high intensity of infiltration | 14f6e92e7f07d7ca55789d924428d2e
xnf5-t1ky-32wr | 1 |  | J7 Rw19 | 1242190052 | 23-03-2017 18:43:30 CET | Kayinamura Innocent | 00:36:07 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Nyarurembo |  |  | Mutagata motorised network | 26296 |  | 144 | 40 | 104 | Yes | Piped Network -- Gravity Only |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.796844299728253 | 30.023242366198367 | 2125.2 | 2ajne5e0 |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7951634963141672 | 30.038867842640506 | 1997.7 | 2agvdbvo | 64 | https://waterforpeople.s3.amazonaws.com/images/4e652bd7-f6ae-4543-9234-e928abbd5324.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | ad8490ab44838725bac81ac313992a
6cga-j6jm-qn7e | 1 |  | J7 Rw24 | 1223450520 | 16-03-2017 08:59:49 CET | Kabalisa Manzi Christella | 00:07:28 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Rugaragara |  |  | charity water 203.207 | 6572 |  | 815 | 815 | 0 | Yes | Piped Network with Pump |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8024532750946713 | 30.042616473975034 | 1748.3 | 2asxebwq |  | Yes | 3 | Yes | 1 |  |  | 2016 | Normal | 3 | Yes | 1 |  | 2016 | Normal | 35000 | Yes | 2 | -1.7575350016834248 | 30.02449548695202 | 1874.2 | 28qmz6dw |  | 2016 | Normal | Yes | 2 |  |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 1000 | Yes | 3 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7765234253882805 | 30.027301664842398 | 1999.1 | 29m1lc6p | 1 | https://waterforpeople.s3.amazonaws.com/images/29d108f1-c9e8-4e39-91cd-f379551b3844.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 2b69b9cf721918b4ec2966cdf83191
8e54-17xe-tp4 | 1 |  | J7 Rw26 | 1202890095 | 02-01-2015 05:50:45 CET | Byukusenge Elie | 00:10:34 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Gihemba |  |  | Nyamagana | 20456 |  | 85 | 75 | 10 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6282030479714942 | 29.927155502831905 | 1804.4 | 22sr02yv | 29 | https://waterforpeople.s3.amazonaws.com/images/67be72f7-e275-49df-9929-33d9d65f18f3.jpg | 2011 | Normal | Yes | 10 | 30 | The distribution reservoir does not supply water in this transmission line network | Yes |  | Poor |  | f145b02ad99a6bd63a64595daaaff67c
tnhb-mem5-phya | 1 |  | J7 Rw26 | 1203950149 | 02-01-2015 05:52:28 CET | Byukusenge Elie | 00:07:09 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Gihemba |  |  | Nyamagana | 20456 |  | 75 | 60 | 15 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Poor | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6347501449933435 | 29.92881918030919 | 1775.7 | 233kz07s | 29 | https://waterforpeople.s3.amazonaws.com/images/8bb5e712-af83-494d-a56c-a8bb922c4836.jpg | 2011 | Normal | No |  |  |  | Yes |  | Poor | Water are available at centre Gitovu | b4417c65d37dcf3c1caa1524f46953d6
q7jb-rvhk-thc8 | 1 |  | J7 Rw8 | 1244550686 | 23-03-2017 11:36:36 CET | Amani Desire | 00:09:33 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Rukurazo |  |  | Mutagata Gravity Network | 26296 |  | 247 | 107 | 140 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | Ruri,musenga,umubuga,amataba,rusine,marenge |  |  | 1 | Groundwater (well, etc.) | -1.8023389079852206 | 30.042447389592418 | 1691.2 | 2asq94nc |  | Yes | 8 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2004 | Poor | 8 | Yes | 1 |  | 2004 | Poor | 3500 | Yes | 6 | -1.8078446763653504 | 30.066649761552014 | 1669.8 | 2b1uaz5m |  | 2004 | Poor | Yes | 4 | Distribution Chamber¦washout and Air release chamber |  | 2004 | Poor | Yes | 2 |  | 2004 | Poor | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8214416696711182 | 30.074271539487835 | 1586.8 | 2boc0hxi | 12 | https://waterforpeople.s3.amazonaws.com/images/b9909ee7-6135-414b-b9cb-bc87726ff5ec.jpg | 2007 | Poor | No |  |  |  | Yes |  | Poor | 1.the extension to nyabinyana village has 2 reservoirs and two water points which is under construction 2.this system have been constructed in 2004 3.it serves a part of Masoro sector and parts is located in Gasabo district 4. 2 water points and one reservoir have been constructed in 2016 5.in general this network has 27 water points in wich 12 are in Rulindo district and others are in Gasbo district | 5203a744bcd0b65d4b28e252db4415
nsyd-h6ew-89xr | 1 |  | J7 Rw23 | 1200042867 | 24-03-2017 15:50:35 CET | Rugirangoga Augustin | 00:49:28 | 2017 | Rwanda | Rulindo | Buyoga | Butare | Karambi |  |  | Nyagahera |  |  | 107 | 100 | 7 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | kankanga karambi ryanyirakayobe | Governement (District, WASAC) and Water For People | this network has no problem | 1 | Groundwater (well, etc.) | -1.9477961957998693 | 30.39250392332349 | 1576 | 2hhakgs5 |  | Yes | 16 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2017 | Poor | 16 | Yes | 1 |  | 2014 | Normal | 6800 | Yes | 3 | -1.6902852583901373 | 30.034148165390133 | 1811.3 | 25nf3391 |  | 2014 | Normal | Yes | 3 | Distribution Chamber |  | 2014 | Normal | Yes | 1 |  | 2014 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7081612084231181 | 30.01626442011942 | 1649 | 26gzm4qq | 1 | https://waterforpeople.s3.amazonaws.com/images/1b290f4e-59c6-45f8-b1ef-ec8093f66cc1.jpg | 2014 | Poor | No |  |  |  | Yes |  | Normal | System has not enough water needs to be increased | 856fe334a352f11fc15a73575d53eb
ubmr-kcq6-0jyb | 1 |  | J7 Rw8 | 1235340219 | 23-03-2017 07:54:12 CET | Amani Desire | 00:10:42 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Ruri |  |  | Mutagata Motorised Network | 26296 |  | 189 | 70 | 119 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8134767967970127 | 30.042089548151356 | 1845.3 | 2bb5i0jo | 64 | https://waterforpeople.s3.amazonaws.com/images/f017e56b-3c8d-414a-859b-0cbba9b254aa.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | fefcc9edfe93ddc389d227b421c98f
yqmk-1rkb-59dq | 1 |  | J7 Rw26 | 1192950858 | 07-03-2017 11:02:40 CET | Byukusenge Elie | 00:09:32 | 2017 | Rwanda | Rulindo | Cyungo | Marembo | Gahinga |  |  | Mugomero Murambo | 3456 |  | 652 | 602 | 50 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | Kidomo, Gahinga, Nganzo,Rusayo, Buyaga and Murambo | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.577496463341437 | 29.93714072556937 | 2147.8 | 20gvuyej |  | Yes | 120 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 120 | Yes | 2 |  | 2015 | Normal | 10000 | Yes | 10 | -1.5961706844323926 | 29.91257085345822 | 2085.4 | 21bs0o8l |  | 2015 | Normal | Yes | 3 | Distribution Chamber |  | 2015 | Normal | Yes | 2 |  | 2015 | Normal | 10000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.609046302103302 | 29.914217190554265 | 2035.4 | 21x29jt2 | 8 | https://waterforpeople.s3.amazonaws.com/images/40fdc187-6fc4-42be-84f8-a0b4e3a94110.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is in good condition but the users are located fall away of the water tap. | 316cff7ab4c7a643e8295eac7d97d4e
wu9a-58h1-p2pu | 1 |  | J7 Rw15 | 1199330227 | 08-03-2017 19:19:50 CET | Mukakarangwa Assoumpta | 00:12:06 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gisiza |  |  | kinywamagana pumping network | 6436 |  | 212 | 60 | 152 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.852064062747735 | 29.984059608173418 | 1793.4 | 2d2z1rk0 | 1 | https://waterforpeople.s3.amazonaws.com/images/8ba8ef52-9bfd-415c-87d7-5007c8378545.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | water does not reach thi water point because is not well located | 5cb3f1eebdaac18fbe33d1bfe8628f
6dx0-rqg9-nvcj | 1 |  | J7 Rw7 | 1243160052 | 24-03-2017 13:04:21 CET | Safari Bosco | 00:11:40 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo | [5 empty] | 203 | 203 | 0 | Yes | Piped Network with Pump |  | 1998 | No |  | Governement (District, WASAC) and Water For People | This Systems Functions well with 21 taps all functional | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8265117201749177 | 30.05594541357459 | 1859.8 | 2bwpv9hr | 1 | https://waterforpeople.s3.amazonaws.com/images/6f4a310a-d35e-4dcf-b1ba-6a526c2c4636.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 56b0a4f6d3d773fb754a8ebcc27874c1
jyv4-gcu5-ybt2 | 1 |  | J7 Rw23 | 1212340601 | 15-03-2017 05:14:33 CET | Rugirangoga Augustin | 00:28:03 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 1789 |  | 192 | 180 | 12 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | karambi gitovu | Padiri gitovu | good | 4 | Spring¦Groundwater (well, etc.) | -1.6128815953757245 | 29.8745655017548616 | 1956.1 | 223evzsp |  | Yes | 45 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 30 | Yes | 1 |  | 2016 | Normal | 6450 | Yes | 2 | -1.6111677762752643 | 29.8839135826884 | 1852 | 220khftj |  | 2012 | Normal | Yes | 2 | Distribution Chamber |  | 2016 | Normal | Yes | 1 |  | 2012 | Normal | 6450 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6096814645633895 | 29.88585037221405 | 1605.7 | 21y4daay | 2 | https://waterforpeople.s3.amazonaws.com/images/1dcb9cfa-9c38-4125-a4c6-756941566a11.jpg | 2017 | Does Not Function | No |  |  |  | Yes |  | Poor | the water tap does not work because it is just being built by this moment.it is new | 673cd773e9ad30fc5014e98815fd35c3
7ybg-871j-nb7d | 1 |  | J7 Rw24 | 1322090056 | 25-04-2017 00:31:08 CEST | Kabalisa Manzi Christella | 00:12:17 | 2017 | Rwanda | Rulindo | Kisaro | Murama | Ryarubuguza |  |  | Gahama Kisaro network | 10234 |  | 99 | 99 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Government |  | 1 | Spring | -1.6671501074688961 | 30.041830412153367 | 1945.4 | 24l5zh36 |  | Yes | 3 | Yes | 1 |  |  | 2012 | Normal | 3 | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 |  |  | 2012 | Normal | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6108176309070168 | 30.026458923676124 | 2009.8 | 21zznaqw | 1 | https://waterforpeople.s3.amazonaws.com/images/b6cc81f3-8a02-4b4f-98ba-1d70c1054690.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal |  | e8d9837c2ce23e2bc7bd401aade681fa
tq0d-s4g2-yxu7 | 1 |  | J7 Rw23 | 1219420187 | 12-03-2017 18:39:52 CET | Rugirangoga Augustin | 00:47:55 | 2017 | Rwanda | Rulindo | Base | Gitare | Kirwa |  |  | Rwicanyoni | 698 |  | 136 | 100 | 36 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | kirwa gatete gisiza | Governement (District, WASAC) and Water For People | this network works well | 2 | Groundwater (well, etc.) | -1.6644377224987001 | 29.903649586570488 | 1928 | 24go1jh8 | https://waterforpeople.s3.amazonaws.com/images/d415a335-bb1e-4e3a-8848-06118091bf43.jpg | Yes | 10 | Yes | 2 |  | start chamber | 2016 | Normal | 10 | No | [5 empty] | Yes | 3 | -1.66051945904779042 | 29.90927074216649 | 1808.8 | 24a6nmdw |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6641512303055974 | 29.9039151713755 | 1956.4 | 24g7dejj | 2 | https://waterforpeople.s3.amazonaws.com/images/f3e32fbb-5c51-4e0e-aeb9-8a24c4dfa69c.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | no problem | 657ffa749d4edfaff78dfd568372ccf
hyn4-6n92-nptp | 1 |  | J7 Rw26 | 1230030687 | 21-03-2017 13:53:45 CET | Byukusenge Elie | 00:05:02 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Kabingo |  |  | Kabonanyoni | 7894 |  | 40 | 40 | 0 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 19000 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.64093797813412 | 29.966856619244787 | 2012 | 23dswwd0 | 31 | https://waterforpeople.s3.amazonaws.com/images/5ea66a39-1a09-4b82-9a77-8e1e53e6a5ad.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | 23e657736734acb71d7f8849a1c24b42
fdgb-vg3k-qet8 | 1 |  | J7 Rw8 | 1236140729 | 23-03-2017 11:40:45 CET | Amani Desire | 00:12:02 | 2017 | Rwanda | Rulindo | Masoro | Shengampuri | Amataba |  |  | Mutagata Gravity Network | 26296 |  | 178 | 60 | 118 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | Ruri,musenga,umubuga,amataba,rusine,marenge |  |  | 1 | Spring | -1.80233890798552206 | 30.042447389592418 | 1691.2 | 2asq94nc |  | Yes | 8 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2004 | Poor | 8 | Yes | 1 |  | 2004 | Poor | 3500 | Yes | 6 | -1.8078446763653504 | 30.066649761552014 | 1669.8 | 2b1uaz5m |  | 2004 | Poor | Yes | 4 | Distribution Chamber¦washout and Air release chamber |  | 2004 | Poor | Yes | 2 |  | 2004 | Poor | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8138714971026335 | 30.096224156237067 | 1454 | 2bbtbd5u | 12 | https://waterforpeople.s3.amazonaws.com/images/31a2b0db-2b5b-41c7-88f4-bd6d6bb6a48f.jpg | 2004 | Poor | No |  |  |  | Yes |  | Poor | 1.the extension to nyabinyana village has 2 reservoirs and two water points which is under construction 2.this system have been constructed in 2004 3.it serves a part of Masoro sector and parts is located in Gasabo district 4. 2 water points and one reservoir have been constructed in 2016 5.in general this network has 27 water points in wich 12 are in Rulindo district and others are in Gasbo district | d1490e6593c2be7da88d60bb44c561
s945-ybm7-6f7n | 1 |  | J7 Rw7 | 1245740105 | 24-03-2017 08:34:26 CET | Safari Bosco | 00:38:59 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 5544 |  | 214 | 214 | 0 | Yes | Piped Network with Pump |  | 1986 | No |  |  | This system has problems in the rainy season, water gets dirty | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228065710007637 | 30.055376173807932 | 1827.2 | 2bqkzg21 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.829743051670469 | 30.059042563148825 | 1771.7 | 2c2269wu | 1 | https://waterforpeople.s3.amazonaws.com/images/c6ec14f1-99ec-42b0-8e72-5204c599758c.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | In the dry season there is not enough water | cbd079e74a6238cbae397987fb4f5c86
86cx-t6sx-u0n3 | 1 |  | J7 Rw26 | 1247510144 | 03-01-2015 04:53:28 CET | Byukusenge Elie | 00:06:17 | 2017 | Rwanda | Rulindo | Rukozo | Mbuye | Mujebe |  |  | Kabonanyoni | 7894 |  | 50 | 46 | 4 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare, Kabera,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe, Kabyayi, Kabingo, Kamiyove, Murwa, Nyenyeri, Rukingu and Kivomo | Governement (District, WASAC) and Water For People | This is the New pumping system which serves the community located at the uphill, it has 5 sources, one source which is located in Miyove sector, Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro,This network has one reservoir which is not functioning, This network serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6290006651346545 | 29.95729597798981 | 2102.9 | 22u2mrlg | 31 | https://waterforpeople.s3.amazonaws.com/images/632beada-7149-40f5-99f7-91ed669a0c4e.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | 6de66dfe1275cfa2585179c28b3b4195
9tj2-6ece-1ym4 | 1 |  | J7 Rw23 | 1218620251 | 15-03-2017 08:03:07 CET | Rugirangoga Augustin | 00:16:46 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 2456 |  | 214 | 200 | 14 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | mushongi buramba | Governement (District, WASAC) and Water For People | Many water points on this system are not functional others water is not flowing | 1 | Spring | -1.6358367374763643 | 29.9135277934778 | 1996.9 | 235d9tfj |  | Yes | 15 | No | [5 empty] | 15 | Yes | 1 |  | 2016 | Poor | 7200 | Yes | 6 | -1.6498521069502532 | 29.917613599705728 | 1996.9 | 23sjzjl4 |  | 2016 | Normal | No | [5 empty] | Yes | 1 |  | 2016 | Poor | 7200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6496636447045052 | 29.909021691739117 | 1812.3 | 23s8ob0y | 2 | https://waterforpeople.s3.amazonaws.com/images/4baa31fc-86a4-4593-a0ff-2c60125dfac5.jpg | 2016 | Does Not Function | Yes | 7 | 7 | water is not enough to cover all villages | No | not enough pressure to reach the points | Does Not Function | this network does not work properly | f7147fe0c12dba16bedafa92db879edd
2gjr-uq9q-sqwk | 1 |  | J7 Rw7 | 1199093129 | 23-03-2017 10:25:30 CET | Safari Bosco | 01:25:37 | 2017 | Rwanda | Rulindo | Murambi | Mvuzo | Kabuga |  |  | rwiseke | 9536 |  | 199 | 195 | 4 | Yes | Piped Network -- Gravity Only |  | 2001 | Yes | kabuga,gatare,kigarama,taba,karwa,kigarama | Governement (District, WASAC) and Water For People | Water is not enough in the system it is thought the source might have strayed | 3 | Spring | -1.8081127252820783 | 30.019302406005654 | 1889.4 | 2b2ado4h | https://waterforpeople.s3.amazonaws.com/images/15d68678-d2ca-4425-8ef8-f29d5ace62ad.jpg | Yes | 14 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/60df2236-9173-4a67-97be-df91d237917f.jpg | "Springbox" --Intake Structure at a Spring | 2001 | Normal | 14 | Yes | 1 |  | 2001 | Normal | 1200 | Yes | 7 |  |  |  |  | https://waterforpeople.s3.amazonaws.com/images/1ba842b2-eedb-4f92-bcad-9d09a7186096.jpg | 2001 | Normal | No | [5 empty] | Yes | 1 |  | 2001 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8083673788125414 | 30.018576770492718 | 1798.1 | 2b2p9i8p | 1 | https://waterforpeople.s3.amazonaws.com/images/ffebfdb8-808e-44e4-aa70-ab223365f02a.jpg | 2001 | Poor | No |  |  |  | Yes |  | Normal | In the dry season there is not enough water and the system has 7 water points plus one at the source | b5b24fc157274e0b6b1be594f3511
6srj-g223-je30 | 1 |  | J7 Rw23 | 1236260179 | 23-03-2017 06:25:45 CET | Rugirangoga Augustin | 01:06:41 | 2017 | Rwanda | Rulindo | Buyoga | Gahororo | Bunyana |  |  | Kiruruma | 8295 |  | 108 | 102 | 6 | Yes | Piped Network with Pump |  | 2014 | Yes | rutabo gitaba nyarubuye remera rusongati rugarama cyasuli munini shagasha | Governement (District, WASAC) and Water For People |  | 1 | Groundwater (well, etc.)¦null | -1.668151432446623 | 30.04664574413683 | 1956.1 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 15 | -1.6684773741137722 | 30.047381335897573 | 1775.8 | 24nckozd |  | 2014 | Normal | Yes | 5 | Pressure Break Tank |  | 2014 | Normal | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7038929371566562 | 30.065668198264376 | 1854.4 | 269xe1tc | 2 | https://waterforpeople.s3.amazonaws.com/images/23d78809-2f36-482c-9f51-10f34ecafb83.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | the network is functioning well | 17ef673847bb0f22514313c62664217
nm2w-ub6j-vfsv | 1 |  | J7 Rw23 | 1326440072 | 23-04-2017 14:40:57 CEST | Rugirangoga Augustin | 00:16:43 | 2017 | Rwanda | Rulindo | Buyoga | Ndarage | Kimagali |  |  | kiruruma | 8295 |  | 125 | 100 | 25 | Yes | Piped Network with Pump |  | 2017 | Yes | kimagali | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 11 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2014 | Normal | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6855261230593372 | 30.036896340485978 | 2040 | 25fjorbk | 1 | https://waterforpeople.s3.amazonaws.com/images/f147a542-ab65-4423-a4d2-7c6292c6202e.jpg | 2017 | Does Not Function | No |  |  |  | No | Water point under construction | Poor |  | 80754a9bfd73f3b860334c65860bb3
4vgn-gat6-0446 | 1 |  | J7 Rw15 | 1203190300 | 09-03-2017 21:05:54 CET | Mukakarangwa Assoumpta | 00:33:06 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kirurumo |  |  | Bitete-Rwahi network | 1316 |  | 80 | 50 | 30 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8336417737979869 | 29.94346668826428 | 1815.5 | 2c8iday2 | https://waterforpeople.s3.amazonaws.com/images/ea5dfbd2-7d37-4ab9-aeb7-ab9468728016.jpg | Yes | 12 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/7f70dd76-9f95-40d4-a38a-8c3cf841e6c7.jpg | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/1b989ff4-5c60-4e0c-b2c3-6860e001793e.jpg | 2013 | Normal | 600 | Yes | 6 | -1.8427360326225883 | 29.938932546871705 | 1676.5 | 2cnjkbst | https://waterforpeople.s3.amazonaws.com/images/d0d175dc-21c6-4b73-a2cd-3d62fad5e626.jpg | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout | https://waterforpeople.s3.amazonaws.com/images/e6d22cb6-0732-4693-accd-fd3baa2522c6.jpg | 2013 | Normal | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/45257e9d-f9a0-4d51-928d-f0c1b4c5386c.jpg | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.834346985255156 | 29.943555833035514 | 1735.8 | 2c9o1naj | 1 | https://waterforpeople.s3.amazonaws.com/images/7db2d71c-0346-4d06-95cc-2376fdf02834.jpg | 2013 | Poor | No |  |  |  | Yes |  | Normal | There some reservoirs which are not in good condition because during the rehabilitation of 2013 they did not rehabilitate those reservoirs. | 45905ea99b45e698bc80b161ba57fac2
xupw-64jj-2xy1 | 1 |  | J7 Rw26 | 1196560875 | 02-01-2015 05:52:51 CET | Byukusenge Elie | 00:25:32 | 2017 | Rwanda | Rulindo | Cyungo | Rwili | Karambi |  |  | Nyamagana | 20456 |  | 50 | 45 | 5 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank |  | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Normal | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6054950759608764 | 29.92911192201171 | 1935 | 21r6wo63 | 29 | https://waterforpeople.s3.amazonaws.com/images/a113a6ea-0ec4-41f9-81bb-746978f85e05.jpg | 2011 | Normal | Yes | 10 | 30 | The distribution reservoir does not supply water in this transmission line towards reservoir which distribute in Rwili cell | No | bad connection of tee junctions towards Gitare centre | Poor | water tap is at G.S.Gitare and no water available | 32ea352a3b89ec3e73296a627897f9d6
kxm7-0dr1-vc2m | 1 |  | J7 Rw10 | 1205120711 | 10-03-2017 11:33:57 CET | Tuyisenge Vianney | 00:06:35 | 2017 | Rwanda | Rulindo | Bushoki | Mukoto | Buyogoma |  |  | Buyogoma water point/Tare-Rusiga pumping system | 9577 |  | 130 | 130 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This Buyogoma water point operates normally | 8 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 4000 | Yes | 1 | -1.6975730951272476 | 29.89335139673467 | 2119.9 | 25zh425x | https://waterforpeople.s3.amazonaws.com/images/50d1fd29-3cc5-4cf5-9252-aa2bbcd33b3a.jpg | 2015 | Normal | No | [5 empty] | Yes | 1 |  | 2015 | Normal | 8000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.69755594483054 | 29.893253197213703 | 2135.8 | 25zfx6yc | 2 | https://waterforpeople.s3.amazonaws.com/images/3b4e9c0e-f3bb-4995-878d-2f9b84fb96e2.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Buyogoma water point operates normally | 488daa5ccfe2eebda6392dfad73a9b8a
swg3-9y8h-b2x2 | 1 |  | J7 Rw10 | 1218280420 | 14-03-2017 21:58:08 CET | Tuyisenge Vianney | 00:47:02 | 2017 | Rwanda | Rulindo | Tumba | Gahabwa | Mafene |  |  | Nyirambuga 2Pumping station/Source Nyakagezi | 30604 |  | 172 | 172 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | GoR | The Nyirambuga2 puming is operating with a run of one pump due to the fact that the 2nd pump is not operating and is uninstalled to get repaired and maintained | 3 | Spring | -1.727203364074144 | 29.952907868674092 | 1902.1 | 27ch7g21 | https://waterforpeople.s3.amazonaws.com/images/58c81520-f33d-459e-b631-ac61a442a1c8.jpg | Yes | 10 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/ad8db783-350a-4f0c-9565-c10f9aac896b.jpg | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 10 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/3990123d-419b-4b4f-80bc-879546d648c3.jpg | 2012 | Normal | 200 | Yes | 1 | -1.7278167283085102 | 29.95199173165361 | 1808.5 | 27dhivy7 | https://waterforpeople.s3.amazonaws.com/images/5d6e823a-c36a-4da7-9b72-5dd75fab4369.jpg | 2012 | Poor | Yes | 2 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/0f0a85d7-1265-4a6e-a473-70e785fe34a4.jpg | 2012 | Normal | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/de4b18f2-be66-4270-b7e7-e73ee2bb29b8.jpg | 2012 | Normal | 800 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/ad2d8dce-9e50-4b95-9a01-5f66edd8965e.jpg | 2012 | Poor | Yes | https://waterforpeople.s3.amazonaws.com/images/b605fda1-2f2a-4a8b-a9f9-204270f52af4.jpg | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.727254113386681 | 29.953175349536583 | 1807.5 | 27ck6m2z | 1 | https://waterforpeople.s3.amazonaws.com/images/52340e5f-b4fc-4ca2-9d60-c3efd13dee18.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | The Nyirambuga2 pumping station pumps Nyakagezi source(Q=2l/s) to reinforce Nyirambuga1 pumping station.The suction tank for Nyirambuga2 pumping station has started leaking;it needs repair.Only one pumping operating because the second one is not operating due to pumps lubes that cracked and it is under repair and maintenance. A water point is needed to be left nearby pumping station because the present doesnot deliver sufficiently | 7dfdc125462d8f750c3dba8fc94ce5e
3gbu-m66v-8shb | 1 |  | J7 Rw23 | 1215191485 | 15-03-2017 05:15:05 CET | Rugirangoga Augustin | 00:25:42 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Gitovu |  |  | Rwankende | 1789 |  | 154 | 130 | 24 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | gitovu karambi | Governement (District, WASAC) and Water For People |  | 3 | Spring | -1.6128815953757245 | 29.874655017548616 | 1956.1 | 223evzsq |  | Yes | 30 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 30 | Yes | 1 |  | 2012 | Normal | 6450 | Yes | 3 | -1.611167776275264 | 29.8839135826884 | 1852. | 220khftj |  | 2016 | Normal | Yes | 2 | Distribution Chamber |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 6450 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6152549293262255 | 29.88658147328347 | 1819.8 | 227bzq9d | 2 | https://waterforpeople.s3.amazonaws.com/images/f0e82db4-79b4-4782-a200-26dd86441905.jpg | 2017 | Does Not Function | No |  |  |  | Yes |  | Poor |  | 166cb4f78c69e4c2af231d5d8f7fbee
hhuh-68kx-k3uc | 1 |  | J7 Rw26 | 1203950131 | 02-01-2015 05:51:21 CET | Byukusenge Elie | 00:11:58 | 2017 | Rwanda | Rulindo | Cyungo | Burehe | Sove |  |  | Nyamagana | 20456 |  | 74 | 45 | 29 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6296826581236308 | 29.932573310792076 | 1895.7 | 22v748jh | 29 | https://waterforpeople.s3.amazonaws.com/images/2a65f3a8-d537-41f8-9423-83113af4e438.jpg | 2011 | Poor | Yes | 10 | 30 | The distribution reservoir does not supply water in this transmission line | No | bad connection of tee junctions towards Paroisse and G.S.Burehe | Poor | G.S.Burehe water tap doesn't use the water from network they preferred to use rain water | 56e483e723349eec6515641b66a88e5
x348-2wwq-sucg | 1 |  | J7 Rw10 | 1301130100 | 15-04-2017 22:58:11 CEST | Tuyisenge Vianney | 00:13:06 | 2017 | Rwanda | Rulindo | Rusiga | Kirenge | Ntaruka |  |  | Ntaruka water point/Ntaruka-Nyange gravity system | 1567 |  | 176 | 176 | 0 | Yes | Piped Network -- Gravity Only |  | 2010 | Yes | Ntaruka and Kinini | Local government and Nyange girls school | This water point connected to this network is not operational | 1 | Spring | -1.7696354837500834 | 29.920797407345603 | 2024.6 | 29andnk7 | https://waterforpeople.s3.amazonaws.com/images/750c73ed-17cd-41fe-94d4-2e5d40faa0f8.jpg | Yes | 30 | No | [5 empty] | 30 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/c77690b6-2b2b-43fe-848e-ddbe042f8f0d.jpg | 2010 | Normal | 100 | Yes | 1 | -1.7695710385246382 | 29.920989717384256 | 2107.8 | 29ajt1xl | https://waterforpeople.s3.amazonaws.com/images/10f61f77-1f4c-4e79-9d3e-f90d8b26a10c.jpg | 2010 | Poor | No | [5 empty] | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/95027444-441f-48a8-9589-fa13266d1f59.jpg | 2010 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.769401974363637 | 29.92113821294333 | 2008.5 | 29a9oonf | 1 | https://waterforpeople.s3.amazonaws.com/images/e5810fcf-1a23-41e3-9fdb-156354dfeca8.jpg | 2010 | Does Not Function | No |  |  |  | Yes |  | Does Not Function | This water point connected to this network is not operational.However,in water storage tank there is water that is also served to Nyange girls school.The water tap stand got damaged and removed | 77c424a17b97ed8cf26facdc0256b71
ke54-uwn5-17ga | 1 |  | J7 Rw7 | 1233011021 | 24-03-2017 14:44:09 CET | Safari Bosco | 00:27:43 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 5544 |  | 214 | 214 | 0 | Yes | Piped Network with Pump |  | 1986 | Yes | rusenyi,kabeza,kigomwa,gacyamwo,marenge,mutagata,gasharu,kabunga na marembo | Governement (District, WASAC) and Water For People | System works well but has issues in the dry season has 15 resevoirs, 21 taps, and 5000 meter long served by two sources | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 1 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8284906124110314 | 30.064097137403223 | 1580.8 | 2bzzr3c0 | 21 |  | 2016 | Normal | No |  |  |  | Yes |  | Normal | The System was built in 1986 and Rehabilitated by Water For People | 60b5327fad7afa88a874dc986978ec
ut96-w919-xtmh | 1 |  | J7 Rw10 | 1273310104 | 06-04-2017 18:46:56 CEST | Tuyisenge Vianney | 00:08:26 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Bubiro |  |  | Bubiro water point/Rutomvu gravity system | 3015 |  | 158 | 158 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Government of Rwanda | The water point is not operational and was closed for the reason of not having water meter and now the people are fetching from the spring | 1 | Spring | -1.677891751247546 | 29.90118126071259 | 1802.6 | 252xezpf |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6839266229060539 | 29.898537746195398 | 1756.5 | 25cwfdgp | 1 | https://waterforpeople.s3.amazonaws.com/images/017806de-0275-42ba-8ad9-f9ece79220d8.jpg | 2013 | Does Not Function | No |  |  |  | No | The water tap was closed due to no water meter installed | Does Not Function | The water point is not operational and was closed for the reason of not having water meter and now the people are fetching from the spring | 2d695025bd94a26666f7a5c61e73bea
6am4-er9t-cqgn | 1 |  | J7 Rw24 | 1221260292 | 16-03-2017 07:57:34 CET | Kabalisa Manzi Christella | 00:08:29 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Gashinge |  |  | Rwamugaza | 14106 |  | 435 | 435 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government | no problem | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3.5 | Yes | 2 |  |  | 2003 | Normal | 3.5 | Yes | 1 |  | 2003 | Poor | 8000 | Yes | 10 | -1.7374173333138418 | 30.06563288387298 | 1723.9 | 27td31kg |  | 2003 | Normal | Yes | 8 |  | https://waterforpeople.s3.amazonaws.com/images/3cb87c8c-3e70-4f09-9d62-a3a6535796e3.jpg | 2003 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7383948745649853 | 30.06483357604763 | 1735.6 | 27uzfiug | 1 | https://waterforpeople.s3.amazonaws.com/images/d5b78b86-1fde-464e-921f-a35630f69fa6.jpg | 2014 | Poor | No |  |  |  | No | Broken parts | Poor |  | c6114f4fdc31fad0f55c51b4051b994
s5qd-yem8-61d9 | 1 |  | J7 Rw26 | 1201090134 | 02-01-2015 05:53:35 CET | Byukusenge Elie | 00:13:20 | 2017 | Rwanda | Rulindo | Cyungo | Rwili | Kabanda |  |  | Nyamagana | 20456 |  | 69 | 59 | 10 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Normal | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6252943205316805 | 29.927615265550152 | 1846.1 | 22nxqxxo | 29 | https://waterforpeople.s3.amazonaws.com/images/c79682d1-4ad1-427a-a278-210b842518ef.jpg | 2011 | Poor | Yes | 12 | 30 | The distribution reservoir does not supply water in reservoir which distribute in Rwili cell because of bad connection of tee junctions | No | No water in distribution reservoir located in Rwili cell | Poor | water tap is located neat Rwili small market and no water available because of the previous problem in the network | 106bac4bb472e659ce2b5152a7b99949
7ggk-7bvw-8ms | 1 |  | J7 Rw15 | 1238630258 | 21-03-2017 15:11:05 CET | Mukakarangwa Assoumpta | 00:10:11 | 2017 | Rwanda | Rulindo | Kinihira | Rebero | Kabuga |  |  | Miyove-Kinihira | 10452 |  | 191 | 80 | 111 | Yes | Piped Network -- Gravity Only |  | 2001 | Yes | Ndusu | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6597084841567151 | 29.994730011853672 | 1895.4 | 248ufj1n | 2 | https://waterforpeople.s3.amazonaws.com/images/957f7ba1-a4de-4545-a9ca-0d323b1c1db2.jpg | 2015 | Normal | No |  |  |  | Yes |  | Poor |  | 4043a8755e79f012c078495de88157bc
7c1p-41gt-2km5 | 1 |  | J7 Rw15 | 1238630254 | 21-03-2017 15:47:28 CET | Mukakarangwa Assoumpta | 00:14:56 | 2017 | Rwanda | Rulindo | Kinihira | Rebero | Taba |  |  | Miyove-Kinihira | 10452 |  | 122 | 70 | 52 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6637404436908476 | 29.98780374996223 | 2015.6 | 24fiyndy | 1 | https://waterforpeople.s3.amazonaws.com/images/c99bf9df-4d8d-41d5-a049-c7470c19f0a5.jpg | 1989 | Poor | No |  |  |  | Yes |  | Poor | Water point function but is not in good condition | c953ef4fedf4f7fd70a8da88155d0fc
kbha-pgj5-95w3 | 1 |  | J7 Rw23 | 1211540546 | 09-03-2017 08:44:14 CET | Rugirangoga Augustin | 01:21:08 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 1458 |  | 77 | 70 | 7 | Yes | Piped Network -- Gravity Only |  | 2005 | No |  | Governement (District, WASAC) and Water For People | Rehabilitated by Water For people | 1 | Spring | -1.6426625760859115 | 29.882931577022582 | 1948.1 | 23gnwvd9 |  | Yes | 75 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2005 | Normal | 75 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6427455672933784 | 29.88297265715982 | 1913.3 | 23gsoc7h | 2 |  | 2005 | Normal | No |  |  |  | Yes |  | Poor | Water point is leaking and water is wasted | 6fc423703f85ccc12c2789c5ccafe8
mp41-8m72-utds | 1 |  | J7 Rw15 | 1211480311 | 08-03-2017 21:23:15 CET | Mukakarangwa Assoumpta | 00:08:56 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 6436 |  | 354 | 45 | 309 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.859939320022563 | 29.965866276312546 | 2004.3 | 2dfzlwi2 | 1 | https://waterforpeople.s3.amazonaws.com/images/d9e2e655-acab-42bb-9c45-f7912695f0ca.jpg | 2013 | Does Not Function | No |  |  |  | Yes |  | Poor | water point does not function because is not well located | b48b666312c461bc116d2a42fae0c3b7
hkhc-pdb4-njuc | 1 |  | J7 Rw10 | 1237650097 | 02-01-2015 23:27:34 CET | Tuyisenge Vianney | 00:07:00 | 2017 | Rwanda | Rulindo | Tumba | Misezero | Kavumu |  |  | Water point at Kavumu/Nyirambuga pumping | 30604 |  | 139 | 139 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This water tap at Kavumu of Tumba operates well with two taps stands.Its water storage tank valve chamber does nolonger have a cover | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.7034434822125202 | 29.957268169888685 | 2138.3 | 2696lir8 | https://waterforpeople.s3.amazonaws.com/images/594728e2-3acc-40c9-9edb-2663a5def7f2.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7033159922978618 | 29.95723370068306 | 2167.9 | 268yuvw4 | 2015 | https://waterforpeople.s3.amazonaws.com/images/05a45a82-1cb4-412b-8ddb-bbdbde496a87.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap at Kavumu of Tumba operates well with two taps stands.Its water storage tank valve chamber does nolonger have a cover | 81042d1bd88571ba9b39c62e18fba2
q3u2-jcd1-1742 | 1 |  | J7 Rw10 | 1314200068 | 20-04-2017 08:29:43 CEST | Tuyisenge Vianney | 00:05:13 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Rusura |  |  | Water point chez Gidasi/Nyirambuga pumping | 30604 |  | 157 | 157 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | Operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | Yes | 1 | -1.6810517148568218 | 29.94632958579528 | 1846.4 | 2585jz7r | https://waterforpeople.s3.amazonaws.com/images/1802b6c9-5787-4c92-a41b-cf2eaa7c110e.jpg | 2017 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6813363402217574 | 29.94773654496635 | 1810.7 | 258m845x | 2 | https://waterforpeople.s3.amazonaws.com/images/bb268518-ce25-4384-ba8e-a78cc2544349.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | operational | 2a7c59a6ac1e9c83cbd7c49e64b8a19
4ysq-xbnv-8pv5 | 1 |  | J7 Rw23 | 1219010133 | 15-03-2017 06:10:20 CET | Rugirangoga Augustin | 00:24:43 | 2017 | Rwanda | Rulindo | Rukozo | Bwimo | Gatiba |  |  | Gihanga II |  |  | 151 | 151 | 0 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | gatiba gatwa | Governement (District, WASAC) and Water For People | this network has no problem | 1 | Groundwater (well, etc.) | -1.6358367374763643 | 29.917613599705728 | 1996.9 | 235d9tgo |  | Yes | 15 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 15 | Yes | 1 |  | 2016 | Normal | 7000 | Yes | 3 | -1.6473083060242772 | 29.929930420012894 | 1827.6 | 23oc60f7 | https://waterforpeople.s3.amazonaws.com/images/e30ce008-282c-4288-b546-f610f80d2ec9.jpg | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6472183683106405 | 29.92965106025873 | 1830.4 | 23o6t3z4 | 2 | https://waterforpeople.s3.amazonaws.com/images/fc6ec9ed-e6a1-4c10-a8cf-6e927cbf8730.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | Gihanga II network has no problem | afdf0a173ff948e868f4f3ec9733ffa
4mtx-kpsg-wd59 | 1 |  | J7 Rw10 | 1214361341 | 16-03-2017 17:43:10 CET | Tuyisenge Vianney | 00:08:04 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | Rwintare1water point[RW.WFP.Q3.14.166.028]/Tare-Rusiga pumping | 9577 |  | 281 | 281 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | The water point located in Rwintare village of Gako/Rusiga.It operates very well and normally | 1 | Spring | -1.69919116767908 | 29.937233740854015 | 1848.2 | 2625kai4 |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8347913523118269 | 29.951416863360556 | 2034.2 | 2caeu5kq | 1 | https://waterforpeople.s3.amazonaws.com/images/298201b7-4aea-4e2e-ab74-61ff0591e8bd.jpg | 2015 | Normal | No |  |  |  | Yes |  | Poor | The water point located in Rwintare village of Gako/Rusiga.It operates very well and normally | ac409ebb79e48990c5d1268bd74c5aa5
5m2m-p3yx-520p | 1 |  | J7 Rw24 | 1252100147 | 28-03-2017 10:04:14 CEST | Kabalisa Manzi Christella | 00:10:08 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyagasozi |  |  | Kararama network | 6572 |  | 197 | 197 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People |  | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 1 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 7 | -1.7558238738774876 | 30.05848449136532 | 1855.1 | 28nt627c | https://waterforpeople.s3.amazonaws.com/images/e4b3c109-0cc0-4ac2-9f9d-40048e9a07ac.jpg | 2012 | Normal | Yes | 14 |  | https://waterforpeople.s3.amazonaws.com/images/fe1bdb4f-2047-44cf-a178-774dcbe34305.jpg | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.755608510831598 | 30.058686025859913 | 1866 | 28ng2iwa | 1 | https://waterforpeople.s3.amazonaws.com/images/95f8398e-7d4f-445e-97e8-a67b93e91174.jpg | 2012 | Does Not Function | No |  |  |  | No | Broken parts | Does Not Function |  | 74234391f01f38f241775c22a99a26d
tmg6-k7pn-20q8 | 1 |  | J7 Rw24 | 1221260274 | 16-03-2017 08:13:30 CET | Kabalisa Manzi Christella | 00:07:24 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Kigabiro |  |  | Rwamugaza | 14106 |  | 565 | 565 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3.5 | Yes | 2 |  |  | 2003 | Normal | 3.5 | Yes | 1 |  | 2003 | Normal | 8000 | Yes | 20 | -1.7430462257687191 | 30.059140540269198 | 1780 | 282oa33j | https://waterforpeople.s3.amazonaws.com/images/24cdab03-5a87-43d9-a9ca-51e54f329299.jpg | 2003 | Poor | Yes | 16 |  | https://waterforpeople.s3.amazonaws.com/images/a01f819b-345a-412f-b96a-48cdf7bbf4d5.jpg | 2003 | Poor | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.742698265803926 | 30.059412899740575 | 1783.7 | 2823fwxe | 1 | https://waterforpeople.s3.amazonaws.com/images/c9555d1c-28ad-43eb-9232-c84dd9d2ea29.jpg | 2003 | Normal | No |  |  |  | No | System under rehabilitation | Normal |  | 4cce87197c43e1032a859ff104e54b3
dhvt-ywp2-jg8m | 1 |  | J7 Rw7 | 1236940977 | 24-03-2017 10:23:11 CET | Safari Bosco | 01:14:48 | 2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Kigomwa |  |  | marenge | 5544 |  | 118 | 118 | 0 | Yes | Piped Network with Pump |  | 1997 | Yes | rusenyi,kabeza,kigomwa,gacyamo,marenge,mutagata,gasharu,kabuga,marembo | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 15 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.05522315814525 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8202967854502825 | 30.05263683371014 | 1888.5 | 2bmfjn72 | 1 | https://waterforpeople.s3.amazonaws.com/images/a0bea71b-5f55-4c41-b0f4-4fbf401e7add.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | a9419a838c1b6dce8a808ad89c4d0e6
23rc-ks4u-x120 | 1 |  | J7 Rw19 | 1235330142 | 23-03-2017 19:14:55 CET | Kayinamura Innocent | 00:09:41 | 2017 | Rwanda | Rulindo | Masoro | Kabuga | Kigarama |  |  | Mutagata motorised network | 26296 |  | 176 | 95 | 81 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Water for People and Government will |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2017 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.781043092444677 | 30.05482402475248 | 1777.3 | 29tip9tw | 64 | https://waterforpeople.s3.amazonaws.com/images/b01ad30e-6e8d-4d00-8ed8-da88296993b8.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 6186821958ba8e5a33c8d7404990a59f
asss-vau2-51h5 | 1 |  | J7 Rw10 | 1204712636 | 03-01-2015 01:51:38 CET | Tuyisenge Vianney | 00:08:19 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Water point near TCT/Nyirambuga pumping | 30604 |  | 174 | 174 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | The water point nearby TCT operates well | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.6955598855995109 | 29.92194956947296 | 2119.9 | 25w4ui6r | https://waterforpeople.s3.amazonaws.com/images/dda6984b-133d-4a5d-a8f2-b0e18437d9ff.jpg | 2015 | Normal | Yes | 1 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/16d156e9-1aea-42e5-b045-082d4d1af78b.jpg | 2015 | Normal | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/8a69882d-0627-435f-8b17-a548746e1ba1.jpg | 2015 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6949149630376994 | 29.92169101377827 | 2121.5 | 25v2qrgw | 2 | https://waterforpeople.s3.amazonaws.com/images/8e9c25a6-4101-439a-b5fc-c31f8a0064d8.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The water point nearby TCT operates well and the storage tank R100m3 serves Bushoki and some parts of Tumba | e6e5affc57756d25e40985a60b487
ar7g-us0e-k4dr | 1 |  | J7 Rw15 | 1239940180 | 23-03-2017 06:29:52 CET | Mukakarangwa Assoumpta | 00:12:34 | 2017 | Rwanda | Rulindo | Kinihira | Marembo | Cyogo |  |  | Nyamagana-Kinihira |  |  | 420 | 420 | 0 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People | -Water point located in Cyogo village is for Kigali primary school | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦Ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6663241940694076 | 29.935566850551517 | 1889.5 | 24jskh23 | 3 | https://waterforpeople.s3.amazonaws.com/images/2d9ae147-e60f-483c-948e-3ba5049872dd.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | 50bfbc464c129c3bb2a59447dd452d1
3hty-raf6-c2vn | 1 |  | J7 Rw10 | 1204712637 | 03-01-2015 02:23:33 CET | Tuyisenge Vianney | 00:05:09 | 2017 | Rwanda | Rulindo | Tumba | Barari | Gaseke |  |  | Gaseke center water point/Nyirambuga pumping | 30604 |  | 149 | 149 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | Water point have not yet been delivering water to the people | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7161838475233637 | 29.927668427639375 | 1776.5 | 26u93r7w | 2 | https://waterforpeople.s3.amazonaws.com/images/c2ba9c41-65c4-4ac9-af6c-286a1234b7da.jpg | 2017 | Normal | No |  |  |  | No | Not yet open to the people however water is available since it sometimes leakes | Does Not Function | Not yet open to the people however water is available since it sometimes leakes | ec757e1dbd4bbb538a718423d348b84
9e5q-qwvh-vunh | 1 |  | J7 Rw23 | 1202111894 | 15-03-2017 08:04:48 CET | Rugirangoga Augustin | 00:25:05 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 2456 |  | 214 | 185 | 29 | Yes | Piped Network -- Gravity Only |  | 2017 | Yes | buramba mushongi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6498521069502532 | 29.917613599705728 | 1996.9 | 23sjzjl4 |  | Yes | 15 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 15 | Yes | 2 |  | 2016 | Poor | 7200 | Yes | 6 | -1.6498521069502532 | 29.917613599705728 | 1996.9 | 23sjzjl4 |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6527824398187623 | 29.9130307087954 | 1768.2 | 23xefjsq | 2 | https://waterforpeople.s3.amazonaws.com/images/206523be-06e1-4557-90eb-79d6538e3414.jpg | 2017 | Does Not Function | No |  |  |  | No | the road destroyed the pipes | Poor | some tanks and water taps do not receive water because road construction project destroyed them | 85159a57acba3d67f8fe8edaabf0348a
2yga-nycu-ur66 | 1 |  | J7 Rw8 | 1214692670 | 16-03-2017 08:51:17 CET | Amani Desire | 00:10:40 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  |  | 510 |  | 186 | 38 | 148 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi |  |  | 1 | Spring | -1.768794219980039 | 29.93859037021456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7413338226723385 | 29.930371637634263 | 2025.9 | 27zugxnr | 28 | https://waterforpeople.s3.amazonaws.com/images/95b0f056-e8b0-414f-8ede-9eb470bf3a9e.jpg | 2014 | Does Not Function | Yes | 8 | 30 | water doesnt reach the distribution Reservoir R50m3 located at kibamba village | No | water doesnt reach the distribution R50m3 located at kibamba village and all water points served by this Reservoir do not have water since last july 2016 | Does Not Function | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | 4e4277fb87648c3ba9c99e49d9173e43
6dup-uq2a-0k5r | 1 |  | J7 Rw8 | 1241920593 | 23-03-2017 08:00:44 CET | Amani Desire | 00:10:10 | 2017 | Rwanda | Rulindo | Murambi | Gatwa | Kabeza |  |  | Mutagata Motorised Network | 26296 |  | 134 | 134 | 0 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release chamber |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8155267997514342 | 30.038510043037157 | 1845.4 | 2bejjvj5 | 64 | https://waterforpeople.s3.amazonaws.com/images/768d1b48-d76e-459e-b04e-a9d5a31fb247.jpg | 2016 | Does Not Function | No |  |  |  | No | the pipe from reservoir to the water point is broken | Does Not Function | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | 3fb19ca5f1864d4349af3beb6a90af5e
2a3v-7hc6-1604 | 1 |  | J7 Rw10 | 1275300051 | 05-04-2017 21:40:02 CEST | Tuyisenge Vianney | 00:06:29 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Karambi |  |  | Nyabishengeshi gravity system/Karambi water point | 893 |  | 79 | 79 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People | Karambi water point does nolonger deliver water to the people due to taps stolen and damaged | 1 | Spring | -1.6778517470929726 | 29.880934967401814 | 2032.3 | 252v194p |  | Yes | 50 | No | [5 empty] | 50 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6764723948617257 | 29.885090750975195 | 1981.2 | 250kvfoi | 0 | https://waterforpeople.s3.amazonaws.com/images/572abd6a-4039-4686-bb57-d0aa86658e44.jpg | 2013 | Does Not Function | No |  |  |  | No | Karambi water point does nolonger deliver water to the people due to taps stolen and damaged | Does Not Function | Karambi water point does nolonger deliver water to the people due to taps stolen and damaged | 9d6fdf75c32cbfac5dc3b2e29acb
5e4j-kacs-570h | 1 |  | J7 Rw8 | 1223880212 | 16-03-2017 08:48:14 CET | Amani Desire | 00:17:04 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kibamba |  |  | Musenge Network | 6074 |  | 176 | 100 | 76 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber¦washout and Air release |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7525693147309045 | 29.93218464377976 | 1956.3 | 28if2q0p | 28 | https://waterforpeople.s3.amazonaws.com/images/27c23a11-0c35-4cbc-b4d3-e58399022a07.jpg | 2014 | Does Not Function | Yes | 8 | 30 | the water point was out of service because water do not reach the distribution reservoir that serves this water point | No | water do not reach the distribution reservoir that serves this water point | Does Not Function | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | 8a74c1591952c5e27c6e48a850898a2e
ag7k-20p7-r45x | 1 |  | J7 Rw24 | 1221300172 | 15-03-2017 16:08:49 CET | Kabalisa Manzi Christella | 00:15:08 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Muhomdo |  |  | Rwamugaza | 14106 |  | 305 | 0 | 305 | Yes | Piped Network with Pump |  | 2014 | No |  | Governement (District, WASAC) and Water For People | No Problem with the Water Point | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 3000 | Yes | 3 | -1.7555179528295524 | 30.03970289656239 | 1690.5 | 28napmb1 |  | 2014 | Does Not Function | Yes | 8 |  |  | 2014 | Does Not Function | Yes | 2 |  | 2014 | Does Not Function | 3000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Does Not Function | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7498833917114711 | 30.042604665791 | 1589.1 | 28dzikqy | 1 | https://waterforpeople.s3.amazonaws.com/images/b5ff1ee7-357c-4461-a339-de0497061a88.jpg | 2014 | Does Not Function | Yes | 365 | 0 | Water is not Flowing | No | Water is not Flowing | Does Not Function | Water is not Flowing | b2c03a6da35ac42d832afa924edda95
uh87-1wbm-cbp | 1 |  | J7 Rw10 | 1234030503 | 03-01-2015 00:59:17 CET | Tuyisenge Vianney | 00:08:04 | 2017 | Rwanda | Rulindo | Tumba | Taba | Nkinda |  |  | Nkinda water point/Nyirambuga pumping | 30604 |  | 127 | 127 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point at Nkindi operates well and functions normally. | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7241712024227362 | 29.959716190628022 | 2094.7 | 277gt3t9 | 2 | https://waterforpeople.s3.amazonaws.com/images/04e88868-df83-493e-b8d9-87da5465694f.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point at Nkindi operates well and functions normally. | 62fb76f7c1381239ff32dd848d1877ba
ycuy-ksrs-p8hp | 1 |  | J7 Rw10 | 1316860070 | 20-04-2017 17:51:38 CEST | Tuyisenge Vianney | 00:07:48 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | NKANGA SCHOOL WATER POINT/KIVOMO-NTAKARA GRAVITY |  |  | 129 | 129 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Not operational | 2 | Spring | -1.827334932521246 | 29.95090160939001 | 1943.1 | 2by2osad |  | Yes | 50 | No | [5 empty] | 50 | No | [5 empty] | No | [8 empty] | Yes | 1 | Water point valve chamber | https://waterforpeople.s3.amazonaws.com/images/bd891272-5067-4ee5-96d1-721db4ab60c8.jpg | 2015 | Does Not Function | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8192049235118855 | 29.962049358620746 | 1681.7 | 2bkmndk4 | 1 | https://waterforpeople.s3.amazonaws.com/images/6af57dd3-a8d9-427d-8dd8-bbd8681bcebe.jpg | 2015 | Does Not Function | No |  |  |  | No | not operational | Does Not Function | Pupils have cut the pipeline serving water to the school and till now they do not have water because no maintenance works have been done | d87eb87f8c1db69f029fb24f083fae9
j3j9-v772-e9ym | 1 |  | J7 Rw7 | 1241830342 | 24-03-2017 12:56:10 CET | Safari Bosco | 00:12:47 | 2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Kigomwa |  |  |  | 5544 |  | 118 | 118 | 0 | Yes | Piped Network with Pump |  | 1998 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8304402295570403 | 30.05690363552983 | 1839.2 | 2c37um8p | 2 | https://waterforpeople.s3.amazonaws.com/images/bacc7294-8246-4a5c-aaa8-74186e4cdbb8.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | e873d2efef9e6193cd53c32012d3e5c4
k51x-ujpb-y9sc | 1 |  | J7 Rw15 | 1199310668 | 09-03-2017 20:40:24 CET | Mukakarangwa Assoumpta | 00:06:36 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Gisoro- Nyundo network | 2297 |  | 188 | 35 | 153 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.840451151026817 | 29.948165560771624 | 1795.9 | 2cjrthy1 |  | Yes | 13 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 13 | Yes | 1 |  | 2013 | Normal | 30 | Yes | 6 | 1.8406374522240199 | 29.94836287627501 | 1783.7 | 2ck2jau3 |  | 2013 | Poor | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 7000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.852379487372217 | 29.94257048909944 | 1497.5 | 2d3hi6zl | 1 | https://waterforpeople.s3.amazonaws.com/images/f2913bc4-5695-4310-ad86-1bb813a064c3.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 3ad9a49b15e0a28bd1516efcfade8596
fetj-4pr2-msum | 1 |  | J7 Rw24 | 1255500224 | 28-03-2017 10:49:51 CEST | Kabalisa Manzi Christella | 00:06:05 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nombe |  |  | Rwamugaza network | 14106 |  | 193 | 193 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7572344734002943 | 30.072258234569123 | 1732.3 | 28q546lu | 1 | https://waterforpeople.s3.amazonaws.com/images/9101a566-776e-4732-bd72-2e3ca6c015de.jpg | 2003 | Does Not Function | No |  |  |  | No | Water is not Flowing | Poor |  | 6016afb371d38c19159ec42f8ca6843d
kepm-fx4f-97h5 | 1 |  | J7 Rw23 | 1324530093 | 23-04-2017 14:43:47 CEST | Rugirangoga Augustin | 00:33:17 | 2017 | Rwanda | Rulindo | Buyoga | Gahororo | Gatenderi |  |  | Kiruruma | 8295 |  | 141 | 102 | 39 | Yes | Piped Network with Pump |  | 2014 | Yes | gatenderi gatare shagasha rutabo |  |  | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 11 | -1.6684773741137722 | 29.8839135826882 | 1775.8 | 24ncknpz |  | 2014 | Normal | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7207539945015276 | 30.06521483108458 | 1626 | 271t6vqk | 2 | https://waterforpeople.s3.amazonaws.com/images/d0c59d50-d555-4e68-9103-d720dce166b5.jpg | 2014 | Normal | No |  |  |  | No | Water seller was not around | Normal |  | ce317caba97ff89e5ffcd3d75f6c6580
pnn6-qfja-acy | 1 |  | J7 Rw10 | 1237760284 | 03-01-2015 00:04:58 CET | Tuyisenge Vianney | 00:08:06 | 2017 | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point at GS Gisha/Nyirambuga pumping | 30604 |  | 133 | 133 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | At GS Gisha the water tap is well served with water from the Main Reservoir R300m3.Only water lacks in rationing system.However the supplying storage tank valve chamber has no cover. | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.735574705199902 | 29.963301840053223 | 2119.1 | 27qbj9gx | https://waterforpeople.s3.amazonaws.com/images/0bd97af5-5b04-44e7-9bda-4f4e6aa08d06.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.741530068280557 | 29.966437362941264 | 2061.4 | 2806dm1c | 3 | https://waterforpeople.s3.amazonaws.com/images/d87472c3-0521-4ec2-a12c-65b8fca226c9.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | At GS Gisha the water tap is well served with water from the Main Reservoir R300m3.Only water lacks in rationing system.However the supplying storage tank valve chamber has no cover. | 405e6144dae1ae147c16f1636ba886
a7sh-gkgq-pw6j | 1 |  | J7 Rw15 | 1433410372 | 02-06-2017 07:20:03 CEST | Mukakarangwa Assoumpta | 00:13:29 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | rwamugaza | 14106 |  | 200 | 200 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | Yes | all villages of Ntarabana | Government | water point of kajevuba health center | 2 | Spring | 1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | 1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 | Sedimentation Tank¦Pressure Break Tank¦Distribution Chamber |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8090092273909542 | 30.12648036110569 | 1426 | 2b3rd9sg | 1 | https://waterforpeople.s3.amazonaws.com/images/07f48cd6-3be7-4c72-98d2-509293117cf4.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | 511735e2f91ada3c4f83bd336586e1d
n873-jkpc-0ef2 | 1 |  | J7 Rw26 | 1244900060 | 03-01-2015 04:45:48 CET | Byukusenge Elie | 00:05:31 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Shyondwe |  |  | Kabonanyoni | 7894 |  | 75 | 70 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare, Kabera,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe, Kabyayi, Kabingo, Kamiyove, Murwa, Nyenyeri, Rukingu and Kivomo | Governement (District, WASAC) and Water For People | This is the New pumping system which serves the community located at the uphill, it has 5 sources, one source which is located in Miyove sector, Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro,This network has one reservoir which is not functioning, This network serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 10 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.644236999570869 | 29.955962458560606 | 2042.3 | 23j9dxwn | 31 | https://waterforpeople.s3.amazonaws.com/images/c05aa3c3-ad09-4539-958b-c8c3cc304fe5.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | 2a77973b7268cca5ccb4482776384
wu93-v30f-q3bs | 1 |  | J7 Rw8 | 1211930903 | 10-03-2017 10:18:22 CET | Amani Desire | 00:22:28 | 2017 | Rwanda | Rulindo | Ngoma | Karambo | Kagwa |  |  | Kabarore- Ngoma- Nyabuko network | 8284 |  | 123 | 38 | 85 | Yes | Piped Network with Pump |  | 2014 | Yes | nyabuko,kigwa, kiruli, busizi,ngaru,kirungu,kiboha,kigina | Governement (District, WASAC) and Water For People |  | 4 | Spring | -1.8123357076877171 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦collection chamber | 2014 | Poor | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.808716485895084 | 29.973362007273437 | 2001 | 2b3a3o2d |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8410402188505337 | 29.98755429516009 | 1644.7 | 2ckqy2xv | 17 | https://waterforpeople.s3.amazonaws.com/images/763775b1-f599-4723-be20-c1fc721231c8.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | -The network has 17 water points -water points are in good operational conditions except the water point at the source that is damaged -4 water points don't have water today - the pipes are in good operational conditions -The pump is not working properly as it was expected during Design, Today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy -the transformer at the pumping station is doesnt offer the required energy to the pump - the anti hammers of pump are not functioning because of bad installation of pumping house -The system has two pumps with four units with two units pumping in one direction towards Nyabuko and other two in an other direction towards ngoma sector office -The suction tank is in bad physical conditions | 9ab787d4f190152bd8107a996d344b92
pk10-ar07-4581 | 1 |  | J7 Rw24 | 1220870295 | 16-03-2017 08:02:49 CET | Kabalisa Manzi Christella | 00:07:30 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Mayaga |  |  | Rwamugaza | 14106 |  | 525 | 525 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government | no problem | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3.5 | Yes | 2 |  |  | 2003 | Normal | 3.5 | Yes | 1 |  | 2003 | Normal | 8000 | Yes | 10 | -1.7374173333138418 | 30.06563288387298 | 1723.9 | 27td31kg |  | 2014 | Normal | Yes | 8 |  |  | 2014 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7438388313141766 | 30.067954554180183 | 1654.1 | 283zbbyf | 1 | https://waterforpeople.s3.amazonaws.com/images/68fce995-7b10-4067-80d4-0ffb76d68e48.jpg | 2014 | Poor | No |  |  |  | No | System has some problems | Poor |  | c257eb3ed5ec64258640917b64877be
sug9-p4fx-cv5k | 1 |  | J7 Rw8 | 1242950132 | 23-03-2017 08:12:11 CET | Amani Desire | 00:38:40 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Ruri |  |  | Mutagata Motorised Network | 26296 |  | 189 | 79 | 110 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release chamber |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8116825982240459 | 30.040094567937054 | 1888.6 | 2b86xf8w | 64 | https://waterforpeople.s3.amazonaws.com/images/cfc5ab1d-8b63-469d-87fa-12d3fef82b92.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | dcb22ad5deafac5f4e46ec46d3d82e22
rr1b-57w8-bsw6 | 1 |  | J7 Rw10 | 1218280691 | 15-03-2017 19:25:47 CET | Tuyisenge Vianney | 00:06:59 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Gatsinde |  |  | Gatsinde water point/Nyirambuga pumping | 30604 |  | 178 | 178 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | GoR | Gatsinde water point/Nyirambuga pumping operates well though tap valves are not fixed | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.6795031455153646 | 29.92850282627714 | 1938.1 | 255l9sb9 | https://waterforpeople.s3.amazonaws.com/images/f0406b04-366c-409f-b623-4f9423af1ee6.jpg | 2012 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6792386721268995 | 29.92845278712606 | 1929.3 | 255572z8 | 1 | https://waterforpeople.s3.amazonaws.com/images/69c9ae60-9718-4ba6-8a3b-29a0bd5ac936.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Gatsinde water point/Nyirambuga pumping operates well though tap valves are not fixed | 23d5bba0e37d58512c5f8d493ef2322
3kvw-5ss5-274d | 1 |  | J7 Rw26 | 1209260078 | 12-03-2017 07:15:39 CET | Byukusenge Elie | 00:09:46 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Kivomo |  |  | Nyamagana | 20456 |  | 80 | 30 | 50 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank | This network serves four sectors Cyungo,Rukozo, Base,Base and Kinihira, It has some problems in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible because it serves many populations and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Poor | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6559757169847988 | 29.955985558109298 | 1797.9 | 242ocu3r | 29 | https://waterforpeople.s3.amazonaws.com/images/48acb1f0-5cc6-491c-8923-7dd68ceeedc0.jpg | 2011 | Poor | Yes | 10 | 30 | Bad tee connections and the bad types of pipeline | No | No taps on the water tap | Poor | No water available in centre Kivomo and the Population use the wetland water near Kinihira and they use the protected spring. | 882917badc6a5877e13e4b9b12ae
bqq4-4695-vrc1 | 1 |  | J7 Rw7 | 1238670498 | 24-03-2017 12:45:56 CET | Safari Bosco | 00:37:47 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 5544 |  | 214 | 214 | 0 | Yes | Piped Network with Pump |  | 1998 | No |  | Governement (District, WASAC) and Water For People | This Systems Functions well | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.05522315814525 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8264661417489594 | 30.055944150751554 | 1887.1 | 2bwmw3gv | 1 | https://waterforpeople.s3.amazonaws.com/images/ddc800ad-4ab7-4bd4-b4b8-e4824e86b598.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | Water is available and system is functional and has 21 water taps | e5761d54ea6c8c4348e416cc95dbf233
scwq-erj5-4ee5 | 1 |  | J7 Rw10 | 1295730114 | 15-04-2017 23:53:36 CEST | Tuyisenge Vianney | 00:08:57 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Ntakara |  |  | Kivomo water point/Kivomo-Ntakara |  |  | 200 | 200 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | Kabunigo,Rwintare and Ntakara villages | Local government with partnering with the community | The water point is operation and functions well | 1 | Spring | -1.827334932521246 | 29.95090160939001 | 1943.1 | 2by2osad | https://waterforpeople.s3.amazonaws.com/images/4d689c38-6610-4636-9e2f-4decd6a9ee39.jpg | Yes | 50 | No | [5 empty] | 50 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/6782c4d1-9d5e-464d-97df-3cc9dc4595f4.jpg | 2015 | Normal | 100 | Yes | 1 | -1.8272713668427036 | 29.95112068798981 | 1931.8 | 2bxz46nr | https://waterforpeople.s3.amazonaws.com/images/e28398af-ec55-487f-bce4-8a6b0069026e.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8272557781680918 | 29.951292880763233 | 1934 | 2bxxxbg8 | 1 | https://waterforpeople.s3.amazonaws.com/images/b01cdce6-d81c-4936-be38-6fdc866e0e08.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The water point is operation and functions well.It is shared by Kabunigu,Rwintare and Ntakara | ff6e6b71a948291c4295ea2d236a152
5c9s-a63r-nnbn | 1 |  | J7 Rw23 | 1222070224 | 15-03-2017 05:48:42 CET | Rugirangoga Augustin | 00:23:26 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 1458 |  | 229 | 190 | 39 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | This Systems Functions well | 1 | Groundwater (well, etc.) | -1.647515621777326 | 29.88420972245651 | 1745 | 23ooo3ru |  | Yes | 75 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2017 | Normal | 75 | Yes | 1 |  | 2016 | Normal | 3000 | Yes | 1 | -1.6503465715220755 | 29.883009582768896 | 1737.7 | 23td5rym | https://waterforpeople.s3.amazonaws.com/images/3aeb594b-41a8-4ba7-b046-fb2502c37608.jpg | 2016 | Normal | Yes | 1 | Pressure Break Tank |  | 2016 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6503993876246474 | 29.882830045126585 | 1728.3 | 23tg4xzg | 2 | https://waterforpeople.s3.amazonaws.com/images/751fd939-ae7d-4112-9d29-18511485b4e7.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | the system works well | 1e3c874226f41630a727db5760b04cac
34rt-1x6q-y2ws | 1 |  | J7 Rw15 | 1201250482 | 08-03-2017 19:43:30 CET | Mukakarangwa Assoumpta | 00:11:16 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kigarama |  |  | kinywamagana pumping network | 6436 |  | 233 | 89 | 144 | Yes | Piped Network with Pump |  | 2013 | Yes | Nyakaruri | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8539157226491598 | 29.978082502356624 | 1895.2 | 2d616yf8 | 1 | https://waterforpeople.s3.amazonaws.com/images/c03c6a60-928f-4d06-895f-fb6a4477de1f.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | 3cf25b61f1affccfe1723b857ea76d3
3vdq-gpve-kt73 | 1 |  | J7 Rw23 | 1322790102 | 23-04-2017 14:42:54 CEST | Rugirangoga Augustin | 00:13:21 | 2017 | Rwanda | Rulindo | Buyoga | Gahororo | Gipfundo |  |  | rukondo |  |  | 162 | 120 | 42 | Yes | Piped Network -- Gravity Only |  | 2012 | No |  | G.thierry | System originates from Gicumbi | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 30 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 30 | Yes | 1 |  | 2012 | Normal | 4500 | No | [8 empty] | No | [5 empty] | Yes | 1 |  | 2012 | Normal | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7157830318933 | 30.080218942947564 | 1528.1 | 26tlag76 | 1 | https://waterforpeople.s3.amazonaws.com/images/ca3944ef-d66b-4a0c-9c40-a154e60de6a1.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | This System originates from Gicumbi District | ee6dfc81e1f1e6c47b05480c8a95216
2q9d-23jw-sq3f | 1 |  | J7 Rw10 | 1320550056 | 20-04-2017 13:25:04 CEST | Tuyisenge Vianney | 00:06:27 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Rugando |  |  | Water point at Rugando chez Ndayambaje/Nyirambuga pumping | 30604 |  | 161 | 161 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | Water available but taps not yet fixed | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6780597496753507 | 29.935016249066038 | 1790 | 2536xxna | 2 | https://waterforpeople.s3.amazonaws.com/images/8da5c0b6-6cd4-40f0-bb47-32ad156e7dc2.jpg | 2017 | Does Not Function | No |  |  |  | No | Taps not yet fixed | Does Not Function | Water available but taps not yet fixed | dce065624d544a3d75ad090c9aaf28a
u6qa-erap-69vw | 1 |  | J7 Rw10 | 1205750418 | 10-03-2017 11:15:30 CET | Tuyisenge Vianney | 00:08:49 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Nyenyeri |  |  | Nyenyeri water point/Tare-Rusiga pumping | 9577 |  | 68 | 68 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This Nyenyeri water point operates normally though one water tap among the two risk to get damaged | 10 | Spring | -1.737983836200818 | 29.9058560590111 | 2048.8 | 27ub0pte |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 70 | Yes | 1 |  | 2015 | Normal | 4000 | Yes | 1 | -1.6938699778976278 | 29.88802790510189 | 2157.8 | 25tc88ow | https://waterforpeople.s3.amazonaws.com/images/be6d2817-108a-478b-9b22-b23731b1f0c6.jpg | 2015 | Normal | No | [5 empty] | Yes | 3 |  | 2015 | Normal | 8000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6939905422974624 | 29.888105232491917 | 2157 | 25tjyvk1 | 2 | https://waterforpeople.s3.amazonaws.com/images/0bc4173a-46e3-4767-af9d-b34de37b56b1.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water points operates normally though one of its two taps risk to get damaged | 8395e68260bbea2da8335ec51f833381
np3f-gc3k-9ppt | 1 |  | J7 Rw19 | 1225090085 | 17-03-2017 05:24:05 CET | Kayinamura Innocent | 00:22:47 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Munini |  |  | Musenge network | 6074 |  | 111 | 49 | 62 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma, Karehe, Rutonde, Gitaba, Kiruri, Buhira, Ruhanya, Kibamba, and Karindi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.9385370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Washout and Air release chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.794608367466457 | 29.950350144046055 | 1926.5 | 2afy11bj | 28 | https://waterforpeople.s3.amazonaws.com/images/42da9415-00a1-4519-b0ce-698c0162d2d4.jpg | 2014 | Does Not Function | No |  |  |  | Yes |  | Poor | 1. the system has two Pumps but one is damaged and is not working, only one pump is used to pump water 2. Eleven (11) water points served by the distribution reservoir R 50m3 located at Kibamba village do not have water today because water don't reach this reservoir reservoir, there is not water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5. one water point doesn't Function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | d35c749f993d11e4e6232631fd7c6d
xcs7-rp9e-ap6f | 1 |  | J7 Rw24 | 1222090698 | 16-03-2017 06:40:03 CET | Kabalisa Manzi Christella | 00:07:13 | 2017 | Rwanda | Rulindo | Burega | Taba | Nyagisozi |  |  | Rwamugaza | 14106 |  | 520 | 520 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | no problem | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7351185822787192 | 30.00671512151363 | 2029.3 | 27pk5bz7 | 1 | https://waterforpeople.s3.amazonaws.com/images/4ace8090-33ec-4d34-9998-b7b4e42fc7a7.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | no problem | b295f32ab415a92d9cc5d7699b76363
sq2a-g5pj-c4d5 | 1 |  | J7 Rw15 | 1200280448 | 09-03-2017 19:51:11 CET | Mukakarangwa Assoumpta | 00:06:44 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Gishyita |  |  | Gisoro- Nyundo network | 2297 |  | 205 | 110 | 95 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.840451151026817 | 29.948165560771624 | 1795.9 | 2cjrthy1 |  | Yes | 13 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 13 | Yes | 1 |  | 2013 | Normal | 30 | Yes | 6 | 1.8406374522240199 | 29.94836287627501 | 1783.7 | 2ck2jau3 |  | 2013 | Poor | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 7000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8692767214564603 | 29.938327478747848 | 1456.4 | 2dvforav | 1 | https://waterforpeople.s3.amazonaws.com/images/38356e44-ac3f-49f6-96df-b2eaf139f19d.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | c712d4ffd1f1624c12e6858b35fccbbe
8jq1-a60u-bmu5 | 1 |  | J7 Rw24 | 1217930669 | 15-03-2017 17:04:58 CET | Kabalisa Manzi Christella | 00:07:41 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Gacyamo |  |  | Rwamugaza | 14106 |  | 550 | 550 | 0 | Yes | Piped Network with Pump |  | 2012 | Yes | Gacyamo na Kisigiro | Governement (District, WASAC) and Water For People | No Problem with the Water Point | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 23 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7472752482627212 | 30.048158066467842 | 1917.1 | 289o4fwh | 1 | https://waterforpeople.s3.amazonaws.com/images/ec88d03d-8a63-4103-b754-74b6b545dbec.jpg | 2012 | Normal | No |  |  |  | No | Water seller was not around | Normal | This Water Point/system functions well | 41d9cc308f7e2a1169b587218e81375d
t7at-mggc-s3uk | 1 |  | J7 Rw26 | 1193310245 | 07-03-2017 10:08:01 CET | Byukusenge Elie | 00:09:26 | 2017 | Rwanda | Rulindo | Cyungo | Marembo | Rusayo |  |  | Nyabirarama |  |  | 150 | 100 | 50 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This network has two water taps and it serves the Population of Rusayo village and the main purpose is to serve G.G.S.Nganzo | 1 | Spring | -1.604039112491394 | 29.911449592055785 | 2015.7 | 21orzdpm |  | Yes | 150 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 150 | Yes | 1 |  | 2015 | Normal | 1200 | Yes | 1 | -1.6034700300768703 | 29.91505418395048 | 1924.9 | 21nun3v2 |  | 2015 | Normal | Yes | 1 | Distribution Chamber |  | 2015 | Normal | Yes | 1 |  | 2015 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6034210472599661 | 29.915515522551168 | 1876 | 21nrnxub | 2 | https://waterforpeople.s3.amazonaws.com/images/43fb8c34-68d1-4a2e-880a-91b9d1e3c8e6.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | the network has been used by G.S.Nganzo school and the Population used the water tap on The source and i found as main challenge. | 48b482364a9af139be5b5b4c72ad490
xjyt-1u25-8v5y | 1 |  | J7 Rw10 | 1305650101 | 16-04-2017 23:02:00 CEST | Tuyisenge Vianney | 00:03:51 | 2017 | Rwanda | Rulindo | Buyoga | Karama | Kigarama |  |  | Kigarama water point/Nyirambuga pumping system | 30604 |  | 121 | 121 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | Under construction | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6915073936798586 | 29.976581161027127 | 1897.2 | 25pfpylx | 2 | https://waterforpeople.s3.amazonaws.com/images/fce2a7ac-2004-4d46-bf50-52f9f320a247.jpg | 2017 | Does Not Function | No |  |  |  | No | under progress | Does Not Function | under progress | ebb5e47440d4dc91ea94b7d0f55f54bd
dx1p-usmt-h7rt | 1 |  | J7 Rw26 | 1203940168 | 02-01-2015 05:57:43 CET | Byukusenge Elie | 00:12:15 | 2017 | Rwanda | Rulindo | Cyungo | Rwili | Karambi |  |  | Nyamagana | 20456 |  | 50 | 5 | 45 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6113663164147713 | 29.928452952212123 | 1831 | 220we49g | 29 | https://waterforpeople.s3.amazonaws.com/images/f82cc619-97da-4c69-88ac-c632825995e9.jpg | 2011 | Poor | Yes | 10 | 30 | The distribution reservoir does not supply water in this transmission line and in the distribution reservoir located in Rwili cell | No | bad connection of tee junctions towards Rwili cells | Poor | water tap is well placed in centre gitare and there is no water available for long time | dc5d6e94e6e2c7e7345e35e03096abd0
5vbw-ajj4-bdy1 | 1 |  | J7 Rw7 | 1241150244 | 24-03-2017 11:58:50 CET | Safari Bosco | 00:11:33 | 2017 | Rwanda | Rulindo | Masoro | Shengampuri | Agasharu |  |  |  | 6740 |  | 130 | 130 | 0 | Yes | Piped Network with Pump |  | 1998 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.813352982413237 | 30.062258321086187 | 1784.6 | 2bayctfy | 2 | https://waterforpeople.s3.amazonaws.com/images/5e2d3dcb-5f05-4f22-9383-1ba3f0846dbc.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 1c53777099f3d1283035a2523c6785ce
7ddv-7xwy-8cpc | 1 |  | J7 Rw26 | 1230030634 | 21-03-2017 13:56:52 CET | Byukusenge Elie | 00:15:36 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Kabingo |  |  | Kabonanyoni | 7894 |  | 35 | 35 | 0 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Poor | Yes | 1 |  | 2015 | Normal | 720 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6444523084923446 | 29.966992215536276 | 2027.3 | 23jmhhat | 31 | https://waterforpeople.s3.amazonaws.com/images/80f5e6dd-51bf-4e25-b5af-ff8f88287065.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is in good condition and most of the community prefer to use it. | 67811135a79dec750e95e83f382615a
ys1r-4x6g-2mcj | 1 |  | J7 Rw26 | 1245730114 | 03-01-2015 04:52:44 CET | Byukusenge Elie | 00:09:00 | 2017 | Rwanda | Rulindo | Rukozo | Mbuye | Mujebe |  |  | Kabonanyoni | 7894 |  | 800 | 800 | 0 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare, Kabera,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe, Kabyayi, Kabingo, Kamiyove, Murwa, Nyenyeri, Rukingu and Kivomo | Governement (District, WASAC) and Water For People | This is the New pumping system which serves the community located at the uphill, it has 5 sources, one source which is located in Miyove sector, Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro,This network has one reservoir which is not functioning, This network serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6199860067484741 | 29.95782828125414 | 2051.4 | 22f5lry2 | 31 | https://waterforpeople.s3.amazonaws.com/images/4b5e9308-8a1a-4317-b233-7698091f2753.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water tap in good condition at E.P.Kabonanyoni and it is used by the students and staff. | 9c1afa4ed73bf3f39967135b71deb1f6
3qs8-bvkw-0ekt | 1 |  | J7 Rw19 | 1194211663 | 07-03-2017 15:33:30 CET | Kayinamura Innocent | 00:14:17 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Ruhondo |  |  | Kishwi network | 1309 |  | 184 | 58 | 126 | Yes | Piped Network -- Gravity Only |  | 2003 | Yes | Buraro and Ruhondo | Goverment | One Part of the system was Rehabilitated By the Government (District, WASAC) and Water For People | 1 | Spring | -1.7722077069769515 | 29.962926865497884 | 1849 | 29ewe2ct |  | Yes | 25 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 25 | Yes | 2 |  | 2016 | Normal | 700 | Yes | 2 | -1.7714946380440713 | 29.96372874178695 | 1845.6 | 29dq4aet |  | 2003 | Normal | No | [5 empty] | Yes | 2 |  | 2003 | Normal | 680 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7721771599288656 | 29.963585834470017 | 1852.6 | 29eulrjn | 4 | https://waterforpeople.s3.amazonaws.com/images/523e41fa-97e1-4989-84c5-fbe41c566e68.jpg | 2003 | Does Not Function | No |  |  |  | Yes |  | Poor | Source gets dirty in the rainy season, part of the system was destroyed, one water point is not functional | f9129f9e854f35c303715356ca99f6c
m05a-00en-kjwy | 1 |  | J7 Rw10 | 1320480049 | 20-04-2017 06:51:05 CEST | Tuyisenge Vianney | 00:07:38 | 2017 | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point Kumanga /Nyirambuga pumping | 30604 |  | 115 | 115 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | One tap stand and cover for storage tank were removed | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | Yes | 1 | -1.7077983784477964 | 29.957013304520803 | 2227.4 | 26gdl2wi | https://waterforpeople.s3.amazonaws.com/images/9fb572d4-43d0-42d5-a4bc-33f28a83fae2.jpg | 2012 | Poor | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7078651098993654 | 29.958069572099667 | 2193.9 | 26ghr458 | 2 | https://waterforpeople.s3.amazonaws.com/images/59bda652-1de0-45b5-8335-95b5b8163be5.jpg | 2012 | Poor | No |  |  |  | Yes |  | Poor | One tap stand and cover for storage tank were removed | a0ab3b98ac8d9a1b91a1032174d75
vt5j-y9wd-7fw1 | 1 |  | J7 Rw15 | 1203320359 | 09-03-2017 20:15:56 CET | Mukakarangwa Assoumpta | 00:25:16 | 2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Rimwe |  |  | Gisoro- Nyundo network | 2297 |  | 120 | 25 | 95 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.840451151026817 | 29.948165560771624 | 1795.9 | 2cjrthy1 |  | Yes | 13 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 13 | Yes | 1 |  | 2013 | Normal | 30 | Yes | 6 | 1.8406374522240199 | 29.94836287627501 | 1783.7 | 2ck2jau3 |  | 2013 | Poor | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 7000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8781620631864513 | 29.95170498457644 | 1427.8 | 2ea4z471 | 1 | https://waterforpeople.s3.amazonaws.com/images/4c97a546-f22f-48e5-a772-6e23a9f6d7f0.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 521d809f8ad4028dae991b91a271f3
a9jr-dhd6-gvjy | 1 |  | J7 Rw15 | 1238960290 | 22-03-2017 18:19:47 CET | Mukakarangwa Assoumpta | 00:16:06 | 2017 | Rwanda | Rulindo | Kinihira | Rebero | Karambi |  |  | Nyamagana-Kinihira |  |  | 144 | 80 | 64 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦Ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6745885074986744 | 29.971631870402373 | 1974.8 | 24xgcj0k | 2 | https://waterforpeople.s3.amazonaws.com/images/9570febd-1e98-4b55-a905-8363d22f1dd1.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | cee6259f175781f8c6a251e2e775638
6q7q-sr34-k7uf | 1 |  | J7 Rw8 | 1211930923 | 10-03-2017 10:25:08 CET | Amani Desire | 01:16:54 | 2017 | Rwanda | Rulindo | Ngoma | Kabuga | Nyabuko |  |  | Kabarore-Ngoma-Nyabuko network | 8284 |  | 122 | 30 | 92 | Yes | Piped Network with Pump |  | 2014 | Yes | Nyabuko, Kagwa,kiruri,busizi,ngaru,kirungu,kiboha, kigina | Governement (District, WASAC) and Water For People |  | 4 | Spring | -1.8123357076877171 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦collection chamber | 2014 | Normal | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.808716485895084 | 29.973362007273437 | 2001 | 2b3a3o2d |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8114646081587216 | 29.97319674889057 | 1991 | 2b7ttvf7 | 17 | https://waterforpeople.s3.amazonaws.com/images/58a89385-53d5-4a82-a2da-ede507917133.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | -the network has 17 water points - water points are in good operational conditions expect water point at the source that is damaged -4 water points don't have water today -The pipes are in good condition - the pump is not working properly as it was expected during Design due to the the lack of sufficient energy - the transformer at the pumping station doesnt offer the required energy to the pump - the anti hammers of pump are not functioning because of bad installation of the pumping house -the system has two pumps with 4 units with two units pumping in one direction towards Nyabuko and other two in an other direction towards Ngoma sector office - The suction tank is in bad physical conditions | 6d3e6bad9c835c5572e579fdd855d9
pq3q-q3py-8ru8 | 1 |  | J7 Rw23 | 1204700674 | 12-03-2017 18:40:43 CET | Rugirangoga Augustin | 00:14:04 | 2017 | Rwanda | Rulindo | Base | Gitare | Gatete |  |  | Rwicanyoni | 698 |  | 141 | 135 | 6 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | kirwa gatete gisiza | Governement (District, WASAC) and Water For People | Water system has no problem | 2 | Spring | -1.6644377224987001 | 29.903649586570488 | 1928 | 24go1jh8 |  | Yes | 10 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 10 | Yes | 1 |  | 2016 | Normal | 8600 | Yes | 3 | -1.6605194594779042 | 29.90927074216649 | 1808.8 | 24a6nmdw |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6545027828404797 | 29.904978605053525 | 1752.1 | 2408u3s9 | 2 | https://waterforpeople.s3.amazonaws.com/images/ea87727b-ab2a-4e86-8cbb-700e3396d8d6.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | the network is fine | 7d5f3e1c4cdd3e73947f5651589c9cf3
nx0n-jhxq-4rjr | 1 |  | J7 Rw26 | 1237880170 | 21-03-2017 14:17:15 CET | Byukusenge Elie | 00:15:47 | 2017 | Rwanda | Rulindo | Rukozo | Mbuye | Nyarusebeya |  |  | Kabonanyoni | 7894 |  | 80 | 70 | 10 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6042831128865018 | 29.950528487079147 | 2041.6 | 21p6v84x | 31 | https://waterforpeople.s3.amazonaws.com/images/b04eef3f-0641-4877-81ac-776d5d6dbdcc.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is located to the source Sindiye and the community use it as they do not pay for water. | b14245f66355a1c21cb38f82a67bb2bf
d1h1-4eqc-uaew | 1 |  | J7 Rw8 | 1193310651 | 07-03-2017 21:09:08 CET | Amani Desire | 00:16:14 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gihonga |  |  | Kibuye | 1232 |  | 110 | 60 | 50 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | Network is new and is in good operational conditions -water points are new and in good conditions | 2 | Spring | -1.73191032363990618 | 29.9285227727732 | 1850.6 | 27k9mlsl |  | Yes | 45 | Yes | 2 |  | start and collection chamber | 2016 | Normal | 45 | Yes | 1 |  | 2016 | Normal | 1500 | No | [8 empty] | Yes | 1 | washout chamber |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7252645615805617 | 29.93084170930244 | 1768.5 | 2799pcj0 | 1 | https://waterforpeople.s3.amazonaws.com/images/1a402564-c72a-46ca-b8da-b097ce3bffed.jpg | 1998 | Does Not Function | No |  |  |  | No | the connection to this water point is damaged | Does Not Function | the water is not in good operational conditions | c11bb26f4c97a25bb9601c3523755d59
x9bc-0323-vyuy | 1 |  | J7 Rw15 | 1202310331 | 09-03-2017 06:35:57 CET | Mukakarangwa Assoumpta | 00:14:57 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Gishyita |  |  | kirikumuryango network |  |  | 205 | 120 | 85 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8742643999895792 | 29.935768742434384 | 1358.4 | 2e3os259 | 1 | https://waterforpeople.s3.amazonaws.com/images/2f74102c-d6c0-4d2e-a442-cdbc938b4207.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | a4cee8e75b66f58759f9e1b8967104e
qrvr-q4g8-y04c | 1 |  | J7 Rw24 | 1323090187 | 24-04-2017 21:51:54 CEST | Kabalisa Manzi Christella | 00:32:18 | 2017 | Rwanda | Rulindo | Kisaro | Kigarama | Runyinya |  |  | wasac network towards Mutete in Gicumbi district |  |  | 148 | 148 | 0 | Yes | Piped Network -- Gravity Only |  | 2000 | No |  | Government |  | 2 | Spring | -1.6521994188708533 | 30.063205521865356 | 2032.1 | 23wfb09k |  | Yes | 5 | Yes | 1 |  |  | 2003 | Normal | 5 | Yes | 1 |  | 2003 | Normal | 30000 | Yes | 7 | -1.6521994188708533 | 30.063205521865356 | 2032.1 | 23wfb09k | https://waterforpeople.s3.amazonaws.com/images/325779c4-ad1e-485a-a2b2-a9a69f9f60e7.jpg | 2003 | Normal | Yes | 14 |  |  | 2003 | Normal | Yes | 1 |  | 2003 | Normal | 30000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.652362079674339 | 30.063264640267157 | 2060.1 | 23wpfdjs | 1 | https://waterforpeople.s3.amazonaws.com/images/01865d36-a788-4543-8730-a1ff18a47200.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal | This System originates from Gicumbi District | a4ddca103fa997cea1348d17df4fbe38
464h-uws1-87th | 1 |  | J7 Rw15 | 1214440108 | 08-03-2017 20:13:11 CET | Mukakarangwa Assoumpta | 00:11:43 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatimba |  |  | kinywamagana pumping network | 6436 |  | 217 | 82 | 135 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8536058576265706 | 29.967111752011117 | 1926.8 | 2d5iqil3 | 1 | https://waterforpeople.s3.amazonaws.com/images/22034dc5-e48f-40cd-8ce3-781bb5de7e30.jpg | 2013 | Does Not Function | No |  |  |  | Yes |  | Poor | This water point does not used | 1d6386cc71c845ecd06ac73daaacc2
85sx-ddh7-fa68 | 1 |  | J7 Rw15 | 1239960217 | 23-03-2017 07:17:40 CET | Mukakarangwa Assoumpta | 00:37:31 | 2017 | Rwanda | Rulindo | Kinihira | Marembo | Gatare |  |  | Nyamagana- Kinihira |  |  | 168 | 70 | 98 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 18 | Distribution Chamber¦Washout, Ventouse |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6583869308030887 | 29.919259766897365 | 1936.9 | 246nuam0 | 2 | https://waterforpeople.s3.amazonaws.com/images/12776059-98d7-4725-80d7-02416a118de3.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | 73446e5c70b6b7576cf7b7d411d6c
we4m-e3jd-1fja | 1 |  | J7 Rw26 | 1193820719 | 02-01-2015 04:33:27 CET | Byukusenge Elie | 01:17:40 | 2017 | Rwanda | Rulindo | Cyungo | Rwili | Nturo |  |  | Nyamabara |  |  | 2785 | 1450 | 1335 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs | https://waterforpeople.s3.amazonaws.com/images/b199f9a9-4cad-4cfd-adab-8d8e0f60db04.jpg | Yes | 5 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/1f7bcac2-473c-4989-bbf0-87d5aa485a69.jpg | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/ae4e201c-1374-41f2-bc98-784cadc37065.jpg | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x | https://waterforpeople.s3.amazonaws.com/images/16e5224d-aa84-45cd-aa17-31a28ce464ba.jpg | 2011 | Normal | Yes | 15 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/7e86f2fc-219c-4115-9899-434f300febae.jpg | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6226673483071388 | 29.921801903817286 | 1940.9 | 22jl5xsi | 29 | https://waterforpeople.s3.amazonaws.com/images/9227d468-077a-46a1-a5f5-5c9c06279035.jpg | 2011 | Normal | Yes | 10 | 30 | The problem of inter connection and bad connection of tee junctions even not well located main distribution reservoir at Sakara Village | Yes |  | Poor | This water tap is located near another water tap from Sakara Pumping thus the Population prefer to use that one. | 354b77357661d72e9bb4a756e260b321
y28d-e6p2-t39y | 1 |  | J7 Rw7 | 1233741193 | 23-03-2017 16:19:15 CET | Safari Bosco | 00:32:42 | 2017 | Rwanda | Rulindo | Murambi | Bubangu | Taba |  |  | rwiseke | 9536 |  | 193 | 193 | 0 | Yes | Piped Network -- Gravity Only |  | 2001 | Yes | gashubi,taba,rebero | Governement (District, WASAC) and Water For People | This Water Point works well | 3 | Spring | -1.8081127252820783 | 30.019302406005654 | 1889.4 | 2b2ado4h |  | Yes | 14 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2001 | Normal | 14 | Yes | 1 |  | 2001 | Normal | 12000 | Yes | 7 | -1.8083188633668612 | 30.018599981640595 | 1825.6 | 2b2mac7t |  | 2001 | Normal | No | [5 empty] | Yes | 1 |  | 2001 | Normal | 12000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.851156785980757 | 30.037195765762668 | 1760.8 | 2d1gvbwz | 1 | https://waterforpeople.s3.amazonaws.com/images/d76bff66-d1cf-44ad-9290-82b6b52de70b.jpg | 2001 | Normal | No |  |  |  | Yes |  | Normal | The system has a problem water reduced | c66fc4376f42e52ea57337cd9eb4fda5
rng3-u68h-n8ky | 1 |  | J7 Rw15 | 1205330375 | 09-03-2017 17:53:49 CET | Mukakarangwa Assoumpta | 00:10:35 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Ngendo |  |  | kirikumuryango network |  |  | 180 | 180 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | Yes | Nyabyondo | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 10000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.910878274581095 | 29.982994207645937 | 1352.7 | 2fs8g06t | 1 | https://waterforpeople.s3.amazonaws.com/images/ae818972-4dc8-4092-9de3-a8e25c8e2d63.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | -This network of Kirikumuryango was rehabilitated in 2013 and it has 11km. -During the rain season source become dirty. | afcb5d7da86156fcd887272be8f653d
fw4s-xr81-76ah | 1 |  | J7 Rw15 | 1223630078 | 12-03-2017 12:56:33 CET | Mukakarangwa Assoumpta | 00:07:19 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kagunda |  |  | Muvumu- Taba |  |  | 94 | 25 | 69 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.8242130164596562 | 29.931083430301516 | 1700.7 | 2bswxje6 |  | Yes | 25 | No | [5 empty] | 25 | Yes | 1 |  | 2013 | Normal | 800 | Yes | 3 | 1.828985219687556 | 29.926634523104315 |  | 2c0sxawy |  | 2013 | Poor | Yes | 9 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 7500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8356287129933786 | 29.925799839209034 | 1624.8 | 2cbs94l5 | 1 | https://waterforpeople.s3.amazonaws.com/images/685facc3-5bb4-4820-aaaf-4aaad39a3505.jpg | 2013 | Normal | Yes | 1 | 3 | Those rehabilitating Rushinya source had strayed it | Yes |  | Poor |  | aabcb2e62617b8b6b1b2dc96d1beeb1
bdp0-yg20-4n4j | 1 |  | J7 Rw10 | 1317470066 | 20-04-2017 12:01:13 CEST | Tuyisenge Vianney | 00:05:14 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point chez Haguma/Nyirambuga pumping | 30604 |  | 169 | 169 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | Operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | Yes | 1 | -1.689313034457321 | 29.93747945297606 | 2091.6 | 25ltc0tq | https://waterforpeople.s3.amazonaws.com/images/f06be139-b93f-421f-94e3-c0e0e6ce3787.jpg | 2017 | Normal | Yes | 1 | Pressure Break Tank | https://waterforpeople.s3.amazonaws.com/images/f938c070-26c3-4b13-8110-fbee06a0c027.jpg | 2017 | Normal | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/005b21e6-0e27-4c97-837d-bcb7f5a394b8.jpg | 2017 | Normal | 100 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.687064311797058 | 29.936745522538597 | 2057.5 | 25i3dhpj | 2 | https://waterforpeople.s3.amazonaws.com/images/c2a3def3-8b6c-4404-a21a-1d4560e36b71.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | operational | e13bc18c35efd39bbc878424e9a7c65
jv5b-aet2-vaxt | 1 |  | J7 Rw15 | 1202350691 | 09-03-2017 21:52:47 CET | Mukakarangwa Assoumpta | 00:07:13 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Rwahi |  |  | Bitete-Rwahi network | 1316 |  | 360 | 360 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.8336417737979869 | 29.94346668826428 | 1815.5 | 2c8iday2 |  | Yes | 12 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 |  | 2013 | Normal | 600 | Yes | 6 | 1.8427360326225883 | 29.938932546871705 | 1676.5 | 2cnjkbst |  | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦Washout, Ventouse |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8595530396503857 | 29.925995628517203 | 1430 | 2dfczf7f | 1 | https://waterforpeople.s3.amazonaws.com/images/78309f60-8fd9-4486-8882-ee3208fd5c62.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 35607fb4ff040e8566ec557b6e5316f
ywvj-gg4s-pgfr | 1 |  | J7 Rw15 | 1244760070 | 23-03-2017 06:13:46 CET | Mukakarangwa Assoumpta | 00:05:35 | 2017 | Rwanda | Rulindo | Kinihira | Marembo | Cyogo |  |  | Nyamagana-Kinihira |  |  | 184 | 60 | 124 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦Ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6668998044016576 | 29.941056675766742 | 1957.6 | 24kqi6ky | 2 | https://waterforpeople.s3.amazonaws.com/images/53f8539a-8c23-4987-9f4a-b6e180fc14d0.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | ab388e34bd8b66b22fb7b2b3a9b46b87
rukx-2bkv-8aqb | 1 |  | J7 Rw8 | 1219440168 | 10-03-2017 12:13:23 CET | Amani Desire | 00:32:07 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Rwambogo |  |  | Rwambogo | 934 |  | 156 | 54 | 102 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | the system is new and is in good operational conditions | 2 | Spring | -1.7494428720359798 | 29.92803731989297 | 1795.4 | 28d9bh8w | https://waterforpeople.s3.amazonaws.com/images/3ac84c44-c250-4a5f-8af4-f44400300239.jpg | Yes | 60 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/f44bcf2d-07b4-48f5-b6f3-2eabc4706c8f.jpg | "Springbox" --Intake Structure at a Spring¦collection chamber | 2016 | Normal | 60 | Yes | 1 |  | 2016 | Normal | 700 | Yes | 1 | -1.7469516964101284 | 29.923916567592556 | 1765.3 | 28952jl3 | https://waterforpeople.s3.amazonaws.com/images/fce50baa-3c8e-4435-b389-62ab3a9d28c2.jpg | 2016 | Poor | No | [5 empty] | Yes | 1 |  | 2016 | Poor | 350 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7497097862059392 | 29.927387177960835 | 1787.6 | 28dosqyx | 3 | https://waterforpeople.s3.amazonaws.com/images/324a55a2-c4a2-40bf-a50d-0b3746f40e73.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | -No water at all water points excpet at the water point at the source - water don't reach the Distribution reservoir because the pipe that enters water to the tank is disconnected and broken | e0b0af92f14f1de1e2f13a833f829c
n8xx-sa8g-f7ec | 1 |  | J7 Rw15 | 1205330377 | 09-03-2017 19:38:40 CET | Mukakarangwa Assoumpta | 00:07:50 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Kigali |  |  | Gisoro- Nyundo network | 2297 |  | 300 | 300 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.840451151026817 | 29.948165560771624 | 1795.9 | 2cjrthy1 |  | Yes | 13 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 13 | Yes | 1 |  | 2013 | Normal | 30 | Yes | 6 | 1.8406374522240199 | 29.94836287627501 | 1783.7 | 2ck2jau3 |  | 2013 | Poor | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 7000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8618559366311842 | 29.944875640774214 | 1578.5 | 2dj5x4hk | 1 | https://waterforpeople.s3.amazonaws.com/images/9b1e3bfe-c96c-457f-b573-ee35f2650e6a.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | Water point is for Nyundo primary school | a8e5a1133d3914c4eacbec91721043e
rsvk-yj9j-5k2y | 1 |  | J7 Rw8 | 1317910087 | 20-04-2017 14:45:58 CEST | Amani Desire | 00:09:27 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kinini/Mbogo |  |  |  | 510 |  | 188 | 80 | 108 | Yes | Piped Network -- Gravity Only |  | 2004 | No |  |  |  | 2 | Spring | -1.759698733765297 | 29.933777367513624 | 1859.9 | 28u7kscp |  | Yes | 180 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 180 | Yes | 1 |  | 2016 | Normal | 1000 | Yes | 1 | -1.7580489779060636 | 29.93419245007874 | 1843.1 | 28rhc9jh |  | 2003 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7654922549522123 | 29.932708976310913 | 1816 | 293sw77j | 2004 | https://waterforpeople.s3.amazonaws.com/images/5df2176b-b405-4e39-a93a-fe5d57969e50.jpg | 2004 | Normal | No |  |  |  | Yes |  | Poor |  | 31d6d2e57d4a7fe420439c36f985d549
hu52-agtb-b8t6 | 1 |  | J7 Rw15 | 1229190575 | 22-03-2017 18:38:18 CET | Mukakarangwa Assoumpta | 00:08:52 | 2017 | Rwanda | Rulindo | Kinihira | Butunzi | Bunahi |  |  | Nyamagana-Kinihira |  |  | 105 | 60 | 45 | Yes | Piped Network with Pump |  | 2015 | Yes | All villages of Butunzi and Marembo and Karambi village | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦Ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6642194298858077 | 29.96213381467028 | 1890.5 | 24gay0md | 2 | https://waterforpeople.s3.amazonaws.com/images/9c6e5b86-6a91-41f6-b4e1-7599b837a9ba.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | a3a9da1cbc2e594e349b0e3c9d382e
b2nw-a4td-g3fx | 1 |  | J7 Rw7 | 1442611745 | 04-06-2017 13:25:00 CEST | Rugirangoga Augustin | 00:19:19 | 2017 | Rwanda | Rulindo | Kisaro | Gitatsa | Ruberano |  |  | gahama | 10234 |  | 132 | 100 | 32 | Yes | Piped Network with Pump |  | 2012 | Yes | ruberano gatete mugomero gishinge nyakarekare kibingwe | waterforpeople | ntakibazo uyu muyoboro ufite | 2 | Spring | -1.6675834297797398 | 30.0428712210569 | 1965.7 | 24lvl43w |  | Yes | 65 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 65 | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 | Pressure Break Tank¦Distribution Chamber¦washout, air release |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6520949082846663 | 30.04109467095679 | 1887.8 | 23w9co1m | 1 | https://waterforpeople.s3.amazonaws.com/images/54b49fbd-9879-4a21-b213-3cf9a131634b.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | uyu muyoboro(ivomo) ntakibazo rifite | 7fac18a06668d91a9fc51ac9b2537029
u7fd-4wqw-50un | 1 |  | J7 Rw26 | 1202140134 | 02-01-2015 05:52:14 CET | Byukusenge Elie | 00:08:34 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Kabingo |  |  | Nyamagana | 20456 |  | 50 | 45 | 5 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.592031897072048 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Poor | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6436175209590775 | 29.92540989807403 | 1794.6 | 23i8h25y | 29 | https://waterforpeople.s3.amazonaws.com/images/ed542386-d3ea-4cd3-b54e-085ae2a5be18.jpg | 2011 | Normal | No |  |  |  | Yes |  | Poor | The community does not use it and they prefer to use the rain water and the wetland water | 203ecf8768ae451697f199fcb3c99e4
81n7-q3j3-7wjf | 1 |  | J7 Rw23 | 1242080213 | 23-03-2017 17:26:01 CET | Rugirangoga Augustin | 00:31:31 | 2017 | Rwanda | Rulindo | Buyoga | Ndarage | Gahondo |  |  | Ndarage |  |  | 105 | 100 | 5 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | karambi Gahondo Bunyana Rugarama Gasave | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.6829614865475908 | 30.031434012077444 | 1962 | 25bb9sey |  | Yes | 30 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 30 | Yes | 1 |  | 2014 | Normal | 6300 | Yes | 5 | -1.6902852583901373 | 30.03414816539013 | 1811.8 | 25nf3391 | https://waterforpeople.s3.amazonaws.com/images/4c2bc2fb-f6dc-456c-af5b-c63241677025.jpg | 2014 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6902852583901373 | 30.03414816539020 | 1810.5 | 25nf3391 | 1 |  | 2014 | Normal | No |  |  |  | Yes |  | Normal |  | 1cb3c81dd22c8083a56f9a66a99028cd
g2dv-ec66-0j4x | 1 |  | J7 Rw19 | 1244890166 | 23-03-2017 18:33:32 CET | Kayinamura Innocent | 00:11:00 | 2017 | Rwanda | Rulindo | Masoro | Kabuga | Nyakizu |  |  | Mutagata motorised network | 26296 |  | 196 | 106 | 90 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.777015078219158 | 30.06105742678471 | 1717.6 | 29murl36 | 64 | https://waterforpeople.s3.amazonaws.com/images/6f4a4d7e-3201-4073-bd3f-fce1714dbf29.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 298dbb44cdbd3e13971b128339e735
5ugv-am0x-5ach | 1 |  | J7 Rw23 | 1236140591 | 23-03-2017 06:26:54 CET | Rugirangoga Augustin | 00:42:10 | 2017 | Rwanda | Rulindo | Buyoga | Gitumba | Munini |  |  | Kiruruma | 8295 |  | 158 | 150 | 8 | Yes | Piped Network with Pump |  | 2014 | Yes | Rutabo gitaba nyarubuye remera rusongati rugarama cyasuli munini | Governement (District, WASAC) and Water For People | this network has no problems | 2 | Groundwater (well, etc.) | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 15 | -1.6111677762752643 | 29.8839135826884 | 1852 | 220khftj |  | 2014 | Normal | Yes | 5 | Pressure Break Tank |  | 2014 | Normal | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6862747139419287 | 30.051575421169506 | 1999.3 | 25gsc9sz | 2 | https://waterforpeople.s3.amazonaws.com/images/5c271200-aac6-4214-88c2-c889c7af527e.jpg | 2014 | Does Not Function | No |  |  |  | No | this water tap is not working | Poor | the water tap does not work | 643bd8ae12778604b20828a31c51da7
mx0r-ux8y-2xy6 | 1 |  | J7 Rw8 | 1220240935 | 16-03-2017 08:49:21 CET | Amani Desire | 00:09:11 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gicumbi |  |  | Musenge Network | 6074 |  | 141 | 41 | 100 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi |  |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.77801882415555 | 29.94376186134791 | 1903.2 | 29oiawod | 28 | https://waterforpeople.s3.amazonaws.com/images/92a89b7e-cf2a-453d-b7ea-f2bafeff32b5.jpg | 2014 | Does Not Function | No |  |  |  | No | water is damaged and is not functioning | Does Not Function | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | b3e5c99e04cc0d168d8e6b825ddfafb
w75g-r0r2-yrhh | 1 |  | J7 Rw15 | 1210500418 | 08-03-2017 21:29:54 CET | Mukakarangwa Assoumpta | 00:06:35 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 6436 |  | 354 | 89 | 265 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8636748667810057 | 29.963155579827312 | 1970.3 | 2dm6a0q7 | 1 | https://waterforpeople.s3.amazonaws.com/images/0cfe73a7-17ad-491c-8ecb-3ebbead7e7b1.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | 1c4352f8e2edbc8b2685f724ba7881e
bpuk-nscu-ysk5 | 1 |  | J7 Rw15 | 1202320523 | 09-03-2017 19:20:00 CET | Mukakarangwa Assoumpta | 00:07:32 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyabitare |  |  | Gisaro-Nyundo network |  |  | 130 | 50 | 80 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.840451151026817 | 29.948165560771624 | 1795.9 | 2cjrthy1 |  | Yes | 13 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 13 | Yes | 1 |  | 2013 | Normal | 38 | Yes | 6 | 1.8406374522240199 | 29.94836287627501 | 1783.7 | 2ck2jau3 |  | 2013 | Poor | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 7000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.851609902418587 | 29.954569111030587 | 1642.6 | 2d27nti1 | 1 | https://waterforpeople.s3.amazonaws.com/images/60efa3ee-e87c-45c2-9652-97237d00c6d8.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 9db2ee74c24728e878dbafb55555ffb0
aea8-qg2u-3mrk | 1 |  | J7 Rw26 | 1193310222 | 07-03-2017 10:39:41 CET | Byukusenge Elie | 00:10:39 | 2017 | Rwanda | Rulindo | Cyungo | Marembo | Gahinga |  |  | Mugomero Marembo | 3456 |  | 652 | 602 | 50 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | Kidomo, Gahinga, Nganzo, Rusayo,Buyaga and Murambo | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.5777496463341437 | 29.93714072556937 | 2147.8 | 20haqsiz |  | Yes | 120 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 120 | Yes | 2 |  | 2015 | Normal | 10000 | Yes | 10 | -1.5961706844323926 | 29.91257085345822 | 2085.4 | 21bs0o8l |  | 2015 | Normal | Yes | 3 | Distribution Chamber |  | 2015 | Normal | Yes | 2 |  | 2015 | Normal | 10000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6053755548515243 | 29.914471694842266 | 1982.3 | 21qzrgso | 8 | https://waterforpeople.s3.amazonaws.com/images/140edaba-455d-45ef-b00d-50f4458c86ef.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The population of gahinga do not use this water tap as it is located fall way from their home so it will be better if we change the horizontal alignment of The network so that this water tap Will have located near the Population. | 58b289f8be80ea5aa79c072adfa7e81
t8u5-d9tu-k41u | 1 |  | J7 Rw15 | 1239070128 | 21-03-2017 17:53:30 CET | Mukakarangwa Assoumpta | 00:07:49 | 2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Ntunguru |  |  | Miyove- Kinihira | 10452 |  | 168 | 60 | 108 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6715103367031914 | 29.964593094699875 | 1977.2 | 24sdkg8t | 1 | https://waterforpeople.s3.amazonaws.com/images/997236c4-3a7f-42c2-8b49-3a5d77269dc4.jpg | 2001 | Does Not Function | No |  |  |  | Yes |  | Poor |  | faa6be4b7b4f776ad85f82b836e69f7
wx3c-65y7-ph9j | 1 |  | J7 Rw23 | 1225600203 | 15-03-2017 08:07:33 CET | Rugirangoga Augustin | 00:23:48 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 2456 |  | 214 | 200 | 14 | Yes | Piped Network -- Gravity Only |  | 2017 | Yes | mushongi Buramba | Governement (District, WASAC) and Water For People | this network works in one part | 1 | Spring | -1.6358367374763643 | 29.9135277934778 | 1996.9 | 235d9tfj |  | Yes | 15 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 15 | Yes | 2 |  | 2016 | Poor | 7200 | Yes | 6 | -1.6498521069502532 | 29.917613599705728 | 1996.9 | 23sjzjl4 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Poor | 7200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6533339518832098 | 29.912839907596755 | 1763.5 | 23yb6e2g | 2 | https://waterforpeople.s3.amazonaws.com/images/7651d243-2c65-4792-8405-7fb4eb417b7c.jpg | 2017 | Does Not Function | Yes | 7 | 7 | it is new(it is still in construction). | No | water pipes have been destroyed | Poor | some water taps and tanks do not get water | 7a1cad7ff5b86d8c4531eac8c9f781c
7wrm-na6f-jhme | 1 |  | J7 Rw10 | 1311290294 | 20-04-2017 15:58:34 CEST | Tuyisenge Vianney | 00:06:52 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Karambo |  |  | Water point at Buramira Primary school/Buramira-Kivure gravity system | 1255 |  | 250 | 250 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Students are 1150 approaching 250 families.The water point is operational and water is available | 2 | Spring | -1.6776639816373493 | 29.911131429480132 | 2061.4 | 252jq0vb |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6686222104797874 | 29.922559798951145 | 1784.5 | 24nli63d | 2 | https://waterforpeople.s3.amazonaws.com/images/05daeb29-19ff-4269-b3fe-38bed798d3b6.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Students are 1150 approaching 250 families.The water point is operational and water is available | 637d46db47472aee6ee61b4d28ee936c
synq-s7sp-4yxj | 1 |  | J7 Rw15 | 1212380222 | 08-03-2017 21:51:35 CET | Mukakarangwa Assoumpta | 00:10:08 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatwa |  |  | kinywamagana pumping network | 6436 |  | 354 | 30 | 324 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Poor | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.875218272222894 | 29.963893189815558 | 1853.1 | 2e59c8ty | 1 | https://waterforpeople.s3.amazonaws.com/images/32b1e829-a1e8-4638-8040-afb9bdba3b7a.jpg | 2013 | Does Not Function | No |  |  |  | Yes |  | Poor | -water point does not function because is not well located. -They are 2 distribution reservoirs, 1 is recent and is used to reinforce the existing one. | fbe8776afad7e5629a04cb34ec88318
ugds-fp0b-nate | 1 |  | J7 Rw24 | 1256650051 | 27-03-2017 08:27:23 CEST | Kabalisa Manzi Christella | 00:10:33 | 2017 | Rwanda | Rulindo | Kisaro | Murama | Kibingwe |  |  | Gahama Kisaro network | 10234 |  | 610 | 610 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6671501074688961 | 30.041830412153367 | 1945.4 | 24l5zh36 |  | Yes | 3 | Yes | 1 |  |  | 2012 | Normal | 3 | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 |  | https://waterforpeople.s3.amazonaws.com/images/9102b3af-4033-40a6-9f77-76e430437be7.jpg | 2012 | Normal | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Poor | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6264989081256989 | 30.02969897903348 | 2228.9 | 22px6zbc | 1 | https://waterforpeople.s3.amazonaws.com/images/b2511f90-e236-42a6-984e-41fa05d8fea9.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | The system has apump problem | 949def8ddb8dddbe59157da1c3ccd97f
cwuk-b2un-md53 | 1 |  | J7 Rw7 | 1232771186 | 24-03-2017 10:56:52 CET | Safari Bosco | 00:17:53 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo |  |  | marenge | 5544 |  | 203 | 203 | 0 | Yes | Piped Network with Pump |  | 1986 | No |  |  |  | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 1 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8219375023419242 | 30.059875485866172 | 1825.9 | 2bp56qgm | 1 | https://waterforpeople.s3.amazonaws.com/images/2270bd2c-e219-4b09-a461-dc6e31cf6bbc.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | f12c6f86e5e1734b6c62e79ab0347453
jmsg-sjm9-cxqv | 1 |  | J7 Rw10 | 1235980241 | 03-01-2015 01:27:51 CET | Tuyisenge Vianney | 00:06:25 | 2017 | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at ADEPR Buyoga/Nyirambuga pumping | 30604 |  | 177 | 177 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point at ADEPR Buyoga operates well though one tap stand valve was damaged | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.68568228350285 | 30.015822987374957 | 2137.5 | 25ft7ou6 | https://waterforpeople.s3.amazonaws.com/images/a4a96f5a-fd94-49ce-929d-c9eeac8a9d01.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.685660944699171 | 30.015831305051677 | 2112.1 | 25fs0tmm | 2 | https://waterforpeople.s3.amazonaws.com/images/e01aa5fe-5fda-495f-946e-661d94247439.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point at ADEPR Buyoga operates well though one tap stand valve was damaged | 6e81759f58b4c8eede7ae272cd39b90
13kg-1x2m-7wv3 | 1 |  | J7 Rw8 | 1215580797 | 10-03-2017 11:42:15 CET | Amani Desire | 00:17:17 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | Nganzo-Kabarore |  |  | 198 | 100 | 98 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | nkanga,kagwa | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8123160408683467 | 29.96796382144226 | 1787.1 | 2b98fpsv |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 20 | Yes | 1 |  | 2014 | Poor | 400 | Yes | 3 | -1.8123911178819008 | 29.967599969457293 | 1761.4 | 2b9d76mz |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Does Not Function | 800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8199450564434003 | 29.962194851629686 | 1684.5 | 2blupgbp | 5 | https://waterforpeople.s3.amazonaws.com/images/33a526ea-f3d8-4f96-a021-e51f549a8f21.jpg | 2014 | Does Not Function | Yes | 5 | 30 | The water and pipes are destroyed by the local population due to the unwillingness to buy water | No | The pipeline are broken | Does Not Function | -The water point at the source that is damaged but it is functioning -the pipeline is damaged, all distribution pipes are broken -there are no water at all water points | fcfca4e38019f2c3b0bb4fc3176aadca
9gwb-f178-ej2b | 1 |  | J7 Rw24 | 1252900066 | 28-03-2017 08:48:30 CEST | Kabalisa Manzi Christella | 00:05:28 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Rukore |  |  | Rwamugaza network | 14106 |  | 184 | 184 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  | https://waterforpeople.s3.amazonaws.com/images/0d25054c-890a-4bb0-8d79-99cf754f6f31.jpg | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8010272970538554 | 30.114340574308645 | 1593.8 | 2aqk9cyf | 1 | https://waterforpeople.s3.amazonaws.com/images/413435ca-c8d8-4cde-982b-b7588e11d957.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | b641679329113344c3ff7c297232
c7w1-e2wa-pn9n | 1 |  | J7 Rw10 | 1312370051 | 20-04-2017 08:16:53 CEST | Tuyisenge Vianney | 00:06:11 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Rusura |  |  | Water point chez Ntihabose/Nyirambuga pumping | 30604 |  | 157 | 157 | 0 | Yes | Piped Network with Pump |  | 2012 | Yes | Gatare and Rusura |  |  | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.685738204816077 | 29.94482048293456 | 1969.4 | 25fw6ubc | 2 | https://waterforpeople.s3.amazonaws.com/images/40baaf09-b992-468f-8e40-da04981aa7a5.jpg | 2012 | Poor | No |  |  |  | Yes |  | Poor | operational | 75115726fad41332af23cc854859e3fa
upp5-duc2-9xsc | 1 |  | J7 Rw19 | 1236751031 | 23-03-2017 12:00:37 CET | Kayinamura Innocent | 00:11:53 | 2017 | Rwanda | Rulindo | Masoro | Kabuga | Kigarama |  |  | Mutagata motorised network | 26296 |  | 176 | 81 | 95 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.8018522287450358 | 30.042875565044753 | 4708.3 | 2arxobm4 |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7813273923289477 | 30.054835548790606 | 1807.4 | 29tzdero | 64 | https://waterforpeople.s3.amazonaws.com/images/a4f1a261-a7ff-4b2d-8bb6-bcc2b93a3819.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | f51495e12f040e57dc6f369a35954a
8334-87vg-qrk | 1 |  | J7 Rw10 | 1299180126 | 15-04-2017 23:07:41 CEST | Tuyisenge Vianney | 00:09:24 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Kabuye |  |  | Ruganzu-Kabuye gravity system |  |  | 169 | 169 | 0 | Yes | Piped Network -- Gravity Only |  | 2010 | No |  | Private operator and local government | This water point and its storage do no longer due to water pipeline to make Kabuye spring.It had been constucted for the reason behind of joining water from Ruhaganzu-Kabuye to gather them in the water tank to pump it for the use not specified.But the private operator failed | 1 | Spring | -1.793183384812883 | 29.929966020487782 | 2001 | 2adlhh9f | https://waterforpeople.s3.amazonaws.com/images/5f421a4d-f236-4ff5-ab9b-6deebe9700b0.jpg | Yes | 0 | No | [5 empty] | 0 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/5747059e-49ae-4b71-b1d7-8b6dc637af83.jpg | 2010 | Does Not Function | 100 | Yes | 1 | -1.7934405318681477 | 29.93023175095219 | 2011.7 | 2ae0yqzq | https://waterforpeople.s3.amazonaws.com/images/4f7a3f50-fdef-458b-8c5a-2bdd0f58bc7c.jpg | 2010 | Does Not Function | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7935238074015345 | 29.930250047711077 | 2013.5 | 2ae5q7ty | 0 | https://waterforpeople.s3.amazonaws.com/images/154d1f02-722d-43b9-aa5f-e3bfe3e96884.jpg | 2010 | Does Not Function | No |  |  |  | No | This water point and its storage do no longer due to water pipeline to make Kabuye spring.It had been constucted for the reason behind of joining water from Ruhaganzu-Kabuye to gather them in the water tank to pump it for the use not specified.But the private operator failed | Does Not Function | This water point and its storage do no longer due to water pipeline to make Kabuye spring.It had been constucted for the reason behind of joining water from Ruhaganzu-Kabuye to gather them in the water tank to pump it for the use not specified.But the private operator failed | 3c16838ee2ad1c4cd7568eab2a9a412
s38x-uyw9-rgn | 1 |  | J7 Rw10 | 1219170078 | 15-03-2017 19:19:31 CET | Tuyisenge Vianney | 00:13:18 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Gatsinde |  |  | Gatsinde wpt/Nyirambuga | 30604 |  | 178 | 178 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | GoR | The water point has been constructed very soon.Water comes rarely.When water is not present they fetch from Buramira water points | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.6733940469827326 | 29.927545746351655 | 1830.8 | 24vhhxor | https://waterforpeople.s3.amazonaws.com/images/0ce7a800-9fbd-4c2d-8fc4-b863b647ba5f.jpg | 2012 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.673320098631946 | 29.927555503990455 | 1818.5 | 24vdbwgb | 1 | https://waterforpeople.s3.amazonaws.com/images/945614d1-5b52-4320-94d9-82954a0cb9c1.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | The water point has been constructed very soon.Water comes rarely.When water is not present they fetch from Buramira water points | b7e551ae62a244d28fe92f7f9c7fcf2
wyjt-wmbv-t8u1 | 1 |  | J7 Rw26 | 1197360204 | 07-03-2017 09:08:02 CET | Byukusenge Elie | 00:52:22 | 2017 | Rwanda | Rulindo | Cyungo | Marembo | Buyaga |  |  | Mugomero Marembo | 3456 |  | 652 | 602 | 50 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | Kidomo, Gahinga,Nganzo, Rusayo, Buyaga and Murambo | Governement (District, WASAC) and Water For People | The source of this network is located in Burera District and this network serves three villages in Burera and It has eight water point in Burera and Starting chamber and one reservoir are also located in Burera District, Ruhunde sector | 1 | Spring | -1.577749646341437 | 29.93714072556937 | 2147.8 | 20haqsiz | https://waterforpeople.s3.amazonaws.com/images/260b7fd0-d966-41c3-84b8-b4337ba208b5.jpg | Yes | 120 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/4fc7260f-ec70-4637-99b8-f5694696f416.jpg | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 120 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/9eac983e-e568-475e-9238-20a94847415e.jpg | 2015 | Normal | 10000 | Yes | 10 | -1.5961706844323926 | 29.91257085345822 | 2085.4 | 21bs0o8l | https://waterforpeople.s3.amazonaws.com/images/695c9b26-05e0-4b39-bc34-c4e3df7e54e8.jpg | 2015 | Normal | Yes | 3 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/21e37054-349b-4eae-b641-a77321b806e8.jpg | 2015 | Normal | Yes | 2 |  | 2015 | Normal | 10000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.5961297362642575 | 29.912692154444738 | 2081.1 | 21bp1i7q | 8 | https://waterforpeople.s3.amazonaws.com/images/3d890403-f9d5-4cb9-afc9-f1de41557205.jpg | 2015 | Poor | No |  |  |  | Yes |  | Normal | This network is in good conditions as it was constructed in 2015 most ofhydraulic structures are in good condtion but the served popolation does not fetch water as i did not found anyone on the water tap or the hour of using water tap was at thr morning and at the evening | a5286e39f43978413f8662749f5a1db3
njv4-sxqn-phv | 1 |  | J7 Rw10 | 1317650258 | 20-04-2017 06:58:55 CEST | Tuyisenge Vianney | 00:05:21 | 2017 | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point at APEKI Accommodation/Nyirambuga pumping | 30604 |  | 115 | 115 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | Yes | 1 | -1.7082982494594126 | 29.952305626009778 | 2213.9 | 26h7cr43 | https://waterforpeople.s3.amazonaws.com/images/3653029d-d2c7-493c-8738-4f8dff3ad8f8.jpg | 2012 | Normal | No | [5 empty] | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/74b09de8-f3dc-4d98-987e-af0b2541d1c5.jpg | 2012 | Normal | 100 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7085589491927757 | 29.951862005950726 | 2205 | 26hmu0u6 | 6 | https://waterforpeople.s3.amazonaws.com/images/ec2e596b-ec06-4eb5-824d-c7c874b9219a.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Operational | ae868cc3f636691f1af58b2076bda1
uscc-b7nq-pc8y | 1 |  | J7 Rw10 | 1320480057 | 20-04-2017 08:06:03 CEST | Tuyisenge Vianney | 00:04:52 | 2017 | Rwanda | Rulindo | Tumba | Misezero | Karambi |  |  | Water point chez Nkurunziza/Nyirambuga pumping | 30604 |  | 160 | 160 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6874816102085595 | 29.954745373595863 | 1941.8 | 25isdp97 | 2 | https://waterforpeople.s3.amazonaws.com/images/4616d7e1-75ae-48f4-a8ff-f86ff2c5f24a.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | operational | 577763c0d9c3abc21371a45f6237151d
5uyu-h254-yt1s | 1 |  | J7 Rw19 | 1234360974 | 23-03-2017 12:23:50 CET | Kayinamura Innocent | 00:07:56 | 2017 | Rwanda | Rulindo | Masoro | Kabuga | Gisiza |  |  | Mutagata motorised network | 26296 |  | 135 | 135 | 0 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.801852228745035 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7776288017050865 | 30.06249784576791 | 1691.1 | 29nv3100 | 64 | https://waterforpeople.s3.amazonaws.com/images/ae3ae062-38c6-4b5e-831e-26b9fc8c302a.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 31231943a4070586e3d38f922952613
xt39-vnm1-t2je | 1 |  | J7 Rw7 | 1448800418 | 06-06-2017 16:22:15 CEST | Rugirangoga Augustin | 00:46:32 | 2017 | Rwanda | Rulindo | Kisaro | Murama | Akamanama |  |  | kano |  |  | 141 | 120 | 21 | Yes | Piped Network with Pump |  | 2012 | Yes | ruberano gashinge kibingwe akamanama rutabo | waterforpeople |  | 2 | Spring | -1.6675834297797398 | 30.0428712210569 | 1965.7 | 24lvl43w |  | Yes | 15 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 15 | No | [5 empty] | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 | Sedimentation Tank¦Pressure Break Tank¦Distribution Chamber¦null |  | 1998 | Normal | Yes | 2 |  | 2012 | Normal | 30000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6445025783544662 | 30.049059935806834 | 2033.3 | 23jpgnyi | 1 | https://waterforpeople.s3.amazonaws.com/images/196cf887-126c-4b62-b027-7a611c40c0f6.jpg | 1998 | Normal | Yes | 1 | 3 | ntawo wapfuye ahubwo amazi ntabwo ahagera | No | ntabwo amazi ahari kuko amazi bayabona kabiri mu cyumwr | Normal |  | 7e530411bfc1f565d633af6b5c87114
m1je-7qq9-q5mx | 1 |  | J7 Rw10 | 1299130059 | 14-04-2017 22:24:50 CEST | Tuyisenge Vianney | 00:04:47 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Budaha |  |  | Budaha water point/Nkome gravity system |  |  | 205 | 205 | 0 | Yes | Piped Network -- Gravity Only |  | 2002 | No |  | COFORWA | This is water point located in Budaha at the peak opposite to Gitwa and above of Mukoto and Gasiza.It operates well with enough water | 1 | Spring | -1.726263209282846 | 29.90351686333194 | 2121.4 | 27ax8ot7 |  | Yes | 18 | No | [5 empty] | 18 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.721794645622152 | 29.91574411308969 | 1938.4 | 273j3xhx | 1 | https://waterforpeople.s3.amazonaws.com/images/58c6dfc6-cc4c-4d72-875e-6dd1c88f269d.jpg | 2002 | Normal | No |  |  |  | Yes |  | Normal | This is water point located in Budaha at the peak opposite to Gitwa and above of Mukoto and Gasiza.It operates well with enough water | f38327c0c99ff1309847eaa5edd077b9
ercf-627c-157s | 1 |  | J7 Rw7 | 1241000857 | 24-03-2017 12:35:27 CET | Safari Bosco | 00:11:57 | 2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Marembo |  |  | marenge | 5544 |  | 173 | 173 | 0 | Yes | Piped Network with Pump |  | 1998 | No |  |  |  | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 1 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.832540941310944 | 30.057314414301374 | 1794.9 | 2c6ovna5 | 2 | https://waterforpeople.s3.amazonaws.com/images/0c9425f6-6cf9-4990-9f55-8cb3add26cbf.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 75c1a7ec7622c382f18153f5231c9e48
tgfu-j5u9-2yqw | 1 |  | J7 Rw26 | 1235770608 | 21-03-2017 14:06:52 CET | Byukusenge Elie | 00:05:31 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Murwa |  |  | Kabonanyoni | 7894 |  | 75 | 70 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6518203003417284 | 29.969810591161053 | 1785.1 | 23vt9y5u | 31 | https://waterforpeople.s3.amazonaws.com/images/26ca85ed-a890-4c15-a95d-b17037fa55b5.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water tap is near adepr kabingo and the community use it. | c5ae27137a8329756d5ec698e41fa71
ebap-g8kg-bd5b | 1 |  | J7 Rw15 | 1204330395 | 08-03-2017 20:36:51 CET | Mukakarangwa Assoumpta | 00:08:11 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | kinywamagana pumping network | 6436 |  | 281 | 50 | 231 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 28 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse;,Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8398990010142395 | 29.954174901922237 | 1986 | 2ciuh845 | 1 | https://waterforpeople.s3.amazonaws.com/images/6bf86f65-94bd-488a-90f6-b9b0fa36ffa4.jpg | 2013 | Does Not Function | No |  |  |  | Yes |  | Poor | water point does not function because is not well located | 3be82e92a946b1bdfcd0a49328fbf45
k07d-rg0m-kf35 | 1 |  | J7 Rw23 | 1236140572 | 23-03-2017 06:28:54 CET | Rugirangoga Augustin | 00:19:08 | 2017 | Rwanda | Rulindo | Buyoga | Gitumba | Remera |  |  | Kiruruma | 8295 |  | 130 | 126 | 4 | Yes | Piped Network with Pump |  | 2014 | Yes | rutabo gitaba nyarubuye remera rusongati rugarama cyasuli munini | Governement (District, WASAC) and Water For People | this network is working well | 1 | Groundwater (well, etc.) | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 15 | -1.6684773741137722 | 30.047381335897573 | 1775.8 | 24nckozd |  | 2014 | Normal | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6778144207237706 | 30.031002268865322 | 2105.1 | 252snjva | 2 | https://waterforpeople.s3.amazonaws.com/images/7393c443-f109-4183-8b08-a7200831643f.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | the network itself works very well | 4e7cd8ec5bb37f65430e13283dab5b0
d1hb-5sa7-199n | 1 |  | J7 Rw26 | 1213120083 | 11-03-2017 10:23:15 CET | Byukusenge Elie | 00:10:28 | 2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 20456 |  | 45 | 40 | 5 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank |  | 2 | Spring | -1.592031897072486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6417435543237726 | 29.944686104759683 | 1835.8 | 23f5506u | 29 | https://waterforpeople.s3.amazonaws.com/images/c7fb4a69-1125-4a18-9c6e-254292b6c509.jpg | 2011 | Poor | Yes | 10 | 22 | Bad tee connections and the types of pipeline needs rehabilitation | No | Pipeline to water tap has damaged. | Poor | The distribution reservoir has water but the pipeline to water tap has damaged and the People use the reservoir washout to fetch water. | a4a862cf75eb19dfaf512e9ac8913619
ehmh-kjkv-3d16 | 1 |  | J7 Rw15 | 1428200279 | 02-06-2017 06:24:37 CEST | Mukakarangwa Assoumpta | 00:10:43 | 2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Kayenzi |  |  | Rwamugaza | 14106 |  | 200 | 20 | 180 | Yes | Piped Network -- Gravity Only |  | 2003 | Yes | All villages of Ntarabana sector | Goverment |  | 2 | Spring | 1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | 1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 | Sedimentation Tank |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.774552334588581 | 30.091234359407185 | 1665.2 | 29isayi8 | 1 | https://waterforpeople.s3.amazonaws.com/images/de20de00-27e4-4f18-a1c1-4e092b2ff35d.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | f128d7cf674fa743ce941081fad1eba4
krth-v4wb-mpfx | 1 |  | J7 Rw7 | 1235290794 | 24-03-2017 12:23:10 CET | Safari Bosco | 00:08:43 | 2017 | Rwanda | Rulindo | Masoro | Nyamyumba | Kabuga | [5 empty] | 119 | 119 | 0 | Yes | Piped Network with Pump |  | 1998 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8134538660783146 | 30.0478239876776 | 1842.2 | 2bb4b5dq | 2 | https://waterforpeople.s3.amazonaws.com/images/67b29b6d-c965-4951-9c5d-d08a21f1894b.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 9dcfa044ffbecb8bf5347bdc35546c81
ky88-nd4u-yx1u | 1 |  | J7 Rw15 | 1207840388 | 09-03-2017 22:14:51 CET | Mukakarangwa Assoumpta | 00:09:31 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kirurumo |  |  | Bitete-Rwahi network | 1316 |  | 80 | 35 | 45 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.8336417737979869 | 29.94346668826428 | 1815.5 | 2c8iday2 |  | Yes | 12 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 |  | 2013 | Normal | 600 | Yes | 6 | 1.8427360326225883 | 29.938932546871705 | 1676.5 | 2cnjkbst |  | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8386354213248237 | 29.94238338618494 | 1708.3 | 2cgrglsv | 1 | https://waterforpeople.s3.amazonaws.com/images/ce42789c-1a92-42c5-953c-2483d8762378.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | c774d67af842625847aaacfd84dabbc
1ta5-6ujw-fkb2 | 1 |  | J7 Rw19 | 1194261443 | 07-03-2017 14:13:07 CET | Kayinamura Innocent | 00:28:33 | 2017 | Rwanda | Rulindo | Mbogo | Mushali | Rwambogo |  |  | Rwambogo Extension network | 934 |  | 69 | 69 | 0 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | iyi Extension ifatiye ku suction Tank ya Kararama pumping network | 2 | Spring | -1.750453987388797 | 29.98652462808167 | 1902.5 | 28exg9sp | https://waterforpeople.s3.amazonaws.com/images/be07ef18-daf8-4645-92b0-188248c0d52d.jpg | Yes | 3 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/991b59f6-6270-4276-aa2d-911a2fdb4340.jpg | Suction Tank | 2009 | Poor | 3 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/8620f4d8-661f-48fd-97fb-80c598b09fec.jpg | 2016 | Normal | 600 | Yes | 1 | -1.7529486605134463 | 29.980553209749576 | 1837.4 | 28j1p7dp | https://waterforpeople.s3.amazonaws.com/images/9241a931-4138-4d18-b677-e4f7f0dc9465.jpg | 2016 | Normal | Yes | 1 | Washout chamber |  | 2016 | Normal | Yes | 1 |  | 2016 | Does Not Function | 100 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7527987008402517 | 29.980766021054947 | 1849.4 | 28isrpb3 | 1 | https://waterforpeople.s3.amazonaws.com/images/53e81dd5-68df-4305-80a9-d38e69c8164b.jpg | 2016 | Normal | No |  |  |  | No | Road construction destroyed some pipes | Does Not Function | Water is not Flowing because pipes were destroyed during road construction | 78362a3c96e1133b6cc33cfec703287
k4sq-vt7j-7v2d | 1 |  | J7 Rw23 | 1214890494 | 15-03-2017 06:06:37 CET | Rugirangoga Augustin | 00:21:17 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Kiruli |  |  | Migogo | 558 |  | 223 | 200 | 23 | Yes | Piped Network -- Gravity Only |  | 2009 | Yes | kiruli kabahama bukangano | padiri(LAKE ANGELS). |  | 1 | Groundwater (well, etc.) | -1.6327309674421784 | 29.901262305566668 |  | 2308pft0 |  | Yes | 50 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2009 | Poor | 50 | Yes | 1 |  | 2009 | Poor | 6800 | Yes | 3 | -1.6327309674421784 | 29.901262305566668 | 1900.3 | 2308pft0 |  | 2009 | Poor | No | [5 empty] | Yes | 1 |  | 2009 | Poor | 6800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6414496283051552 | 29.900113563614667 | 1760.3 | 23en9zp5 | 2 | https://waterforpeople.s3.amazonaws.com/images/7f34e164-ba12-4b8a-8307-37dc2e24ee4e.jpg | 2009 | Normal | No |  |  |  | Yes |  | Poor | this network requires rehabilitation | 206b42214681418ac593695388bec
h6mk-2evm-0qq0 | 1 |  | J7 Rw15 | 1204890568 | 08-03-2017 22:49:44 CET | Mukakarangwa Assoumpta | 00:06:12 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Nyabisindu |  |  | kirikumuryango network |  |  | 149 | 62 | 87 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Poor | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8951063738644407 | 29.974232980820837 | 1397.7 | 2f25jf4u | 1 | https://waterforpeople.s3.amazonaws.com/images/2e316160-31a4-4b2d-82db-88da2f0c1468.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 7d304c10858afb48c146d84199e128c1
1jmh-yre6-df17 | 1 |  | J7 Rw15 | 1207840173 | 08-03-2017 20:02:18 CET | Mukakarangwa Assoumpta | 00:06:20 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gatimba |  |  | kinywamagana pumping network | 6436 |  | 217 | 180 | 37 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8508238856271528 | 29.968016302997032 | 1911.5 | 2d0x80f4 | 1 | https://waterforpeople.s3.amazonaws.com/images/eb528644-e593-47a0-974f-53817648e82a.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | 35e0960d0e0898ea7adf078434c7183
n83q-cupe-y9cw | 1 |  | J7 Rw26 | 1237050149 | 21-03-2017 13:49:17 CET | Byukusenge Elie | 00:07:16 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Rukingu |  |  | Kabonanyoni | 7894 |  | 100 | 95 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6348830448501364 | 29.958021429293154 | 2146.9 | 233spnb0 | 31 | https://waterforpeople.s3.amazonaws.com/images/3d20c61e-58d0-4288-ba77-62fed196fddc.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is in good condition. | 6dbc779753fbc9c9e3eca624dc9233
k2g7-9ju6-jbwa | 1 |  | J7 Rw10 | 1211230774 | 14-03-2017 22:59:23 CET | Tuyisenge Vianney | 00:08:59 | 2017 | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Kingazi 2water point/Nyakabizi1&2 | 1259 |  | 157 | 157 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | The water point operates well.However the quantity of water and irregular supply cause people to complain. | 2 | Spring | -1.803447729664134 | 29.930708856826865 | 1927.1 | 2aukc7xn |  | Yes | 20 | No | [5 empty] | 20 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8078578041429791 | 29.92229517331549 | 1820.3 | 2b1uwdna | 1 | https://waterforpeople.s3.amazonaws.com/images/dd5b3aa9-2aa7-4ad6-a837-a1f8a3202e83.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | The water point operates well.However the quantity of water and irregular supply cause people to complain. | 3ebce2b6d5ff1e5dfafe1c21ca98f3b6
mcgm-0x8s-rkfq | 1 |  | J7 Rw26 | 1203650446 | 01-01-2015 19:57:53 CET | Byukusenge Elie | 00:13:55 | 2017 | Rwanda | Rulindo | Cyungo | Rwili | Nyabisasa |  |  | Sakara |  |  | 570 | 520 | 50 | Yes | Piped Network with Pump |  | 2016 | Yes | Kivumu Nturo and sakara | Governement (District, WASAC) and Water For People | it has source Nyamagana shared with Nyamagana gravity and it was constructed in 2015 and the extensions in Kivumu and Nyabisasa villages was constructed in 2016 and it is not yet used by the community and the pumping station use main distribution reservoir of Nyamagana gravity as suction reservoir | 2 | Spring | -1.59199473719814 | 29.923957502559304 | 2015.8 | 214v5hgn |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1200 | Yes | 2 | -1.6031327757439937 | 29.9227092844118525 | 2131.4 | 21naedcr |  | 2015 | Normal | Yes | 5 | Distribution Chamber |  | 2015 | Normal | Yes | 1 |  | 2016 | Normal | 2300 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.5977421824725995 | 29.9224937358659 | 2117 | 21edhqag | 4 | https://waterforpeople.s3.amazonaws.com/images/360bad4d-7426-4c20-9326-d0242c06071a.jpg | 2016 | Normal | No |  |  |  | No | the network is not yet used by the community because it is under construction | Normal | This is the extension og sakara network to Nyabisasa village and it is almost finished | 9c134cfbf4c75b5e97408a703ec92d
bnhu-x684-8y3v | 1 |  | J7 Rw24 | 1224070202 | 16-03-2017 05:58:45 CET | Kabalisa Manzi Christella | 00:08:06 | 2017 | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 14106 |  | 495 | 495 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | No Problem with the Water Point | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  | https://waterforpeople.s3.amazonaws.com/images/18b4fe01-6f3d-4c4a-aec9-d4b41dbfd149.jpg | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7391845049957506 | 30.037366319242484 | 2002.9 | 27wagrf9 | 1 | https://waterforpeople.s3.amazonaws.com/images/c91b9772-4c00-49c5-a0a5-8d360a6c754c.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | 4fadb76ad71dbce835a74a6899641438
kjfn-6k7q-u4wt | 1 |  | J7 Rw8 | 1213330052 | 10-03-2017 11:17:20 CET | Amani Desire | 00:28:40 | 2017 | Rwanda | Rulindo | Ngoma | Kabuga | Kirambo |  |  | Nganzo-Kabarore |  |  | 131 | 43 | 88 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | nkanga,kagwa | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8123160408683467 | 29.96796382144226 | 1787.1 | 2b98fpsv |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Does Not Function | 20 | Yes | 2 |  | 2014 | Poor | 400 | Yes | 3 | -1.8123911178819008 | 29.9675999457293 | 1761.4 | 2b9d76mz |  | 2014 | Normal | No | [5 empty] | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/35827e28-6d9e-48df-9325-edf4c76f5d1b.jpg | 2014 | Does Not Function | 800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.813946336683523 | 29.96028205290959 | 1658 | 2bbxhdci | 5 | https://waterforpeople.s3.amazonaws.com/images/6e845028-4761-441c-9e51-99ccb42abc88.jpg | 2014 | Does Not Function | Yes | 5 | 30 | The pipes have been damaged and broken | No | the pipes connecting water to this water point is broken | Does Not Function | -the water point at the source is damaged but it is functioning -the pipeline is damaged, all distribution pipes are broken -there are no water at all water points | e0ef1f5926f3e51d9512c8866774d3
umtc-07jd-h0dn | 1 |  | J7 Rw7 | 1229010385 | 24-03-2017 11:25:11 CET | Safari Bosco | 00:10:48 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Nyakibungo | [5 empty] | 229 | 229 | 0 | Yes | Piped Network with Pump |  | 1998 | No |  |  |  | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8167907037760107 | 30.067496631305374 | 1732.5 | 2bgn5xky | 2 | https://waterforpeople.s3.amazonaws.com/images/bf89b51b-24de-4c77-ba65-5014156b3277.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 44b06d7d736e3af297f0234246855e4d
qqsp-83jb-6tab | 1 |  | J7 Rw8 | 1238250111 | 23-03-2017 09:58:08 CET | Amani Desire | 00:10:14 | 2017 | Rwanda | Rulindo | Murambi | Mvuzo | Kabuga |  |  | Mutagata Motorised Network | 26296 |  | 199 | 98 | 101 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.801852287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8134155619206984 | 30.01682322712619 | 1801.6 | 2bb1xeq0 | 64 | https://waterforpeople.s3.amazonaws.com/images/991be474-abde-4682-9bbd-fe658a10f2d8.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | dd548af0e58e2b66247c623e9fdd675
vxvd-cvh3-q6aa | 1 |  | J7 Rw8 | 1232071096 | 23-03-2017 12:14:43 CET | Amani Desire | 00:13:56 | 2017 | Rwanda | Rulindo | Murambi | Bubangu | Nyagisozi |  |  | Gakoma network | 7108 |  | 154 | 154 | 0 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | nyagisozi |  |  | 2 | Spring | -1.820504948163801 | 30.02259538436087 | 1687.1 | 2bms1qo1 |  | Yes | 9 | No | [5 empty] | 9 | No | [5 empty] | Yes | 2 | -1.8204311991738096 | 30.02203801775231 | 1655.6 | 2bmnvpfg |  | 2004 | Normal | No | [5 empty] | Yes | 1 |  | 2004 | Poor | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8371374756784704 | 30.019122131675243 | 1651.4 | 2cea5lnj | 2 | https://waterforpeople.s3.amazonaws.com/images/db2919c9-b2e6-4741-9be5-73a340c487c2.jpg | 2004 | Normal | No |  |  |  | Yes |  | Normal | 1.the system has 6 water points with 2 located in Rulindo district and other in in Gasabo district in Jabana sector 2. in Rulindo only one water point is functinal the other is distroyed | 352ef1262ccbd734b411154e93d4b5d
hp1u-spja-4ng6 | 1 |  | J7 Rw10 | 1223450279 | 13-03-2017 21:02:07 CET | Tuyisenge Vianney | 00:09:09 | 2017 | Rwanda | Rulindo | Base | Gitare | Gihora |  |  | Gihora Water point/Rutomvu gravity system | 3015 |  | 101 | 101 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | This is water point located in Gihora of Base supplied by Rutomvu gravity system | 1 | Spring | -1.677891751247546 | 29.90118126071259 | 1802.6 | 252xezpf |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | Yes | 1 | -1.664093562921035 | 29.890251371173587 | 1730.5 | 24g3sst2 | https://waterforpeople.s3.amazonaws.com/images/5c5f544e-d6d2-4e75-840c-992419f75d0b.jpg | 2013 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6642910998768163 | 29.89040787924969 | 1729.4 | 24gfpgwo | 1 | https://waterforpeople.s3.amazonaws.com/images/ec35d4fb-f890-4b88-8948-c8052cf80248.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | This is Gihora water point supplied by Rutomvu gravity | f814627e6c4a9f4ada5b4ff75c3e1244
vm2n-sdw4-dkqr | 1 |  | J7 Rw15 | 1204890550 | 08-03-2017 22:01:02 CET | Mukakarangwa Assoumpta | 00:17:24 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Mwagiro |  |  | Kirikumuryango network |  |  | 139 | 20 | 119 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y | https://waterforpeople.s3.amazonaws.com/images/19c04f67-a522-4abf-a271-9b3209b91411.jpg | Yes | 11 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/6bb0a396-4e0a-44e5-ae61-dd6721fb7b97.jpg | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/e0fe4556-91c2-426b-ae04-e942914446d1.jpg | 2013 | Normal | 500 | Yes | 17 | -1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 | https://waterforpeople.s3.amazonaws.com/images/11bcf455-8d97-4df9-91ae-c073a8b160c7.jpg | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout | https://waterforpeople.s3.amazonaws.com/images/1e597876-0072-48c3-9fb0-53be67be8992.jpg | 2013 | Normal | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/530486a4-5017-4f54-95c2-8feaa0ad73ba.jpg | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.873582047401951 | 29.976396257654002 | 1682.1 | 2e2kalbn | 1 | https://waterforpeople.s3.amazonaws.com/images/b13558a7-9986-45c0-80dd-39ee139979d6.jpg | 2013 | Poor | No |  |  |  | Yes |  | Normal |  | 14c68156351b175285cfcdd7008054
9em4-qb9y-5bj5 | 1 |  | J7 Rw24 | 1226531211 | 16-03-2017 07:11:39 CET | Kabalisa Manzi Christella | 00:08:55 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Kisigiro |  |  | Rwamugaza | 14106 |  | 605 | 605 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | no problem | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7411311408107093 | 30.045434996607206 | 1905.9 | 27zikag6 | 1 | https://waterforpeople.s3.amazonaws.com/images/fcb0f646-56e6-4fe6-9ace-d6975c85500a.jpg | 2012 | Normal | No |  |  |  | No | Water seller was not around | Normal | no problem | 1e33ec9bb91a53b974aa7d793e19e9b
sj6d-6t3m-smrm | 1 |  | J7 Rw8 | 1214820171 | 10-03-2017 11:04:35 CET | Amani Desire | 00:14:18 | 2017 | Rwanda | Rulindo | Ngoma | Karambo | Kagwa |  |  | Nganzo-Kabarore |  |  | 123 | 44 | 79 | Yes | Piped Network -- Gravity Only |  | 2014 | No |  |  |  | 1 | Spring | -1.812316048683467 | 29.96796382144226 | 1787.1 | 2b98fpsv |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 20 | Yes | 1 |  | 2014 | Poor | 400 | Yes | 3 | -1.8123911178819008 | 29.967599969457293 | 1761.4 | 2b9d76mz |  | 2017 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Does Not Function | 800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8425063672420168 | 29.987530146503495 | 1587.6 | 2cn5vd9f | 5 | https://waterforpeople.s3.amazonaws.com/images/7c4de929-cc0b-488b-902b-81a28334f365.jpg | 2014 | Poor | Yes | 5 | 30 | The pipes are broken | No | Dustribution Pipes are broken | Does Not Function | -Water point at the source is damaged but it is functioning -the pipeline is damaged, all distribution pipes are broken -there are no water at all water points served by garavity by nganzo source | faeee66c6c1f6e26fcda7b46275ddbdf
3hut-66bb-73t1 | 1 |  | J7 Rw19 | 1210130224 | 13-03-2017 06:52:35 CET | Kayinamura Innocent | 00:44:29 | 2017 | Rwanda | Rulindo | Ngoma | Mugote | Kiboha |  |  | Kabarore-Ngoma-Nyabuko network | 8284 |  | 74 | 39 | 35 | Yes | Piped Network with Pump |  | 2014 | Yes | Nyabuko, Kagwa, Kiruri, Busizi, Ngaru, Kirungu, kiboha and Kigina | Governement (District, WASAC) and Water For People | The network has 17 water points and it serves 8 villages | 4 | Spring | -1.8123357076877174 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦Collection Chamber | 2014 | Normal | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.8118879629206273 | 30.003478805087482 | 2031 | 2b8iu32a |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 4 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8135057279710969 | 30.004290086025296 | 2008.1 | 2bb7ab2i | 17 | https://waterforpeople.s3.amazonaws.com/images/e07e44a1-3eb9-466e-a96e-f77cacdc11f6.jpg | 2014 | Normal | Yes | 1 | 10 | it was due to the road Construction | Yes |  | Normal | - The network has 17 water points -water points are in good operation conditions except the water point at the source that is damaged - 4 water points don't have water today -The pipe are in good conditions - The pump is not working properly as it was expected during Design, today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy - the transformer at the pumping station doesn't offer the required energy for the pump -the anti-hammers of pumps are not functioning because of bad installation of pumping house - the system has 4 pumps units with two units pumping in one direction towards Nyabuko, towards Ngoma sector office - the suction tank is in bad physical condition | 59dfe271f46ac2307855204330e89a7a
h34a-sx8p-qwx7 | 1 |  | J7 Rw23 | 1207320716 | 12-03-2017 18:41:26 CET | Rugirangoga Augustin | 00:17:21 | 2017 | Rwanda | Rulindo | Base | Gitare | Kirwa |  |  | Rwicanyoni | 698 |  | 116 | 113 | 3 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | kirwa gatete gisiza | Governement (District, WASAC) and Water For People | the network is new | 2 | Spring | -1.6644377224987001 | 29.903649586570488 | 1928 | 24go1jh8 |  | Yes | 15 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 10 | Yes | 1 |  | 2016 | Normal | 8600 | Yes | 3 | -1.6605194594779042 | 29.90927074216649 |  | 24a6nmdw |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6533326511026156 | 29.881954830704643 | 1723.5 | 23yb6dtv | 2 | https://waterforpeople.s3.amazonaws.com/images/5f70849b-44bc-4fbc-96c8-c0a798520e6d.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 5d3589a3edc420821c0cc283d523916
ca4n-mvdj-0321 | 1 |  | J7 Rw26 | 1437510050 | 02-06-2017 09:32:31 CEST | Byukusenge Elie | 00:11:53 | 2017 | Rwanda | Rulindo | Cyinzuzi | Rudogo | Gasiza |  |  | Rwagitare | 0 |  | 76 | 66 | 10 | Yes | Piped Network -- Gravity Only |  | 2009 | No |  | Water For People |  | 1 | Spring | -1.7644810500752824 | 30.007563048175167 | 1783.6 | 2924rfor |  | Yes | 1.2 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2009 | Normal | 1.2 | Yes | 1 |  | 2009 | Normal | 1200 | Yes | 1 | -1.7744810500852932 | 30.017663038155167 | 1697.6 | 29io4wpc | https://waterforpeople.s3.amazonaws.com/images/6c3b26be-039c-4926-9446-8b25de76dc3b.jpg | 2009 | Normal | Yes | 2 | Pressure Break Tank¦Distribution Chamber |  | 2009 | Normal | Yes | 1 |  | 2009 | Normal | 900 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7760311551180596 | 30.01549783374963 | 1709.7 | 29l8f3ga | 2 | https://waterforpeople.s3.amazonaws.com/images/7b625257-ecd4-4cd8-a2c3-f1078e9a2304.jpg | 2009 | Normal | No |  |  |  | Yes |  | Normal |  | 3d44bb89903b243db11965fc955c7fa
jdmy-f3n2-dm79 | 1 |  | J7 Rw23 | 1231190481 | 23-03-2017 06:26:13 CET | Rugirangoga Augustin | 00:37:49 | 2017 | Rwanda | Rulindo | Buyoga | Gahororo | Shagasha |  |  | Kiruruma | 8295 |  | 209 | 200 | 9 | Yes | Piped Network with Pump |  | 2014 | Yes | rutabo gitaba nyarubuye remera rusongati rugarama cyasuli munini shagasha | Governement (District, WASAC) and Water For People |  | 1 | Groundwater (well, etc.) | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 15 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2014 | Normal | Yes | 5 | Pressure Break Tank |  | 2014 | Normal | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.712559753881015 | 30.0631932844799 | 1809.6 | 26o8zfo7 | 2 | https://waterforpeople.s3.amazonaws.com/images/3f77a978-d37e-4f27-b6f6-987db478001d.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal |  | 46908fcad1a399b3ad4ae8787c7ee18
dr08-eppu-9j9x | 1 |  | J7 Rw10 | 1314210078 | 20-04-2017 09:33:33 CEST | Tuyisenge Vianney | 00:05:44 | 2017 | Rwanda | Rulindo | Tumba | Misezero | Karambi |  |  | Water point chez Nkurunziza/Nyirambuga pumping | 30604 |  | 160 | 160 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | Yes | 1 | -1.6911711948132704 | 29.95632644608825 | 2030.5 | 25ow2nhn | https://waterforpeople.s3.amazonaws.com/images/8996806e-530c-433f-8b01-0b209294093d.jpg | 2017 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6875043712335518 | 29.954761641960303 | 1958.9 | 25itkkgr | 1 | https://waterforpeople.s3.amazonaws.com/images/912187b7-2b5d-42b7-a373-0fece908adb0.jpg | 2017 | Poor | No |  |  |  | Yes |  | Normal | operational | c9de2e8afdf1643aa244d1cb1f06cc6
g8aa-qptn-vjns | 1 |  | J7 Rw15 | 1208010092 | 08-03-2017 18:57:13 CET | Mukakarangwa Assoumpta | 00:15:19 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Nyakaruri |  |  | kinywamagana pumping network | 6436 |  | 127 | 127 | 0 | Yes | Piped Network with Pump |  | 2013 | Yes | Kiziranyenzi | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8501579630556368 | 29.978788746008636 | 1810.5 | 2cztbyyz | 1 | https://waterforpeople.s3.amazonaws.com/images/4063c6a5-25b4-4246-ab61-2596480afe17.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | a9471277f74faa377bc54c689d921e
9snw-89g2-fafu | 1 |  | J7 Rw10 | 1275340163 | 06-04-2017 19:07:46 CEST | Tuyisenge Vianney | 00:13:54 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Remera |  |  | Kinyankeri water point at Buyogoma-Remera border |  |  | 105 | 105 | 0 | Yes | Piped Network -- Gravity Only |  | 2007 | Yes | Remera village of Nyirangarama cell and Buyogoma village of Mukoto cell | Local government in collaboration with the community | This water point in Kinyankeri catchment area that feeds some private connections in Buyogoma village.The water point is operational and functional normally.It is shared by Buyogoma and Remera villages | 1 | Spring | -1.6950597099281783 | 29.890803301352435 | 2001.6 | 25vb2tp8 |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6951866416342263 | 29.890943348950266 | 2038.5 | 25vitgkd | 3 | https://waterforpeople.s3.amazonaws.com/images/4b843569-4975-4502-8765-f326358b753a.jpg | 2010 | Normal | No |  |  |  | Yes |  | Normal | This water point in Kinyankeri catchment area that feeds some private connections in Buyogoma village.The water point is operational and functional normally.It is shared by Buyogoma and Remera villages | c250bbb93b41dc63848ff9ba678e5052
50dn-n5se-g84n | 1 |  | J7 Rw23 | 1240080049 | 23-03-2017 06:25:26 CET | Rugirangoga Augustin | 00:44:31 | 2017 | Rwanda | Rulindo | Buyoga | Gitumba | Rutabo |  |  | Kiruruma | 8295 |  | 128 | 125 | 3 | Yes | Piped Network with Pump |  | 2014 | Yes | Rutabo Gitaba Nyarubuye Remera Rusongati Rugarama Cyasuli Munini | Governement (District, WASAC) and Water For People |  | 2 | Groundwater (well, etc.) | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma | https://waterforpeople.s3.amazonaws.com/images/052273e7-54fb-4d0a-bf96-24a61bf3e118.jpg | No | 3 | Yes | 3 | https://waterforpeople.s3.amazonaws.com/images/e0537e66-534c-4640-a9a1-54b4e8e15771.jpg | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 4000 | Yes | 15 | -1.6684773741137722 | 30.047381335897573 | 1775.8 | 24nckozd | https://waterforpeople.s3.amazonaws.com/images/ff7b6e3f-ee3e-4ba5-978e-dd544501b508.jpg | 2014 | Normal | Yes | 5 | Pressure Break Tank |  | 2014 | Normal | Yes | 3 |  | 2014 | Normal | 4000 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/1cb1176c-5aa9-4e08-af33-ba3ccbbe6dda.jpg | 2014 | Normal | No |  |  |  | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.668601401492188 | 30.046855015065717 | 1774.8 | 24nkbbuc | 1 | https://waterforpeople.s3.amazonaws.com/images/c64aee2a-9810-4409-a332-d26b5979adf5.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | 7b25b5d33481674adff21b85fe6ffac7
xgu9-c59p-3b2s | 1 |  | J7 Rw8 | 1241700327 | 23-03-2017 07:56:12 CET | Amani Desire | 00:09:32 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Buliza |  |  | Mutagata Motorised Network | 26296 |  | 221 | 121 | 100 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.801852228745358 | 30.042845565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.802351623319464 | 30.0368544680217 | 1961.1 | 2asrfztc | 64 | https://waterforpeople.s3.amazonaws.com/images/5b46c46f-5128-4847-9375-b8f6ff0bc762.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | 69bef5516b5d280f011a2a5131c3ef2
6kgy-wcsu-gbcu | 1 |  | J7 Rw23 | 1224690093 | 15-03-2017 05:15:29 CET | Rugirangoga Augustin | 00:29:25 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 1789 |  | 192 | 180 | 12 | Yes | Piped Network -- Gravity Only |  | 2012 | Yes | karambi gitovu | Padiri |  | 3 | Spring¦Groundwater (well, etc.) | -1.6128815953757245 | 29.874655017548616 | 1956.1 | 223evzsq |  | Yes | 30 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 30 | Yes | 1 |  | 2016 | Normal | 6450 | Yes | 2 | -1.6111677762752643 | 29.98839135826884 | 1852 | 220khgmj |  | 2012 | Normal | Yes | 2 | Distribution Chamber |  | 2012 | Normal | Yes | 1 |  | 2016 | Normal | 6450 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6128815953757245 | 29.874655017548616 | 1956.1 | 223evzsq | 1 |  | 2012 | Normal | No |  |  |  | Yes |  | Normal | this network has no problem | 91fde5ca4140d6498fa132ba54f5d5f9
rg4y-526q-wsfv | 1 |  | J7 Rw10 | 1316610289 | 20-04-2017 07:01:14 CEST | Tuyisenge Vianney | 00:04:20 | 2017 | Rwanda | Rulindo | Tumba | Misezero | Misezero |  |  | Water point at APEKI Tumba Boys Dormitory/Nyirambuga pumping | 30604 |  | 115 | 115 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | Yes | 1 | -1.7083024137305112 | 29.952307072235406 | 2216.7 | 26h7y6pv | https://waterforpeople.s3.amazonaws.com/images/a2f5e0b9-6b03-4e8f-92b5-f2359c79b77b.jpg | 2012 | Normal | No | [5 empty] | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/ef63fe08-6fcc-4142-bdce-5cf8ce242272.jpg | 2012 | Normal | 100 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.709326572362805 | 29.951910425067222 | 2217.3 | 26iwoef3 | 6 | https://waterforpeople.s3.amazonaws.com/images/e2e98a1c-4fd3-429e-b238-2463c6e48603.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | operational | efc92d43aefaaf6657410328b2f501d
9pyp-nemm-sqxa | 1 |  | J7 Rw19 | 1239660578 | 23-03-2017 07:15:18 CET | Kayinamura Innocent | 00:09:54 | 2017 | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 26296 |  | 325 | 58 | 267 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2016 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.790198909303726 | 30.04491212897185 | 1858.9 | 2a8ngw9t | 64 | https://waterforpeople.s3.amazonaws.com/images/26b4c9d4-3919-45d7-9a0d-12ed5889f08d.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 95c5afa9a675fecb1e8b98f61e7e2c
fehh-5faa-3x4u | 1 |  | J7 Rw23 | 1214290391 | 15-03-2017 06:06:10 CET | Rugirangoga Augustin | 00:27:44 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Kabahama |  |  | Migogo | 558 |  | 178 | 150 | 28 | Yes | Piped Network -- Gravity Only |  | 2009 | Yes | kabahama kiruli bukangano Rubanda | Padiri(Lake angels). | network covers the area but some tanks, pipes and water taps need rehabilitation | 1 | Spring | -1.6327309674421784 | 29.901262305566668 |  | 2308pft0 |  | No | 50 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2009 | Poor | 50 | Yes | 1 |  | 2009 | Poor | 6800 | Yes | 2 | -1.6350887008641248 | 29.895210480778655 | 1759.6 | 2344max4 | https://waterforpeople.s3.amazonaws.com/images/f09167d7-f886-483c-ade7-4ec7ef801810.jpg | 2009 | Poor | No | [5 empty] | Yes | 1 |  | 2009 | Poor | 6800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6312375089630298 | 29.89428097781437 | 1734.1 | 22xref0e | 1 | https://waterforpeople.s3.amazonaws.com/images/175d7e10-8f15-4c1f-ad05-e6b142d2cbc5.jpg | 2009 | Poor | No |  |  |  | Yes |  | Poor |  | 624aa85d96f15a3c3212fe3df8489da
87yc-8n3a-x8ms | 1 |  | J7 Rw23 | 1244290052 | 25-03-2017 20:48:07 CET | Rugirangoga Augustin | 00:41:55 | 2017 | Rwanda | Rulindo | Buyoga | Butare | Gasave |  |  | Kiduha | 0 |  | 114 | 100 | 14 | Yes | Piped Network -- Gravity Only |  | 2007 | Yes | kankanga giko gasave | Governement (District, WASAC) and Water For People |  | 1 | Spring¦null | -1.69921094772796 | 30.01400249942007 | 1901.3 | 2626r6b0 | https://waterforpeople.s3.amazonaws.com/images/2528fbbe-3d5b-411b-a79f-5303f345fc20.jpg | No | 20 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/07823777-4d22-4985-a3f5-c3e831997cac.jpg | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 20 | Yes | 1 |  | 2007 | Poor | 2200 | Yes | 3 | -1.6932117321635163 | 30.026191374639453 | 1765.8 | 25s9j3fp |  | 2007 | Poor | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.693215760568369 | 30.02631107261556 | 1752.8 | 25s9j3fr | 1 | https://waterforpeople.s3.amazonaws.com/images/dc260124-8fe9-4875-ad2f-e88988573e23.jpg | 2014 | Normal | No |  |  |  | Yes |  | Poor |  | 18fee4b7f146e63dcd9ca7f945c7f76
50e2-56ag-ufr5 | 1 |  | J7 Rw8 | 1315110082 | 20-04-2017 14:39:34 CEST | Amani Desire | 00:09:40 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Karindi |  |  |  | 510 |  | 120 | 40 | 80 | Yes | Piped Network -- Gravity Only |  | 2007 | No |  |  |  | 2 | Spring | -1.759698733765297 | 29.933777367513624 | 1859.9 | 28u7kscp | https://waterforpeople.s3.amazonaws.com/images/f3479333-1903-4440-b3e9-4c52b4637e73.jpg | Yes | 180 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/de7b92be-0ae7-4ea3-b635-216936d727c6.jpg | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 180 | Yes | 1 |  | 2007 | Normal | 1000 | Yes | 1 | -1.7580489779060633 | 29.93419245007874 | 1843.1 | 28rhc9jh |  | 1997 | Poor | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7597288415688388 | 29.933644896112963 | 1898.2 | 28u9d360 | 1 | https://waterforpeople.s3.amazonaws.com/images/5b3192e8-ccdd-45af-9d45-9be0980a3573.jpg | 2007 | Normal | No |  |  |  | Yes |  | Normal |  | ddea94665dff1a8156941ff114a64e9
7n0n-ed89-89by | 1 |  | J7 Rw24 | 1327730154 | 24-04-2017 21:51:14 CEST | Kabalisa Manzi Christella | 00:12:22 | 2017 | Rwanda | Rulindo | Burega | Taba | Gasango |  |  | Rwamugaza network | 14106 |  | 79 | 79 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7374173333138418 | 30.06563288387298 | 1723.9 | 27td31kg |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7464760391368452 | 30.023824580282394 | 1633.4 | 288chrbi | 1 | https://waterforpeople.s3.amazonaws.com/images/796c05de-81f9-4054-86c5-f107487ad9e3.jpg | 2003 | Does Not Function | No |  |  |  | No | In these days the Water syetmen has issues | Poor |  | 63a414923c3b96c4e8de0e73e9399
4tnk-mu0a-f99e | 1 |  | J7 Rw23 | 1236940758 | 23-03-2017 06:28:16 CET | Rugirangoga Augustin | 00:35:44 | 2017 | Rwanda | Rulindo | Buyoga | Gitumba | Gitaba |  |  | Kiruruma | 8295 |  | 169 | 160 | 9 | Yes | Piped Network with Pump |  | 2014 | Yes | rutabo gitaba nyarubuye remera rusongati rugarama cyasuli munini | Governement (District, WASAC) and Water For People | this network is ok | 3 | Groundwater (well, etc.) | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 15 | -1.6111677762752643 | 30.047381335897573 | 1775.8 | 220khh2x |  | 2014 | Normal | Yes | 5 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/06670948-9f68-447d-92d4-464c1478314c.jpg | 2014 | Normal | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.685212146725117 | 30.056654899163664 | 1783.2 | 25f18bpy | 2014 | https://waterforpeople.s3.amazonaws.com/images/a6dbde1e-ba9b-4090-a248-edd183cf118d.jpg | 2014 | Normal | No |  |  |  | Yes |  | Poor | the network is working well | fdf1d742651cec8c8f9e9782322a62e
kx42-1r05-8bjh | 1 |  | J7 Rw10 | 1304640138 | 15-04-2017 23:50:31 CEST | Tuyisenge Vianney | 00:05:55 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Ntakara |  |  | Ntakara water point/Ntakara gravity system |  |  | 129 | 129 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | Local government in partnership with community | The water point is operation and functions well | 1 | Spring | -1.827334938521246 | 29.95090160939001 | 1943.1 | 2by2osad |  | Yes | 50 | No | [5 empty] | 50 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.822581891664508 | 29.961221106081453 | 1676.5 | 2bq7vw0s | 1 | https://waterforpeople.s3.amazonaws.com/images/d5830596-2904-44a1-a75e-d1a06f3e4c5a.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The water point is operation and functions well | a048939ca46e328249e8fa0428787de
a4bq-049y-m5gc | 1 |  | J7 Rw23 | 1218280212 | 15-03-2017 08:03:41 CET | Rugirangoga Augustin | 00:47:49 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Mushongi |  |  | Gihanga | 2456 |  | 214 | 200 | 14 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | mushongi buramba | Governement (District, WASAC) and Water For People | this network is not getting enough water | 1 | Spring | -1.651194351513934 | 29.909579189116428 | 1763.5 | 23urrml3 |  | Yes | 15 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 15 | Yes | 1 |  | 2016 | Normal | 7200 | Yes | 6 | -1.6498521069502532 | 29.917613599705728 | 1996.9 | 23sjzjl4 |  | 2016 | Normal | No | [5 empty] | Yes | 1 |  | 2016 | Poor | 7200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6512099417740973 | 29.909583267150413 | 1769.3 | 23usd26v | 2 | https://waterforpeople.s3.amazonaws.com/images/e2a5fc6c-f24a-4f44-86e3-19a6459a0e94.jpg | 2016 | Normal | Yes | 6 | 7 | water pressure is low(design issue) | No | water pressure due to long distance | Poor | this network needs to be reinforced in design | 7c96766c883eecc18308e5128ed227d
bh4y-but0-bga | 1 |  | J7 Rw19 | 1222390180 | 10-03-2017 04:23:19 CET | Kayinamura Innocent | 00:14:18 | 2017 | Rwanda | Rulindo | Ngoma | Mugote | Kigina |  |  | Shishi network |  |  | 84 | 84 | 0 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | Kigina | Governement (District, WASAC) and Water For People | poor management | 1 | Spring | -1.8097197675805605 | 29.979881122155494 | 1794.6 | 2b4xn0ly |  | No | 28 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 28 | Yes | 1 |  | 2014 | Normal | 700 | Yes | 2 | -1.809674509873321 | 29.981912015157096 | 1778.3 | 2b4v9a7f |  | 2014 | Normal | No | [5 empty] | Yes | 1 |  | 2014 | Normal | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8159483175674132 | 29.989453946416248 | 1657.3 | 2bf8k2k6 | 4 | https://waterforpeople.s3.amazonaws.com/images/6a929540-5433-45d3-9500-126dd4f959f8.jpg | 2014 | Normal | No |  |  |  | Yes |  | Poor | 1. Outlet of start chamber had been damaged 2. poor management | 1f2f1c1f4132451df4ab2e836f89fc
5eu1-2j88-17ap | 1 |  | J7 Rw19 | 1221510178 | 13-03-2017 06:47:36 CET | Kayinamura Innocent | 01:02:09 | 2017 | Rwanda | Rulindo | Ngoma | Munyarwanda | Busizi |  |  | Kabarore-Ngoma-Nyabuko network | 8284 |  | 100 | 39 | 61 | Yes | Piped Network with Pump |  | 2014 | Yes | Nyabuko, Kagwa, Kiruri, Busizi, Ngaru, Kirungu, Kiboha and kigina | Governement (District, WASAC) and Water For People | The network has 17 water points and it serves 8 villages | 4 | Spring | -1.8123357076877171 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦Collection Chamber | 2014 | Normal | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.8118879629206273 | 30.003478805087482 | 2031 | 2b8iu32a |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 4 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8189514793480195 | 30.00557932995757 | 1938 | 2bk7rjrr | 17 | https://waterforpeople.s3.amazonaws.com/images/1e554b65-7a4c-4b00-af3f-c58375b32fa0.jpg | 2014 | Normal | Yes | 1 | 10 | it was due to the road construction | Yes |  | Normal | -the network has 17 water points -water points are in good operation conditions expect the water point at the source that is damaged - 4 water points don't have water today - The pipe are in good conditions - The pump is not working properly as it was expected during Design, today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy - the transformer at the pumping station doesn't offer the required energy for the pump - anti-hammer of pump are not functioning because of bad installation of pumping house - The suction tank is in bad physical condition | 2fa78aa1a48242f4203476a97f2daa
y493-gd01-73b4 | 1 |  | J7 Rw10 | 1306630101 | 16-04-2017 23:15:04 CEST | Tuyisenge Vianney | 00:06:20 | 2017 | Rwanda | Rulindo | Tumba | Barari | Gashoro |  |  | Gashoro water point/Nyirambuga pumping | 30604 |  | 161 | 161 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | under construction | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.7193703649135286 | 29.933522539735662 | 1755.6 | 26zj118n | https://waterforpeople.s3.amazonaws.com/images/6f67ab10-d2b2-408e-aef7-fcfdf0cadd7c.jpg | 2017 | Does Not Function | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7206462556921924 | 29.93216728888707 | 1740.5 | 271mn321 | 2 | https://waterforpeople.s3.amazonaws.com/images/116c0323-86b0-482a-ace7-a22f8a517fd9.jpg | 2017 | Does Not Function | No |  |  |  | No | under construction | Does Not Function | under construction | 434a5e242a851dbe4e582d825fffa630
s67f-hdny-j032 | 1 |  | J7 Rw19 | 1221510174 | 10-03-2017 04:26:25 CET | Kayinamura Innocent | 00:11:40 | 2017 | Rwanda | Rulindo | Ngoma | Karambo | Butare |  |  | Shishi network |  |  | 122 | 38 | 84 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | Kigina | Governement (District, WASAC) and Water For People | Poor management | 1 | Spring | -1.8097197675805605 | 29.97988112215549 | 1794.3 | 2b4xn0ly |  | No | 28 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 28 | Yes | 1 |  | 2014 | Normal | 700 | Yes | 2 | -2.3282316868320994 | 29.13688250238971 | 1581.4 | 2yygz5d4 |  | 2014 | Normal | No | [5 empty] | Yes | 1 |  | 2014 | Normal | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8112704509088884 | 29.98560742313643 | 1686.1 | 2b7iin0w | 4 | https://waterforpeople.s3.amazonaws.com/images/6cf3669b-a050-48fd-9b10-532b4e4a1b00.jpg | 2014 | Poor | No |  |  |  | Yes |  | Poor | 1. Outlet of start chamber had been damaged 2. poor management | c8351c3358c24201e244f88b1e361fc
69nq-u2h7-qgam | 1 |  | J7 Rw10 | 1218280496 | 13-03-2017 22:24:03 CET | Tuyisenge Vianney | 00:04:27 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Kigamba |  |  | Water point at centre kigamba/Rutumvo gravity |  |  | 172 | 172 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | The water point operates good | 1 | Spring | -1.677891751247546 | 29.90118126071259 | 1802.6 | 252xezpf |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7020393652431982 | 29.910026598684414 | 1735.3 | 266une3g | 1 | https://waterforpeople.s3.amazonaws.com/images/afbd014b-3e7c-4bf4-acaf-5de2a21033e4.jpg | 2015 | Poor | No |  |  |  | Yes |  | Poor | The water tap was damaged | 2e45622b931376892cbcdf3ecc55eafb
dgar-eu3m-vuy2 | 1 |  | J7 Rw10 | 1225560452 | 14-03-2017 22:07:15 CET | Tuyisenge Vianney | 00:12:18 | 2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kinini |  |  | Kinini water point/Ntaruka-Gahama gravity | 1567 |  | 250 | 250 | 0 | Yes | Piped Network -- Gravity Only |  | 2008 | No |  | GoR |  | 1 | Spring | -1.765657270137325 | 29.91982532317513 | 2061.6 | 2942f4se |  | Yes | 40 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2006 | Normal | 40 | Yes | 1 |  | 2006 | Normal | 100 | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7662881171514389 | 29.929882695552674 | 1807.9 | 2953xfz6 | 1 | https://waterforpeople.s3.amazonaws.com/images/1ab9c067-95b3-4fde-94e0-b9b96c30547b.jpg | 2008 | Normal | No |  |  |  | No | Ayateke closed the water point due to low courage in paying the water cost | Does Not Function | It is closed due to people who claim the water cost is high.Then they decide to go else where to fetch water | 8ec7eeb2eccb6af3c05ab08e11d22b68
1sdk-0fmn-2v6d | 1 |  | J7 Rw10 | 1225560454 | 14-03-2017 22:16:33 CET | Tuyisenge Vianney | 00:06:30 | 2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kinini |  |  | Kinini 2 water point/Ntaruka-gahama gravity | 1567 |  | 250 | 250 | 0 | Yes | Piped Network -- Gravity Only |  | 2006 | No |  | GoR | The water point got damaged and nolonger operates.Needs repair and maintenance as well as water supply to meet the people demand | 1 | Spring | -1.765657270137325 | 29.91982532317513 | 2061.6 | 2942f4se |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | Yes | 1 | -1.7664773083233913 | 29.928236540255252 | 1825.6 | 295f8ogi | https://waterforpeople.s3.amazonaws.com/images/081af9f7-df48-4fd4-a755-5f6386c4111e.jpg | 2006 | Poor | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7663666519947452 | 29.928556929091794 | 1815.6 | 2958owt1 | 1 | https://waterforpeople.s3.amazonaws.com/images/d0a43098-4dd3-4323-a654-0ec392053440.jpg | 2006 | Does Not Function | No |  |  |  | No | The water point got damaged and nolonger operates.Needs repair and maintenance as well as water supply to meet the people demand | Does Not Function | The water point got damaged and nolonger operates.Needs repair and maintenance as well as water supply to meet the people demand | 29b92729f246d64f8d1ea2b08fcf95b3
nqxj-hdvk-44be | 1 |  | J7 Rw19 | 1232800593 | 24-03-2017 05:17:39 CET | Kayinamura Innocent | 00:12:28 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Rukurazo |  |  | Mutagata Gravity network | 26296 |  | 247 | 140 | 107 | Yes | Piped Network -- Gravity Only |  | 1987 | Yes | Ruri, Musenga, Rukurazo, Umubuga, Amataba, Rusine, Marenge |  |  | 1 | Spring | -1.8023389079852205 | 30.042447389592418 | 1691.2 | 2asq94nc |  | Yes | 8 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2004 | Poor | 8 | Yes | 1 |  | 2004 | Poor | 3500 | Yes | 6 | -1.8078446763653504 | 30.06649761552014 | 1669.8 | 2b1uaz5k |  | 2004 | Poor | Yes | 4 | Distribution Chamber¦Washout and Air release |  | 2004 | Poor | Yes | 2 |  | 2004 | Poor | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8147190833610105 | 30.071367911492313 | 1635.8 | 2bd7brs9 | 12 | https://waterforpeople.s3.amazonaws.com/images/be1c2fe3-f7dc-4d8e-b212-676cbcb9e0fc.jpg | 2004 | Normal | No |  |  |  | Yes |  | Poor | 1. the Extension to Nyabinyana village has 2 reservoirs and two water points which is under construction 2. this system have been constructed in 2004 3. it serve a party of Masoro Sector and other party is located in Gasabo District 4. 2 water points and one reservoir have been constructed in 2016. 5. in general, this network has 27 water points in which 12 are in Rulindo District and the remaining are in Gasabo District. | 6d2f225b98e2e6e9c98126aeba6021
mcme-eq10-74j7 | 1 |  | J7 Rw10 | 1299950062 | 14-04-2017 20:35:01 CEST | Tuyisenge Vianney | 00:13:11 | 2017 | Rwanda | Rulindo | Bushoki | Mukoto | Muko |  |  | Water point at Godoro/Rusave gravity system | 567 |  | 116 | 116 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People | This water point is located in the area known as Godoro.This is connected to Rusave gravity system.It had been mistakenly counted as located in Rusave.It is operating normally | 2 | Spring | -1.1710112286463475 | 29.9009875966343068 | 1931.1 | 1hsn38ld |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.699384219011402 | 29.90683630553078 | 1769.6 | 262gvirg | 1 | https://waterforpeople.s3.amazonaws.com/images/0329e2cb-2de9-4af7-a879-5775120622ed.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | This water point is located in the area known as Godoro.This is connected to Rusave gravity system.It had been mistakenly counted as located in Rusave.It is operating normally | 59545d36f54b479f08eb5cbd540fa2
4qqe-797u-faf3 | 1 |  | J7 Rw10 | 1307560137 | 18-04-2017 06:42:21 CEST | Tuyisenge Vianney | 00:09:48 | 2017 | Rwanda | Rulindo | Tumba | Barari | Kigarama |  |  | Water point nearby APEKI Tumba Technical School/Nyirambuga pumping | 30604 |  | 154 | 154 | 0 | Yes | Piped Network with Pump |  | 2012 | Yes | Kigarama/Barari and Misezero/Misezero cell | Governement (District, WASAC) and Water For People | It is nearby APEKI chez Bernard Ndagijimana.It is frequently having water.And it is served by the Main Reservoir R300m3 at Misezero | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.709668952721241 | 29.950416882008057 | 2202.9 | 26jgx4z4 | 2 | https://waterforpeople.s3.amazonaws.com/images/274d6923-a61d-4ee1-923c-3a7a138571b5.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | It is nearby APEKI chez Bernard Ndagijimana.It is frequently having water.And it is served by the Main Reservoir R300m3 at Misezero | 9f4c45672dbdb0657d716b2e3381debe
98gu-kv79-xq0n | 1 |  | J7 Rw24 | 1227530056 | 15-03-2017 15:30:27 CET | Kabalisa Manzi Christella | 00:30:07 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Nyakabanga |  |  | 0 | 6572 |  | 780 | 0 | 780 | Yes | Piped Network with Pump |  | 2014 | No |  | Governement (District, WASAC) and Water For People | Water doesn’t Flow | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2009 | Normal | 4.5 | Yes | 2 |  | 2014 | Does Not Function | 3000 | Yes | 2 | -1.7555179528295524 | 30.03970289656239 | 1690.5 | 28napmb1 |  | 2014 | Does Not Function | Yes | 8 |  |  | 2014 | Does Not Function | Yes | 2 |  | 2014 | Does Not Function | 3000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7572871420305276 | 30.047023162730806 | 1565.7 | 28q83cfq | 1 | https://waterforpeople.s3.amazonaws.com/images/87133d32-2181-4124-8d7c-50b5b899403d.jpg | 2014 | Does Not Function | Yes | 365 | 0 | Water is not Flowing | No | Water is not Flowing | Does Not Function | System under construction | f5ebe2abea308d3f57359b43e07da
jfth-36uf-xef5 | 1 |  | J7 Rw15 | 1243830169 | 22-03-2017 18:48:00 CET | Mukakarangwa Assoumpta | 00:09:48 | 2017 | Rwanda | Rulindo | Kinihira | Butunzi | Gisekuru |  |  | Nyamagana-Kinihira |  |  | 143 | 80 | 63 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦Ventouse ,Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.664371211313473 | 29.956445843440072 | 1892.4 | 24gkgy98 | 2 | https://waterforpeople.s3.amazonaws.com/images/b51e3002-09c9-4c44-8a15-0376bbc6478b.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | 7ef9a093a2f417769a44b51989fc2685
2rt5-39ny-0bd2 | 1 |  | J7 Rw19 | 1239660562 | 23-03-2017 07:09:28 CET | Kayinamura Innocent | 00:11:35 | 2017 | Rwanda | Rulindo | Masoro | Kivugiza | Nyarurembo |  |  | Mutagata motorised network | 26296 |  | 325 | 69 | 256 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7901711668183091 | 30.045436816631703 | 1895.4 | 2a8ma12e | 64 | https://waterforpeople.s3.amazonaws.com/images/6cd8aace-afee-4e43-acff-79317f86607b.jpg | 2015 | Poor | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 5dc8bcf51424ceac6dc36f126a708e5e
3uqw-xjv9-sk90 | 1 |  | J7 Rw10 | 1231180081 | 02-01-2015 11:55:37 CET | Tuyisenge Vianney | 00:14:19 | 2017 | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at Buyoga sector/Nyirambuga pumping | 30604 |  | 177 | 177 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point is located in Buyoga market.It operates very well and normally however its management is poor since hygiene on the water tap | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.692451897156616 | 30.012431570899686 | 2082.7 | 25r0a5cs | 2 | https://waterforpeople.s3.amazonaws.com/images/792a4b26-a515-4e22-942a-1e1962b74844.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point is located in Buyoga market.It operates very well and normally however its management is poor since hygiene on the water tap | fd5c65014a79191392c577d0422bd5
qbsj-fvvj-b0d1 | 1 |  | J7 Rw7 | 1442280172 | 04-06-2017 13:21:35 CEST | Rugirangoga Augustin | 00:20:46 | 2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Gatete |  |  | gahama | 10234 |  | 163 | 130 | 33 | Yes | Piped Network -- Gravity Only |  | 2012 | Yes | ruberano gatete mugomero gishinge nyakarekare kibingwe | water for people | ntakibazo uyu muyoboro ufite | 2 | Spring | -1.6675834297797398 | 30.0428712210569 | 1965.7 | 24lvl43w |  | Yes | 65 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 65 | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 | Pressure Break Tank¦Distribution Chamber¦washout,air release |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6172728152421039 | 30.031708051594812 | 2187.5 | 22ao9bkt | 1 | https://waterforpeople.s3.amazonaws.com/images/0b7290ec-e28b-4050-9cfe-fa7e31f8b468.jpg | 2012 | Poor | No |  |  |  | Yes |  | Normal |  | 1648654b8f1b31670689fd289d37b21
mhj0-4fp9-991k | 1 |  | J7 Rw24 | 1249080669 | 28-03-2017 10:08:22 CEST | Kabalisa Manzi Christella | 00:05:43 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Rusana |  |  | Rwamugaza network | 14106 |  | 276 | 276 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391495139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8068681020797233 | 30.107258252322993 | 1652.1 | 2b07yi6o | 1 | https://waterforpeople.s3.amazonaws.com/images/1a304cfa-101c-4173-af25-b25b4e68ce3e.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | ac5b9e58ef6c7a588faaee832463152
rn82-5fc1-4xr | 1 |  | J7 Rw15 | 1235060248 | 22-03-2017 18:30:09 CET | Mukakarangwa Assoumpta | 00:08:38 | 2017 | Rwanda | Rulindo | Kinihira | Butunzi | Kiniihira |  |  | Nyamagana-Kinihira |  |  | 118 | 60 | 58 | Yes | Piped Network with Pump |  | 2015 | Yes | All villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 6000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦Ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.666570861495772 | 29.96094511813989 | 1944.2 | 24k7gbdl | 2 | https://waterforpeople.s3.amazonaws.com/images/138e2e33-dd37-43a3-a5c2-1bd0e03090ea.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | b0ec6293a866758fcfd3b260ee7946d
pf3e-njxs-f31v | 1 |  | J7 Rw10 | 1219300630 | 16-03-2017 17:25:07 CET | Tuyisenge Vianney | 00:11:19 | 2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Rwanzu |  |  | Matonyanga source catchment |  |  | 154 | 154 | 0 | Yes | Piped Network -- Gravity Only |  | 2017 | Yes | Rwanzu,Miduha and Rebero | Governement (District, WASAC) and Water For People | The water source has been captured very soon and it is well protected | 1 | Spring | -1.69919116767908 | 29.937233740854015 | 1848.2 | 2625kai4 | https://waterforpeople.s3.amazonaws.com/images/0ceea818-6313-474e-ac8b-8cb00fd5be15.jpg | Yes | 40 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/c074e506-f637-4fd9-b52b-5afb030846a6.jpg | "Springbox" --Intake Structure at a Spring | 2017 | Normal | 40 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/b89d97f4-d1fd-4c9e-985d-82cdedfc2087.jpg | 2017 | Normal | 100 | Yes | 1 | -1.699259214375793 | 29.937150660208275 | 1895.8 | 26294w4r | https://waterforpeople.s3.amazonaws.com/images/bd3ff2bd-8e03-4ce2-8359-8a809af1b380.jpg | 2017 | Normal | No | [5 empty] | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/5ed08ed4-982c-44f2-9175-6e3f1694f60c.jpg | 2017 | Normal | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.699084922126835 | 29.936975987722754 | 1894.8 | 261z0iuh | 1 | https://waterforpeople.s3.amazonaws.com/images/80ab5aaf-e710-45f0-a1fc-91390d737fca.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | The water source catchment area is also having a water point recentĺy completed.In water storage tanks water is there but it hasn't yet delivered water services to the people | 78cbebe8f69dff57f2bb5422d18a61dc
63hc-9qsn-h069 | 1 |  | J7 Rw8 | 1437160077 | 04-06-2017 15:33:12 CEST | Amani Desire | 00:18:22 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Ruhanya |  |  | musenge | 6074 |  | 25 | 25 | 0 | Yes | Piped Network with Pump |  | 2014 | No |  | water for people |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.8 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.8 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber¦Washout and Air release |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.748450583384882 | 29.93826679488638 | 2041.1 | 28bmdkfq | 1 | https://waterforpeople.s3.amazonaws.com/images/4178833c-c587-4684-aeab-5ce2a3d0936a.jpg | 2014 | Poor | No |  |  |  | No | water don't reach the distribution Reservoir that serves this water point | Poor |  | 6c8eec32e61c16e223438e4121d161
wanc-b21k-cwf4 | 1 |  | J7 Rw26 | 1430130367 | 02-06-2017 09:40:52 CEST | Byukusenge Elie | 00:05:37 | 2017 | Rwanda | Rulindo | Cyinzuzi | Migendezo | Gitabage |  |  | Kararama | 6572 |  | 70 | 60 | 10 | Yes | Piped Network with Pump |  | 2009 | Yes | Not Water Tap | Water For People |  | 3 | Spring | -1.750378530192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2009 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 7 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2009 | Normal | Yes | 14 | Pressure Break Tank¦Distribution Chamber |  | 2009 | Normal | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 1 |  | 2012 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7651324776779216 | 29.995913867840148 | 2161.3 | 2937glx3 | 1 | https://waterforpeople.s3.amazonaws.com/images/8b1cfc82-f483-4443-9249-ca33f1127a64.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal |  | e02e8a326319e6a5f682274269f3eb19
e6mg-9mp5-dp9u | 1 |  | J7 Rw10 | 1216031122 | 14-03-2017 23:03:30 CET | Tuyisenge Vianney | 00:05:03 | 2017 | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Kingazi water point chez Rwigema/Nyakabizi gravity | 1259 |  | 157 | 157 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | This water operates well however it doesnot meet the demand of the people | 1 | Spring | -1.803447729664134 | 29.930708856826865 | 1927.1 | 2aukc7xn |  | Yes | 20 | No | [5 empty] | 20 | No | [5 empty] | Yes | 1 | -1.8090841481335838 | 29.91886626727014 | 1747.5 | 2b3w4p10 | https://waterforpeople.s3.amazonaws.com/images/4abe141c-2e66-489b-a60b-9b66a26f76b9.jpg | 2013 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8090600937667847 | 29.9186672478578 | 653.3 | 2b3uxtte | 1 | https://waterforpeople.s3.amazonaws.com/images/aea6f93a-e4ae-4e23-8582-a080a66958d9.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | This water operates well however it doesnot meet the demand of the people | e167f03f572bfd2f881cc6d2ba986560
ence-ck3m-n6pj | 1 |  | J7 Rw10 | 1280470085 | 05-04-2017 21:57:36 CEST | Tuyisenge Vianney | 00:03:41 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Tare |  |  | Nyakariba-Tare gravity system | 9577 |  | 109 | 109 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | Loal government in Ubudehe program | Nyakariba-Tare small gravity system for one water public point with R3m3 as well Sina Gerard Workshop | 1 | Spring | -1.66980932468877 | 29.88823550873981 | 1794.1 | 24pjrb7m |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | Yes | 1 | -1.669679780330946 | 29.88835005513904 | 1748.1 | 24pc0ocj | https://waterforpeople.s3.amazonaws.com/images/c031406d-d467-4fa9-9bef-0aad7b19e802.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.669781684707097 | 29.88847599519527 | 1722.4 | 24pikg04 | 1 |  | 2015 | Normal | No |  |  |  | Yes |  | Normal | Nyakariba-Tare small gravity system for one water public point with R3m3 as well Sina Gerard Workshop | 9f63b7ca8b4f70daf98de8a1119bc42
7vj4-xd4b-9g0h | 1 |  | J7 Rw10 | 1223980100 | 15-03-2017 19:38:14 CET | Tuyisenge Vianney | 00:06:23 | 2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Rwanzu |  |  | Rwanzu2 wpt/Nyirambuga pumping | 30604 |  | 154 | 154 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | GoR | Rwanzu water point/Nyirambuga pumping does no longer.People are fetching from the Nkore water supply system | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.696425924882207 | 29.920481660004302 | 2096 | 25xkn7t0 | 1 | https://waterforpeople.s3.amazonaws.com/images/24a68b0f-1dae-4142-80c0-faea7b54c30f.jpg | 2012 | Does Not Function | No |  |  |  | No | Rwanzu water point/Nyirambuga pumping does no longer.People are fetching from the Nkore water supply system | Does Not Function | Rwanzu water point/Nyirambuga pumping does no longer.People are fetching from the Nkore water supply system | 2f64aca13b26631688254c8b404239e7
v91u-wv6u-rqdc | 1 |  | J7 Rw15 | 1200340463 | 08-03-2017 19:08:20 CET | Mukakarangwa Assoumpta | 00:10:15 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Gisiza |  |  | kinywamagana pumping network | 6436 |  | 212 | 112 | 100 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8521517286323745 | 29.982429597275605 | 1799.4 | 2d34enzk | 1 | https://waterforpeople.s3.amazonaws.com/images/9e044316-231c-4f0a-a0be-18534e5b50f5.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor | water does not reach this water point at this moment | f9dca12e8b28d5b7bf34f353d288b4a
a71h-smk9-rmbh | 1 |  | J7 Rw10 | 1234240176 | 03-01-2015 01:59:24 CET | Tuyisenge Vianney | 00:04:06 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Murambi2 water point/Nyirambuga pumping | 30604 |  | 174 | 174 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Not operating.Was damaged even standing pipe was cut into pieces.Taps were removed.Needs maintenance and repair | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6903874709976452 | 29.930734024600405 | 2097.8 | 25nl1ei3 | 0 | https://waterforpeople.s3.amazonaws.com/images/d4f96c9b-6155-47dc-8b19-8c95fc787161.jpg | 2012 | Does Not Function | No |  |  |  | No | Water point nolonger functions | Does Not Function | Not operating.Was damaged even standing pipe was cut into pieces.Taps were removed.Needs maintenance and repair | 6b8ecf55d4f88cff7f476ad86508eb7
s8hy-k6cg-aft3 | 1 |  | J7 Rw8 | 1240160051 | 23-03-2017 11:45:11 CET | Amani Desire | 00:14:52 | 2017 | Rwanda | Rulindo | Masoro | Shengampuri | Amataba |  |  | Mutagata Gravity Network | 26296 |  | 178 | 126 | 52 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | Ruri,musenga,umubuga,amataba,rusine,marenge |  |  | 1 | Spring | -1.8023389079852206 | 30.04244738995922418 | 1691.2 | 2asq94nc |  | Yes | 8 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2004 | Poor | 8 | Yes | 1 |  | 2004 | Poor | 3500 | Yes | 6 | -1.8078446763653504 | 30.066649761552014 | 1669.8 | 2b1uaz5m |  | 2004 | Poor | Yes | 4 | Distribution Chamber¦Washout and Air release chamber |  | 2004 | Poor | Yes | 2 |  | 2004 | Poor | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8160345509210092 | 30.084923995364118 | 1589.3 | 2bfdwzqp | 12 | https://waterforpeople.s3.amazonaws.com/images/35f5a7e9-ebe3-459e-b77f-8602c5dfbf06.jpg | 2004 | Poor | No |  |  |  | No | pipes are broken | Does Not Function | 1.the extension to nyabinyana village has 2 reservoirs and two water points which is under construction 2.this system have been constructed in 2004 3.it serves a part of Masoro sector and parts is located in Gasabo district 4. 2 water points and one reservoir have been constructed in 2016 5.in general this network has 27 water points in wich 12 are in Rulindo district and others are in Gasbo district | 3b109dc20ed1f973d33471365b9773
rypm-x3fg-6avk | 1 |  | J7 Rw19 | 1240850298 | 23-03-2017 18:41:52 CET | Kayinamura Innocent | 00:14:23 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Nyarurembo |  |  | Mutagata motorised network | 26296 |  | 144 | 56 | 88 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.789068858299376 | 30.040663994106232 | 1966.1 | 2a6s6wvq | 64 | https://waterforpeople.s3.amazonaws.com/images/e2582164-a7ed-45e1-91cb-c8e3828ee4c6.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 959fbd46a58a6e34e413cb287b9cb7
9kbb-bs3q-31u | 1 |  | J7 Rw24 | 1251790138 | 28-03-2017 10:22:04 CEST | Kabalisa Manzi Christella | 00:06:00 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyakambu |  |  | Rwamugaza network | 14106 |  | 186 | 186 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7910627984532141 | 30.125306116036885 | 1441.4 | 2aa39mit | 1 | https://waterforpeople.s3.amazonaws.com/images/1c489b5a-d06e-4920-8118-f1a4cdcac682.jpg | 2003 | Does Not Function | No |  |  |  | Yes |  | Poor |  | f8e9c9d2bdea1837e894c35077ebbddf
a4we-1myq-njk8 | 1 |  | J7 Rw24 | 1202052064 | 16-03-2017 08:08:50 CET | Kabalisa Manzi Christella | 00:07:12 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Gashinge |  |  | Rwamugaza | 14106 |  | 435 | 435 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3.5 | Yes | 2 |  |  | 2003 | Normal | 3.5 | Yes | 1 |  | 2003 | Normal | 8000 | Yes | 10 | -1.7374173333138418 | 30.06563288387298 | 1723.9 | 27td31kg |  | 2014 | Normal | Yes | 8 |  |  | 2014 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7385582724063247 | 30.06170175108448 | 1752.3 | 27v8ygi1 | 1 | https://waterforpeople.s3.amazonaws.com/images/1dc2899c-43a8-451f-a85f-d4d960e407c2.jpg | 2014 | Poor | No |  |  |  | No | System under rehabilitation | Normal |  | ada622fe9ffe6037afb8ec19dff387
k74v-4jhb-58js | 1 |  | J7 Rw24 | 1219270188 | 16-03-2017 07:47:23 CET | Kabalisa Manzi Christella | 00:08:34 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Kibiraro |  |  | Rwamugaza | 14106 |  | 500 | 500 | 0 | Yes | Piped Network -- Gravity Only |  | 2014 | No |  | Governement (District, WASAC) and Water For People | no problem | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3.5 | Yes | 2 |  |  | 2003 | Normal | 3.5 | Yes | 1 |  | 2014 | Normal | 8000 | Yes | 20 | -1.7416188180333267 | 29.988511802248155 | 1861.3 | 280b531p |  | 2003 | Normal | Yes | 16 |  |  | 2014 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7299696922411658 | 30.06477230817845 | 1551 | 27h1j3vr | 1 | https://waterforpeople.s3.amazonaws.com/images/d8311bd4-7b88-41df-81cb-ac6516980460.jpg | 2014 | Does Not Function | Yes | 5 | 25 | Pipes broken | No | Broken parts | Does Not Function | Water is not Flowing | 8127d0a44728b4b188b3c94cc132b3e
q8uc-vg0m-0ds8 | 1 |  | J7 Rw7 | 1197760224 | 06-03-2017 10:16:53 CET | Jeff Vedaste | 00:16:17 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Amahoro |  |  |  | 26296 |  | 120 | 120 | 0 | Yes | Piped Network with Pump |  | 2016 | Yes | Buliza | Governement (District, WASAC) and Water For People |  | 2 | Spring¦null | -1.9864571761211944 | 30.102783835802864 | 1450.5 | 2j98a78j | https://waterforpeople.s3.amazonaws.com/images/b57259c5-615b-4db2-bbfd-746bb1dba32d.jpg | Yes | 3.2 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 3.2 | Yes | 2 |  | 2016 | Normal | 5300 | Yes | 24 | -1.9863381440675376 | 30.10291411353957 | 1497.6 | 2j914zz9 |  | 2016 | Normal | Yes | 2 | Distribution Chamber |  | 2016 | Normal | Yes | 2 |  | 2016 | Normal | 17200 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.9864279334954753 | 30.102890731013535 | 1560.5 | 2j96hwf8 | 32 |  | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | bf58d7d57d513bb3d947fc249cf378
xxtu-ssqf-t2dc | 1 |  | J7 Rw8 | 1238250153 | 23-03-2017 11:30:37 CET | Amani Desire | 00:19:38 | 2017 | Rwanda | Rulindo | Masoro | Shengampuri | Umubuga |  |  | Mutagata Gravity Network | 26296 |  | 175 | 54 | 121 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | Ruri,musenga,umubuga,amataba,rusine,marenge |  |  | 1 | Spring | -1.8023389079852206 | 30.042447389592418 | 1691.2 | 2asq94nc |  | Yes | 8 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2004 | Poor | 8 | Yes | 1 |  | 2004 | Poor | 3500 | Yes | 6 | -1.8078446763653504 | 30.066649761552014 | 1669.8 | 2b1uaz5m |  | 2004 | Poor | Yes | 4 | Distribution Chamber¦Washout and Air release chamber |  | 2004 | Poor | Yes | 2 |  | 2004 | Poor | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8076825304919226 | 30.066851235361085 | 1661.3 | 2b1ks1h8 | 12 | https://waterforpeople.s3.amazonaws.com/images/d9bf432f-d51a-4478-8e4a-9e3cc2d9bd4d.jpg | 2004 | Poor | No |  |  |  | Yes |  | Poor | 1.the extension to nyabinyana village has 2 reservoirs and two water points which is under construction 2.this system have been constructed in 2004 3.it serves a part of Masoro sector and parts is located in Gasabo district 4. 2 water points and one reservoir have been constructed in 2016 5.in general this network has 27 water points in wich 12 are in Rulindo district and others are in Gasbo district | 6dbc41c9c7fca98a9db94d1e57ed97b
gbs8-xgur-1yah | 1 |  | J7 Rw24 | 1224850129 | 16-03-2017 06:46:04 CET | Kabalisa Manzi Christella | 00:08:41 | 2017 | Rwanda | Rulindo | Burega | Taba | Mwenene |  |  | Rwamugaza | 14106 |  | 445 | 445 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | no problem | 3 | Spring | -1.7503785350192073 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7283422490480729 | 30.014136457203506 | 2039.9 | 27ed2vhp | 1 | https://waterforpeople.s3.amazonaws.com/images/48c1bb76-a186-41e5-a351-4abff47b2fce.jpg | 2012 | Does Not Function | No |  |  |  | No | Road construction destroyed some pipes | Poor | No Water Flowing | e26f982e6c3bc1c6d4daf6b6287462d4
90vg-2ktj-yxaj | 1 |  | J7 Rw15 | 1201250802 | 09-03-2017 19:13:39 CET | Mukakarangwa Assoumpta | 00:13:18 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyabitare |  |  | Gisoro-Nyundo network | 2297 |  | 130 | 52 | 78 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.840451151026817 | 29.948165560771624 | 1795.9 | 2cjrthy1 |  | Yes | 13 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 13 | Yes | 1 |  | 2013 | Normal | 30 | Yes | 6 | 1.8406374522240199 | 29.94836287627501 | 1783.7 | 2ck2jau3 |  | 2013 | Poor | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 7000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.845564023898631 | 29.95150559436365 | 1685.9 | 2cs8203f | 1 | https://waterforpeople.s3.amazonaws.com/images/3eae76b0-2b32-4497-a63f-c9994da48bb8.jpg | 2013 | Poor | No |  |  |  | Yes |  | Normal | water point does not function very well because the reservoir does not have flotter | 711363c7dfc63d8ffdea969cf611c5e7
cbf9-6jqt-nb4m | 1 |  | J7 Rw19 | 1313320076 | 20-04-2017 14:57:10 CEST | Kayinamura Innocent | 00:19:46 | 2017 | Rwanda | Rulindo | Ngoma | Karambo | Nyakagezi |  |  | Sehuta |  |  | 99 | 39 | 60 | Yes | Piped Network -- Gravity Only |  | 2014 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8138206649726223 | 29.979785742648726 | 1726.1 | 2bbqc68l | https://waterforpeople.s3.amazonaws.com/images/93dbc38c-be6d-49cd-908c-54624453aa6c.jpg | Yes | 45 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/d9d7702d-4e23-4014-9526-418ce280fd09.jpg | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 30 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/c83e06f5-f9ce-4c81-8e81-2e54bd336163.jpg | 2014 | Normal | 1500 | Yes | 1 | -1.8146320670142189 | 29.982476016583142 | 1706.5 | 2bd2ka9c | https://waterforpeople.s3.amazonaws.com/images/e12057a9-8619-4426-96d2-17b912adf58c.jpg | 2014 | Normal | No | [5 empty] | Yes | 1 |  | 2014 | Normal | 200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8138750214852155 | 29.980131540744573 | 1723 | 2bbtbc9l | 2 | https://waterforpeople.s3.amazonaws.com/images/a62fe9f9-0f22-4eeb-90a9-d953452e3f24.jpg | 2014 | Poor | No |  |  |  | Yes |  | Normal | This network has 3 water points It serves 2 villages and one School | abf1ff76164177a63356aba48eb0
y0cf-9337-w6dy | 1 |  | J7 Rw8 | 1239460921 | 23-03-2017 10:06:57 CET | Amani Desire | 00:08:39 | 2017 | Rwanda | Rulindo | Murambi | Bubangu | Gashubi |  |  | Mutagata Motorised Network | 26296 |  | 140 | 29 | 111 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8365329449747418 | 30.027037076040543 | 1895.3 | 2cdaflf2 | 64 | https://waterforpeople.s3.amazonaws.com/images/6f80c8e8-9a58-44d3-a12c-cd45ec92ff7a.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | 869c274dd23e2a2a2e9c8c9f153e8
ww57-990w-ywe5 | 1 |  | J7 Rw26 | 1236450518 | 21-03-2017 14:10:45 CET | Byukusenge Elie | 00:10:36 | 2017 | Rwanda | Rulindo | Rukozo | Mbuye | Musare |  |  | Kabonanyoni | 7894 |  | 80 | 70 | 10 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 2015 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.61515730433033 | 29.953350181481273 | 2009.8 | 22761eq5 | 31 | https://waterforpeople.s3.amazonaws.com/images/61789843-dd13-4787-9e3f-2bc22706e470.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is located to the source Kabwiru I and the community use it as they do not pay for water. | dad6ca355c45e3fde421b4d75045b9ae
5u10-ts1d-reup | 1 |  | J7 Rw23 | 1243660377 | 24-03-2017 15:50:02 CET | Rugirangoga Augustin | 00:33:33 | 2017 | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | Nyagahera |  |  | 151 | 140 | 11 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | Kankanga ryanyirakayobe | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.69921094772796 | 30.01400249942007 | 1901.3 | 2626r6b0 |  | Yes | 16 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 16 | Yes | 1 |  | 2014 | Normal | 6800 | Yes | 3 | -1.9615191511514802 | 30.348630467018232 | 1652.3 | 2i3zf6f2 |  | 20114 | Poor | Yes | 3 | Distribution Chamber |  | 2014 | Normal | Yes | 1 |  | 2014 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7039157688511504 | 30.026314212577944 | 1623.5 | 269ykwpz | 1 | https://waterforpeople.s3.amazonaws.com/images/42fcd8bc-fd67-45fa-a18b-e9308f77a384.jpg | 2014 | Normal | No |  |  |  | Yes |  | Poor | the source of this network has not enough water. | f6727b40b1c94d805a991c6ed3d856c
xcff-ggh0-b5h0 | 1 |  | J7 Rw10 | 1305660106 | 16-04-2017 22:16:32 CEST | Tuyisenge Vianney | 00:08:11 | 2017 | Rwanda | Rulindo | Base | Gitare | Rugerero |  |  | Water point at Mbarusha/Nyirambuga pumping system | 30604 |  | 143 | 143 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | The water point chez Mbarusha operates well.The water is available however lacks so much on Nyirambuga pumping system which may make it a month | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6781514257198695 | 29.907789042543694 | 2058.6 | 253cw9hh | 2 | https://waterforpeople.s3.amazonaws.com/images/e4709e65-8754-49ff-b729-f3a97fdb953e.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | The water point chez Mbarusha operates well.The water is available however lacks so much on Nyirambuga pumping system which may make it a month | 4c39ce65b76de0e9828d1b864bb11e
ctsh-1g6h-7td3 | 1 |  | J7 Rw10 | 1228690275 | 02-01-2015 12:43:37 CET | Tuyisenge Vianney | 00:07:12 | 2017 | Rwanda | Rulindo | Buyoga | Busoro | Karambo |  |  | Water point2 at Gakoma/Nyirambuga pumping | 30604 |  | 138 | 138 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point at Karambo.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water. | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.7035841324836292 | 30.002505097259473 | 2007.8 | 269exlkp | https://waterforpeople.s3.amazonaws.com/images/a9bfe67c-ad26-44d8-86bd-f70d00029593.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7028178166636743 | 30.00462557773951 | 2005.1 | 2685380e | 2 | https://waterforpeople.s3.amazonaws.com/images/b8045663-4d14-43fc-b9b8-263143786552.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point at Karambo.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water. | a3bef8ac582187e9b89b511beb4c5b7e
mj6a-c769-ht05 | 1 |  | J7 Rw24 | 1219520786 | 16-03-2017 07:52:31 CET | Kabalisa Manzi Christella | 00:09:20 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Karambi |  |  | Rwamugaza | 14106 |  | 365 | 365 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government | no problem | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3.5 | Yes | 2 |  |  | 2003 | Normal | 3.5 | Yes | 1 |  | 2014 | Normal | 8000 | Yes | 10 | -1.7374173333138418 | 30.06563288387298 | 1723.9 | 27td31kg | https://waterforpeople.s3.amazonaws.com/images/42a07b42-310f-4840-94e6-a2a8db2d6487.jpg | 2003 | Poor | Yes | 8 |  | https://waterforpeople.s3.amazonaws.com/images/68fa7eba-8b5a-4310-81df-6c2164cd4f16.jpg | 2003 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.733304215316046 | 30.07005269097404 | 1591.8 | 27mkdvz0 | 1 | https://waterforpeople.s3.amazonaws.com/images/a7f9cac2-f356-4b50-b518-b49b2b02ae5d.jpg | 2014 | Poor | No |  |  |  | No | Water system has broken parts | Poor | No water Flowing | cd2339c94a93baf6b276f52d0502a77
ax22-wks5-ryce | 1 |  | J7 Rw15 | 1205920292 | 09-03-2017 17:18:46 CET | Mukakarangwa Assoumpta | 00:07:10 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Nyamirembe |  |  | kirikumuryango network |  |  | 256 | 120 | 136 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 500 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 10000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.9048164671297043 | 29.977801162429493 | 1362.9 | 2fi7nbk2 | 1 | https://waterforpeople.s3.amazonaws.com/images/792a757c-b291-4b2c-ab77-fa6707083480.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 799d1aff178f30f92a9f22ed78da3e9
mdvr-x07f-ygb5 | 1 |  | J7 Rw23 | 1217950505 | 15-03-2017 06:05:23 CET | Rugirangoga Augustin | 00:17:35 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Kabahama |  |  | Migogo | 558 |  | 178 | 150 | 28 | Yes | Piped Network -- Gravity Only |  | 2009 | Yes | kiruli Rubanda bukangano kabahama | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6327309674421784 | 29.901262305566668 | 1800.8 | 2308pft0 |  | No | 60 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2009 | Normal | 50 | Yes | 1 |  | 2009 | Poor | 6800 | Yes | 3 | -1.6327309674421784 | 29.901262305566668 | 1900.3 | 2308pft0 |  | 2009 | Poor | No | [5 empty] | Yes | 1 |  | 2009 | Poor | 6800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.637676012039191 | 29.89578152739776 | 1760.6 | 238etklp | 1 | https://waterforpeople.s3.amazonaws.com/images/7e325581-a241-4fc3-b2ae-6aa6dfac8ec1.jpg | 2009 | Poor | No |  |  |  | Yes |  | Poor | rehabilitation of some tanks and water taps | 7f1867e47ebd2623024acb9f4e7c9af
a3k4-2g2b-6qq0 | 1 |  | J7 Rw7 | 1227110606 | 24-03-2017 11:32:42 CET | Safari Bosco | 00:09:33 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Gacyamo | [5 empty] | 203 | 203 | 0 | Yes | Piped Network with Pump |  | 1998 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 1 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.824090498278462 | 30.063716138438927 | 1725.5 | 2bspsd5p | 2 | https://waterforpeople.s3.amazonaws.com/images/7bd32a60-d793-4b20-8fae-a33f35d7a710.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | ace83771553c66711b0606b6590a5a8
5e9a-0u6c-e489 | 1 |  | J7 Rw15 | 1220540430 | 12-03-2017 12:41:45 CET | Mukakarangwa Assoumpta | 00:14:18 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kagunda |  |  | Muvumu-Taba |  |  | 94 | 30 | 64 | Yes | Piped Network -- Gravity Only |  | 2013 | Yes | Muvumu | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.8242130164596562 | 29.931083430301516 | 1700.7 | 2bswxje6 |  | Yes | 25 | No | [5 empty] | 25 | Yes | 1 |  | 2013 | Normal | 800 | Yes | 3 | 1.828985219687556 | 29.926634523104315 | 1627.1 | 2c0sxawy |  | 2013 | Poor | Yes | 9 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 7500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8441022457140321 | 29.922425030333322 | 1629.8 | 2cpt4pjs | 1 | https://waterforpeople.s3.amazonaws.com/images/af4dcc9b-c023-4f22-8902-0fa5b212f61e.jpg | 2013 | Normal | Yes | 1 | 3 | Those rehabilitating Rushinya source had strayed it | Yes |  | Poor |  | 4c633ad076b6566257ff4eb5a386287
3fbe-rfj1-3xtt | 1 |  | J7 Rw24 | 1219050557 | 16-03-2017 08:27:29 CET | Kabalisa Manzi Christella | 00:08:01 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kamatongo |  |  | 0 | 6572 |  | 1125 | 1125 | 0 | Yes | Piped Network with Pump |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8024532750946713 | 30.042616473975034 | 1748.3 | 2asxebwq |  | Yes | 3 | Yes | 1 |  |  | 2016 | Normal | 3 | Yes | 1 |  | 2016 | Normal | 35000 | Yes | 3 | -1.767486275024945 | 30.035974538149265 | 1988.5 | 2973dhdz | https://waterforpeople.s3.amazonaws.com/images/2968c501-6c2c-4380-8fb8-6a644aec78cd.jpg | 2016 | Normal | Yes | 6 |  |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 35000 | Yes | 3 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7673096728665019 | 30.03922986229554 | 1920.5 | 296snoiw | 1 | https://waterforpeople.s3.amazonaws.com/images/09bf98f2-4644-4aad-8730-aa8a6b3b39f8.jpg | 2016 | Normal | No |  |  |  | No | Water seller was not around | Normal |  | a8def0627225dd5f9fa39582d97c94a1
m9h4-evjf-jjft | 1 |  | J7 Rw10 | 1234670432 | 03-01-2015 01:42:15 CET | Tuyisenge Vianney | 00:07:50 | 2017 | Rwanda | Rulindo | Tumba | Barari | Rukore |  |  | Water point at Rukore center/Nyirambuga pumping | 30604 |  | 157 | 157 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Rukore center water point operates well but among two tap valves one was damaged.The R25m3 storage tank valve chamber was removed | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.7050591212535062 | 29.946738909812453 | 2154.2 | 26bugb2j | https://waterforpeople.s3.amazonaws.com/images/6c500e64-353c-42ee-9f70-061909db39cf.jpg | 2012 | Normal | No | [5 empty] | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/bcc9460c-d554-494f-8070-a842407d58bc.jpg | 2015 | Normal | 2000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.705123645371419 | 29.946704980033648 | 2147.5 | 26bymcaz | 2 | https://waterforpeople.s3.amazonaws.com/images/fe3c5d26-2a2e-4f7b-b1fe-e413013477dc.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Rukore center water point operates well but among two tap valves one was damaged.The R25m3 storage tank valve chamber was removed | 69ec2095f188c9e270d51ad912d329
khmh-aeq9-cuxd | 1 |  | J7 Rw26 | 1239570167 | 21-03-2017 13:58:10 CET | Byukusenge Elie | 00:06:00 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Nyenyeri |  |  | Kabonanyoni | 7894 |  | 45 | 40 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Poor | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6514628539003968 | 29.964093417042264 | 1888.4 | 23v7ucc8 | 31 | https://waterforpeople.s3.amazonaws.com/images/4b164882-1240-46ac-87fc-ce87f8a1946c.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | It is functioning | c4ac14db0468edb2d1fb1a26fb63d1
sd64-j9nq-f75w | 1 |  | J7 Rw23 | 1236920505 | 23-03-2017 06:26:25 CET | Rugirangoga Augustin | 00:29:30 | 2017 | Rwanda | Rulindo | Kisaro | Sayo | Cyasuli |  |  | Kiruruma | 8295 |  | 129 | 122 | 7 | Yes | Piped Network with Pump |  | 2014 | Yes | rutabo gitaba nyarubuye remera rusongati rugarama cyasuli munini | Governement (District, WASAC) and Water For People | on this network one water tap does not get water | 1 | Groundwater (well, etc.) | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 15 | -1.6684773741137722 | 30.047381335897573 | 1775.8 | 24nckozd |  | 2014 | Normal | Yes | 4 | Sedimentation Tank |  | 2014 | Normal | Yes | 3 |  | 2014 | Normal | 4000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.67013989184797 | 30.027469752411616 | 2052.9 | 24q3en8y | 2 | https://waterforpeople.s3.amazonaws.com/images/78e6634c-19b1-4338-a6f8-87df9e3f8763.jpg | 2014 | Poor | No |  |  |  | Yes |  | Normal | this pumping network is working well | d9431929943a48cdaa156c751bf923ea
91vb-u2v1-ym1y | 1 |  | J7 Rw24 | 1255620235 | 28-03-2017 09:31:09 CEST | Kabalisa Manzi Christella | 00:08:05 | 2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Gakenke |  |  | Gahama Kisaro network | 10234 |  | 173 | 173 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6671501074688961 | 30.041830412153367 | 1945.4 | 24l5zh36 |  | Yes | 3 | Yes | 1 |  |  | 2012 | Normal | 3 | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 |  | https://waterforpeople.s3.amazonaws.com/images/ab6028aa-686a-435b-aafb-9d6274959939.jpg | 2012 | Poor | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Poor | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6244907202091547 | 30.045974281112464 | 2097.5 | 22mm4agb | 1 |  | 2012 | Poor | No |  |  |  | No | Road construction destroyed some pipes | Poor |  | 428d5f7d4218c928113a8d8a6be41d
9r9h-k2sw-8j9j | 1 |  | J7 Rw10 | 1213211811 | 13-03-2017 22:10:27 CET | Tuyisenge Vianney | 00:05:15 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Kivomo |  |  | Kivomo2 water point/Buramira gravity | 1255 |  | 127 | 127 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | GoR | The water point operates well | 1 | Spring | -1.6883400866741962 | 29.91133431277988 | 1897.9 | 25k7kyy1 |  | Yes | 30 | No | [5 empty] | 30 | No | [5 empty] | Yes | 1 | -1.6708862172307928 | 29.923827626910285 | 1775.9 | 24rc24ti | https://waterforpeople.s3.amazonaws.com/images/0c59cb48-dccc-49a8-b0c3-77547aeb25c0.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6709310111808717 | 29.923836281089763 | 1786 | 24rf1aue | 1 | https://waterforpeople.s3.amazonaws.com/images/91a1c49e-3d13-426e-960b-d59ce99f5b65.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The water source operates well | 6df3b8ad2f4bf43bc66155f998d1d0
c41r-v9yb-jyuk | 1 |  | J7 Rw26 | 1200040118 | 01-01-2015 19:47:40 CET | Byukusenge Elie | 00:15:26 | 2017 | Rwanda | Rulindo | Cyungo | Rwili | Nturo |  |  | Sakara |  |  | 570 | 520 | 50 | Yes | Piped Network with Pump |  | 2015 | Yes | Kivumu, Nturo, Nyabisasa and Sakara | Governement (District, WASAC) and Water For People | it has source Nyamagana shared with Nyamagana gravity and it was constructed in 2015 and the extensions ik Kivumu and Nyabisasa was constructed in 2016 and It is2 not yet used2 by the community and the pumping station use main distribution reservoir of Nyamagana gravity as the suction tank | 2 | Spring | -1.59199473719814 | 29.923957502559304 | 2015.8 | 214v5hgn |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1200 | Yes | 2 | -1.6031327755739937 | 29.922709284118525 | 2131.4 | 21naedcr |  | 2015 | Normal | Yes | 5 | Distribution Chamber |  | 2015 | Normal | Yes | 1 |  | 2016 | Normal | 2300 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.612849262913863 | 29.922724563079683 | 2016.1 | 223ci9qz | 4 | https://waterforpeople.s3.amazonaws.com/images/f9f43e67-ffdd-4a43-8865-0c53fcc52dc7.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is im good condition and it serves the Population of Nturo village | 87d69e3f7e3ec67c3ba815b45c9c2d8f
yn7h-g1aw-0t7 | 1 |  | J7 Rw26 | 1233040339 | 21-03-2017 13:51:44 CET | Byukusenge Elie | 00:05:56 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Rukingu |  |  | Kabonanyoni | 7894 |  | 30 | 25 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6341797595176593 | 29.963842725479964 | 1988.6 | 232mfvee | 31 | https://waterforpeople.s3.amazonaws.com/images/ecb42fc6-9cb4-49e3-9465-926241163792.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is used by the community in Centre Nturo | 6d8b8aab8a5124d76a9df2a185d0d77d
3aav-qwt1-vcmu | 1 |  | J7 Rw10 | 1237750258 | 03-01-2015 02:13:44 CET | Tuyisenge Vianney | 00:02:44 | 2017 | Rwanda | Rulindo | Tumba | Barari | Karambi |  |  | Karambi water point/Nyirambuga pumping | 30604 |  | 170 | 170 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Everything operates normally the water is available everyday | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7009823739135375 | 29.94419319742007 | 2092.8 | 26544vu9 | 2 | https://waterforpeople.s3.amazonaws.com/images/8b11a8ea-19f3-4087-a4c7-b4d04b7a7916.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Everything operates normally the water is available everyday | ae83bdcdd4a683dc6a35a33e95d7d272
gs73-xgg8-gchm | 1 |  | J7 Rw24 | 1224070138 | 16-03-2017 06:57:04 CET | Kabalisa Manzi Christella | 00:07:54 | 2017 | Rwanda | Rulindo | Burega | Karengeli | Rwamiko |  |  | Rwamugaza | 14106 |  | 440 | 440 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | no problem | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7270297291079906 | 30.02717229345762 | 1969 | 27c6hnqn | 1 | https://waterforpeople.s3.amazonaws.com/images/081aa602-ef6a-44a4-a0df-3d68aa87deec.jpg | 2012 | Normal | No |  |  |  | No | Water seller was not around | Normal | no problem | 92fdbfab36eb9f0cfad1e1ea62e6d2e
n1c9-8byk-tk0d | 1 |  | J7 Rw23 | 1325670054 | 23-04-2017 14:44:25 CEST | Rugirangoga Augustin | 00:48:47 | 2017 | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | kiduha | 0 |  | 151 | 105 | 46 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | kankanga gatenderi gatare shagasha | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 11 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2014 | Normal | No | [5 empty] | Yes | 32 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.702088413376497 | 30.028786957141097 | 1623.3 | 266xml1b | 1 | https://waterforpeople.s3.amazonaws.com/images/b67be169-2a97-4021-b819-3ad28261ceb3.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | 40114bb68b61bca5a30eeb6cd3b84a
s9gf-5xwx-guws | 1 |  | J7 Rw10 | 1217950910 | 14-03-2017 22:38:40 CET | Tuyisenge Vianney | 00:08:16 | 2017 | Rwanda | Rulindo | Rusiga | Kirenge | Rebero |  |  | Kigarama source/AEP Kigarama | 2621 |  | 243 | 243 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | GoR | The water source is well captured.It is protected. | 1 | Spring | -1.7875070118422336 | 29.92431620181639 | 2051.7 | 2a47b9m3 | https://waterforpeople.s3.amazonaws.com/images/84e93f86-9a7e-4841-b740-2ff6c693e2f5.jpg | Yes | 40 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/12489dc9-9002-4148-ab94-d0ce174c4e66.jpg | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/069d416b-5166-4dbe-ba84-866b5478117f.jpg | 2015 | Normal | 100 | Yes | 1 | -1.7874430063370603 | 29.9244215940554 | 735.8 | 2a43qnzg | https://waterforpeople.s3.amazonaws.com/images/79b834b6-05d2-4c82-a752-b94ecf784790.jpg | 2015 | Normal | Yes | 1 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/7a59503e-48ba-41bb-8ad9-28073404993f.jpg | 2015 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7874125223463622 | 29.92452272618698 | 2039.9 | 2a41yd65 | 1 | https://waterforpeople.s3.amazonaws.com/images/ab01608d-dbf0-4f6e-8aa1-e8012d3ea465.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The water points well.However there should wate meter to control the flow as well as renew the water valve | ef308e4ddd7da43838c55e6aeabf90a0
t5jk-ux9r-1s6n | 1 |  | J7 Rw10 | 1215100150 | 15-03-2017 20:07:16 CET | Tuyisenge Vianney | 00:07:07 | 2017 | Rwanda | Rulindo | Bushoki | Kayenzi | Gitaba |  |  | Gitaba water point/Nyirambuga pumping | 30604 |  | 118 | 118 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | GoR | This water point operates well and normally | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.6972113152394206 | 29.915355908862885 | 1942.6 | 25yvogk1 | https://waterforpeople.s3.amazonaws.com/images/9698c58f-a923-47b7-a8cd-4368d14bcf56.jpg | 2012 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6974624372477833 | 29.915206752513935 | 1929.1 | 25zakaog | 2 | https://waterforpeople.s3.amazonaws.com/images/7733ac7d-a653-4154-9619-9dfcfc5505ab.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Gitaba water point is in good conditions and it operates well | d8f3fe841bf165ae7eaef0f8f92da13d
hkyf-ksj4-3bmc | 1 |  | J7 Rw15 | 1242860146 | 21-03-2017 17:00:51 CET | Mukakarangwa Assoumpta | 00:06:51 | 2017 | Rwanda | Rulindo | Kinihira | Rebero | Kirwa |  |  | Miyove-Kinihira | 10452 |  | 187 | 95 | 92 | Yes | Piped Network -- Gravity Only |  | 1989 | No |  | KGWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6746329156858566 | 29.988279662973977 | 1846.1 | 24xjbp62 | 2 | https://waterforpeople.s3.amazonaws.com/images/7c325d86-5d9c-44ce-9a1f-2868b09c41f0.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | 2f839c5d1b5a2a1df50851350f9b8fe
txn0-srn0-h3r7 | 1 |  | J7 Rw8 | 1189941213 | 07-03-2017 20:57:53 CET | Amani Desire | 00:15:56 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gihonga |  |  | Kibuye | 1232 |  | 110 | 50 | 60 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | the network is new and it is in good operation condition | 2 | Spring | -1.7319103236390618 | 29.9285227727732 | 1850.6 | 27k9mlsl |  | Yes | 45 | Yes | 2 |  | start and collection chamber | 2016 | Normal | 45 | Yes | 1 |  | 2016 | Normal | 1500 | No | [8 empty] | Yes | 1 | washout chamber |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7247637976495984 | 29.930079063730215 | 1757.7 | 278fxo9w | 2 | https://waterforpeople.s3.amazonaws.com/images/069098f9-826d-4371-a166-682026544144.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | the network is new it is in a good operational condition water points are in good condition | 7960b663a96bf1853481771e0b6c5d6
b452-vvye-r6qh | 1 |  | J7 Rw26 | 1215680090 | 11-03-2017 10:02:18 CET | Byukusenge Elie | 00:14:04 | 2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 20456 |  | 200 | 180 | 20 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank | This network serves four sectors Cyungo,Rukozo, Base,Base and Kinihira, It has some problems in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible because it serves many populations and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6248815914931132 | 29.947169520669394 | 1868.2 | 22n9c6a7 | 29 | https://waterforpeople.s3.amazonaws.com/images/333dc9ed-7bd5-4dfc-8881-ba96244f4697.jpg | 2011 | Poor | Yes | 12 | 25 | Bad tee connections and the types of pipeline needs rehabilitation | No | No taps on the water tap | Poor | This water tap in Centre Rukozo in poor condition | 84b435312afc286925eb227f337649
9f91-jkcn-8bun | 1 |  | J7 Rw10 | 1217950916 | 14-03-2017 22:54:41 CET | Tuyisenge Vianney | 00:08:13 | 2017 | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Nyakabizi1 source/Nyakabizi1 gravity-Gakenke | 1259 |  | 200 | 200 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | Kingazi of Ruklindo and Busake of Gakenke | GoR | Source Nyakabizi1 located in Gakenke/Muhondo sect/Busake cel/Kibirizi vill | 1 | Spring | -1.801561587024314 | 29.92996135703427 | 2003.2 | 2argeq77 | https://waterforpeople.s3.amazonaws.com/images/0a79e404-be05-4bf9-a9a3-640e20b95370.jpg | Yes | 20 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/b981e91b-898b-4024-b6aa-085f7df574a8.jpg | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 20 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/6cc201f8-dd93-49f1-a8b3-b7236ac79060.jpg | 2015 | Normal | 100 | Yes | 1 | -1.8016433685572701 | 29.92997652180878 | 1927.8 | 2arl671f | https://waterforpeople.s3.amazonaws.com/images/c47eb777-4539-459f-bdca-02eff2f2fb4f.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.801609178196911 | 29.929676873632598 | 1927.5 | 2arisgm8 | 1 | https://waterforpeople.s3.amazonaws.com/images/b3d12c34-23a8-48fd-bf8f-c9ad04aadab4.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Source Nyakabizi1 located in Gakenke/Muhondo sect/Busake cel/Kibirizi vill | ed361eef424dda594e99e56451e4d25
es9f-hbdq-1q6x | 1 |  | J7 Rw15 | 1206960318 | 08-03-2017 21:09:19 CET | Mukakarangwa Assoumpta | 00:06:11 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 6436 |  | 165 | 20 | 145 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8559851802669034 | 29.974809304651675 | 1964 | 2d9gfomc | 1 | https://waterforpeople.s3.amazonaws.com/images/d085e122-22f7-4fd2-b702-79bce046c21c.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | 15b48c97b275f7ce408fda9a46f2f
8yut-8g63-qsa9 | 1 |  | J7 Rw15 | 1218850129 | 12-03-2017 13:28:10 CET | Mukakarangwa Assoumpta | 00:12:14 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Muvumu |  |  | Muvumu- Taba |  |  | 132 | 45 | 87 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.8242130164596562 | 29.931083430301516 | 1700.7 | 2bswxje6 |  | Yes | 25 | No | [5 empty] | 25 | Yes | 1 |  | 2013 | Normal | 800 | Yes | 3 | 1.828985219687556 | 29.926634523104315 | 1627.1 | 2c0sxawy |  | 2013 | Poor | Yes | 9 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 7500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8488310586655297 | 29.916348665531665 | 1637 | 2cxmqqmz | 1 | https://waterforpeople.s3.amazonaws.com/images/95ea0d5b-37ed-4374-af5c-4a7d403e28b5.jpg | 2013 | Normal | Yes | 1 | 3 | Those rehabilitating Rushinya source had strayed it | Yes |  | Poor |  | 53a1fa3289c23f2ffb4b7a3e29e5c1b6
t8df-scdf-4n5x | 1 |  | J7 Rw15 | 1212310408 | 12-03-2017 13:05:44 CET | Mukakarangwa Assoumpta | 00:08:16 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Kiviri |  |  | Muvumu- Taba |  |  | 135 | 60 | 75 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.8242130164596562 | 29.931083430301516 | 1700.7 | 2bswxje6 |  | Yes | 25 | No | [5 empty] | 25 | Yes | 1 |  | 2013 | Normal | 800 | Yes | 3 | 1.828985219687556 | 29.926634523104315 |  | 2c0sxawy |  | 2013 | Poor | Yes | 9 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 7500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8501689029058657 | 29.913455125695737 | 1571.1 | 2cztxe2m | 1 | https://waterforpeople.s3.amazonaws.com/images/d5024271-9072-4dd0-a3c5-a41dbd0a78ad.jpg | 2013 | Normal | Yes | 1 | 3 | Those rehabilitating Rushinya source had strayed it | Yes |  | Poor |  | 3d76f5f7ff51b6bf218a61a641f6d4eb
46uc-137j-gun | 1 |  | J7 Rw23 | 1327460051 | 23-04-2017 12:42:28 CEST | Rugirangoga Augustin | 00:10:47 | 2017 | Rwanda | Rulindo | Base | Gitare | Bushyiga |  |  | Gihanga | 2456 |  | 170 | 150 | 20 | Yes | Piped Network -- Gravity Only |  | 2014 | No |  | Governement (District, WASAC) and Water For People | This Water Point does not have enough Water | 1 | Spring | -1.641747305035919 | 29.90052447772513 | 1764.8 | 23f54zul | https://waterforpeople.s3.amazonaws.com/images/b740f251-339b-4596-84b0-1ca3f4f77b18.jpg | No | 65 | No | [5 empty] | 75 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6417718573262776 | 29.900526126502513 | 1760.6 | 23f6xanx | 1 | https://waterforpeople.s3.amazonaws.com/images/600614c3-9697-432e-b53e-56fa9cf83a08.jpg | 1978 | Poor | No |  |  |  | Yes |  | Poor | Low water flowing from source | f7b3ddd2352108d5732a17882dfc31c
w6um-51r5-unfg | 1 |  | J7 Rw26 | 1232820527 | 21-03-2017 13:47:47 CET | Byukusenge Elie | 00:41:16 | 2017 | Rwanda | Gicumbi | Miyove | Mubuga | Gatare |  |  | Kabonanyoni | 7894 |  | 30 | 20 | 10 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a | https://waterforpeople.s3.amazonaws.com/images/a35a515e-7148-43ef-8cf6-67866a5eb954.jpg | Yes | 15 | Yes | 5 | https://waterforpeople.s3.amazonaws.com/images/06823726-c7e1-48a8-99ce-f003d5f03e81.jpg | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/8757611b-ea7d-4dfb-83fd-fe9d8de44c35.jpg | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh | https://waterforpeople.s3.amazonaws.com/images/b75818ee-d31d-4c60-8db0-29ffe319ed36.jpg | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null | https://waterforpeople.s3.amazonaws.com/images/d553d398-47e5-4c1c-a4d0-eca91ce86c96.jpg | 2015 | Normal | Yes | 3 | https://waterforpeople.s3.amazonaws.com/images/8aa6f37d-4ddd-4be6-a765-08fb69750162.jpg | 2015 | Normal | 19000 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/578c32e2-f813-4eb3-b016-213047d87967.jpg | 2016 | Normal | Yes | https://waterforpeople.s3.amazonaws.com/images/c8c670d4-aa63-46a0-8136-400b675e033a.jpg | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6030105430606332 | 29.95355180689643 | 2052.7 | 21n396bz | 31 | https://waterforpeople.s3.amazonaws.com/images/6296ced8-a33e-4d3c-9bd4-47622c2c23a4.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This is the water tap of Gatare Source in Miyove sector ,Gicumbi district and is used by some community who are still in highrisk zone. | f4cb14043a8f86baf4da79a58482f
ahnv-n4c2-nb1d | 1 |  | J7 Rw23 | 1321250079 | 23-04-2017 14:44:09 CEST | Rugirangoga Augustin | 00:16:25 | 2017 | Rwanda | Rulindo | Buyoga | Butare | Kankanga |  |  | kiduha | 0 |  | 151 | 100 | 51 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | gatenderi gatare shagasha | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 11 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2014 | Normal | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.70217387967096 | 30.026956885441162 | 1609 | 2672zhgt | 2 | https://waterforpeople.s3.amazonaws.com/images/40972896-99cd-4135-b8ad-ace6081c09e8.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | 924fe6a3b4b30a4fae361facba4ea
cgsy-mqjg-mba1 | 1 |  | J7 Rw10 | 1275930092 | 05-04-2017 20:10:01 CEST | Tuyisenge Vianney | 00:16:59 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Terambere |  |  | Rutare-Nyirangarama gravity system/Water point at Terambere | 726 |  | 118 | 118 | 0 | Yes | Piped Network -- Gravity Only |  | 1960 | No |  | Government | Water point at Terambere is connected at Rutare-Nyirangarama gravity system and is operational though its infrastructure needs to be rehabilitated | 1 | Spring | -1.6705676828047722 | 29.878696276428556 | 2067 | 24qt0942 |  | Yes | 20 | No | [5 empty] | 20 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6682437048919116 | 29.88267662345614 | 1947.8 | 24myvosq | 1 | https://waterforpeople.s3.amazonaws.com/images/286e44cc-8cda-4ea4-ad19-e3b363841bfa.jpg | 1960 | Poor | No |  |  |  | Yes |  | Poor | Water point at Terambere is connected at Rutare-Nyirangarama gravity system and is operational though its infrastructure needs to be rehabilitated | c7d4d2105cdbcf89fc122b9022c52
v4ca-tqus-vp34 | 1 |  | J7 Rw26 | 1235770559 | 21-03-2017 13:53:00 CET | Byukusenge Elie | 00:05:57 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Kabingo |  |  | Kabonanyoni | 7894 |  | 40 | 35 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6381273880977407 | 29.96568403655198 | 2019 | 2395m3d4 | 31 | https://waterforpeople.s3.amazonaws.com/images/cfd24083-118b-4902-882b-1aeeba38644e.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is located near Kabingo Nursery. | fb9cb5b915c2aca5ce91782df78662f
uejt-4ywe-50dn | 1 |  | J7 Rw8 | 1236160600 | 22-03-2017 20:22:48 CET | Amani Desire | 00:13:58 | 2017 | Rwanda | Rulindo | Murambi | Mvuzo | Rurama |  |  | Mutagata Motorised Network | 26296 |  | 155 | 43 | 112 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout ,Air release and chlorination chambre |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2016 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.799589506359881 | 30.021749999809977 | 2111.1 | 2ao6ix4p | 64 | https://waterforpeople.s3.amazonaws.com/images/d4f26021-8dee-4ecd-a152-6c67e2322ffc.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | f4729497b69e9ab7b4cf09f29dd70c5
kk8a-yj3s-b6qw | 1 |  | J7 Rw10 | 1239820451 | 22-03-2017 14:22:31 CET | Tuyisenge Vianney | 00:09:39 | 2017 | Rwanda | Rulindo | Rusiga | Taba | Karambi |  |  | Water point at GS Gitanda/Nyakabizi gravity | 1259 |  | 109 | 109 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People | Water point not operational.Water services not delivered due to water unavailability.Infrastrure started getting damaged needs repair and maintenance | 2 | Spring | -1.803447729664134 | 29.930708856826865 | 1927.1 | 2aukc7xn |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8228581349139266 | 29.91889117172288 | 1683 | 2bqnyl10 | 2 | https://waterforpeople.s3.amazonaws.com/images/9ba4840f-3183-40af-8053-bee886818084.jpg | 2013 | Does Not Function | No |  |  |  | No | Water point not operational.Water services not delivered due to water unavailability.Infrastrure started getting damaged needs repair and maintenance | Does Not Function | Water point not operational.Water services not delivered due to water unavailability.Infrastrure started getting damaged needs repair and maintenance | d4ca5d9c9a419d7e3af65ae6117bb6
6sc9-y2jd-dm1 | 1 |  | J7 Rw8 | 1215472081 | 16-03-2017 08:54:52 CET | Amani Desire | 00:29:31 | 2017 | Rwanda | Rulindo | Mbogo | Bukro | Buhira |  |  | Musenge Network | 6074 |  | 52 | 52 | 0 | Yes | Piped Network with Pump |  | 2014 | Yes | gakoma,karehe,rutonde,gitaba,kiruli, buhira,ruhanya,kibamba,karindi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7659213640842732 | 29.94036224158598 | 1959.3 | 294ihua3 | 28 | https://waterforpeople.s3.amazonaws.com/images/c702eeb6-c357-4610-9ca8-961312745f45.jpg | 2014 | Does Not Function | Yes | 8 | 30 | all water served by R50m3 located at kibamba village do not have water today from last july 2016 | No | all water served by R50m3 located at kibamba village do not have water today from last july 2016 | Does Not Function | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | 8bce178af14bf8f8eb69b2f7bc29c89
6bda-jryj-cww0 | 1 |  | J7 Rw10 | 1304270085 | 18-04-2017 07:01:46 CEST | Tuyisenge Vianney | 00:04:52 | 2017 | Rwanda | Rulindo | Tumba | Gahabwa | Mafene |  |  | Water point chez Mukamponga/Nyirambuga pumping system | 30604 |  | 172 | 172 | 0 | Yes | Piped Network with Pump |  | 2017 | Yes | Mafene,Kabuga and Munyinya | Governement (District, WASAC) and Water For People | The water point is operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.721854799164435 | 29.94752447311533 | 2065.8 | 273mojdf | 2 | https://waterforpeople.s3.amazonaws.com/images/10d57452-21d7-45c1-b470-5eb62ea816fc.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | The water point is operational | 58429cf59a84f6a44dc93ce85d13e6f6
k8v1-ynvj-d46u | 1 |  | J7 Rw10 | 1221110195 | 13-03-2017 21:16:00 CET | Tuyisenge Vianney | 00:06:33 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Cyili |  |  | Cyili water point/Rutomvu gravity | 3015 |  | 169 | 169 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | The water source operates very well and the water point delivers well to the people | 1 | Spring | -1.677891751247546 | 29.90118126071259 | 1802.6 | 252xezpf |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | Yes | 1 | -1.6779120740545417 | 29.899143380844055 | 1773.8 | 252yluwf | https://waterforpeople.s3.amazonaws.com/images/f054b8f0-a345-400d-8609-a4e1782b2324.jpg | 2013 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6783646004563362 | 29.89818189408814 | 1757.7 | 253ped45 | 1 | https://waterforpeople.s3.amazonaws.com/images/9a95d178-0dc0-4db9-97cc-5b64e3173772.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | The water point operates very well | becb92349744539afc5e0a5a450a51d
wv70-aqnr-v8mg | 1 |  | J7 Rw15 | 1204990489 | 08-03-2017 22:44:04 CET | Mukakarangwa Assoumpta | 00:07:46 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Nyabisindu |  |  | kirikumuryango network |  |  | 149 | 38 | 111 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.891675896715459 | 29.97380235789691 | 1423.1 | 2ewhbqmy | 1 | https://waterforpeople.s3.amazonaws.com/images/efae16e5-e398-4a73-9037-f8d9959905f9.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | f07f2d885fcf94924a30e16af58f1dad
j25a-1xsc-way9 | 1 |  | J7 Rw19 | 1253880274 | 25-03-2017 10:50:31 CET | Kayinamura Innocent | 00:34:43 | 2017 | Rwanda | Rulindo | Masoro | Shengampuri | Rusine |  |  | Mutagata Gravity network | 26296 |  | 220 | 220 | 0 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | Ruri, Musenga, Rukurazo, Umubuga, Amataba, Rusine, Marenge |  |  | 1 | Spring | -1.8023389079852206 | 30.042447389592418 | 1691.2 | 2asq94nc |  | Yes | 8 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2004 | Poor | 8 | Yes | 1 |  | 2004 | Poor | 3500 | Yes | 6 | -1.8078446763653504 | 30.06649761552014 | 1669.8 | 2b1uaz5k |  | 2004 | Poor | Yes | 4 | Distribution Chamber¦Washout and Air release |  | 2004 | Poor | Yes | 2 |  | 2004 | Poor | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8142782281073475 | 30.089095529684137 | 1531.2 | 2bch4pay | 12 | https://waterforpeople.s3.amazonaws.com/images/7a7188ba-5e58-4684-bfd2-fb5b67da52ad.jpg | 2004 | Normal | No |  |  |  | Yes |  | Poor | 1. the Extension to Nyabinyana village has 2 reservoirs and two water points which is under construction 2. this system have been constructed in 2004 3. it serve a party of Masoro Sector and other party is located in Gasabo District 4. 2 water points and one reservoir have been constructed in 2016. 5. in general, this network has 27 water points in which 12 are in Rulindo District and the remaining are in Gasabo District. | ef496eb052a97a356e57c92fa96d0
nqrm-jdsm-gnmh | 1 |  | J7 Rw10 | 1214890813 | 14-03-2017 22:12:19 CET | Tuyisenge Vianney | 00:06:09 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kinini/Mbogo |  |  | Kinini-Mbogo water point/Ntaruka-Gahama gravity | 1567 |  | 188 | 188 | 0 | Yes | Piped Network -- Gravity Only |  | 2006 | No |  | GoR | This | 1 | Spring | -1.765657270137325 | 29.91982532317513 | 2061.6 | 2942f4se |  | Yes | 40 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2006 | Normal | 40 | Yes | 1 |  | 2006 | Normal | 100 | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7657616133876883 | 29.931772780171002 | 1802.9 | 2948ywj9 | 1 | https://waterforpeople.s3.amazonaws.com/images/392a9215-6617-4a38-b85f-48fd1d338411.jpg | 2006 | Poor | No |  |  |  | No | The water point does not meet the demand of the people.Water access should be put in place again and reduce the water cost to attract people | Poor | The water point does not meet the demand of the people.Water access should be put in place again and reduce the water cost to attract people | 7c8ac288a2c1e964dff693a44182fac
9t2y-cmg0-ygtj | 1 |  | J7 Rw23 | 1327450072 | 23-04-2017 14:42:02 CEST | Rugirangoga Augustin | 00:14:54 | 2017 | Rwanda | Rulindo | Buyoga | Mwumba | Nyarubuye |  |  | kiruruma | 8295 |  | 173 | 120 | 53 | Yes | Piped Network with Pump |  | 2014 | Yes | nyarubuye nyamwiza gatare gatenderi | Governement (District, WASAC) and Water For People | System under construction | 2 | Spring | -1.6829614865475908 | 30.031434012077444 | 1962 | 25bb9sey |  | Yes | 30 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 30 | Yes | 1 |  | 2014 | Normal | 6700 | Yes | 5 | -1.6902852583901373 | 30.03414 |  | 25nf3391 |  | 2014 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6755876594099404 | 30.00494604671302 | 1954 | 24z3vvrl | 2 | https://waterforpeople.s3.amazonaws.com/images/5a65b4e3-e158-44e2-9ef5-8c605c3f2968.jpg | 2017 | Does Not Function | No |  |  |  | Yes |  | Poor |  | c8a33b3bab7b641bfdd47fa84bdda42f
axtc-b33y-ne3k | 1 |  | J7 Rw7 | 1438950383 | 04-06-2017 13:25:29 CEST | Rugirangoga Augustin | 00:25:28 | 2017 | Rwanda | Rulindo | Kisaro | Murama | Mugomero |  |  | gahama | 10234 |  | 129 | 100 | 29 | Yes | Piped Network with Pump |  | 2012 | No |  | waterforpeople |  | 2 | Spring | -1.66758342977973980 | 30.042871221056 | 1965.7 | 24lvl43w |  | Yes | 30 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 20 | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 | Pressure Break Tank¦Distribution Chamber¦washout,air release |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6307681666382596 | 30.034369706983632 | 2197.1 | 22wzf2nr | 1 | https://waterforpeople.s3.amazonaws.com/images/af8db323-b7af-4e75-a86b-1ce30a11be23.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal |  | bc9762d3a2760962fc6e72b97e4f5eb
hrr2-5dcq-bs20 | 1 |  | J7 Rw26 | 1239570181 | 21-03-2017 14:05:23 CET | Byukusenge Elie | 00:07:43 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Kabgayi |  |  | Kabonanyoni | 7894 |  | 60 | 55 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.644608121279173 | 29.973181989913982 | 1795.5 | 23jvezf7 | 31 | https://waterforpeople.s3.amazonaws.com/images/264fa75c-8ca5-41a1-a251-79a7f8d48db7.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water tap is in good condition but the community use the protected spring. | 4c37336a2ef5ee886bbb594868db96
gfq8-04jt-uhb8 | 1 |  | J7 Rw19 | 1230540158 | 17-03-2017 05:24:57 CET | Kayinamura Innocent | 00:28:28 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gakoma |  |  | Musenge network | 6074 |  | 146 | 46 | 100 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma, Karehe, Rutonde, Gitaba, Kiruri, Buhera, Ruhanya, Kibamba and Karindi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Washout and Air release chamber |  | 2014 | Normal | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7827454343560414 | 29.952622284421526 | 2100.8 | 29wbwxvq | 28 | https://waterforpeople.s3.amazonaws.com/images/c26db833-6054-487b-8fa9-f54eb57076aa.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | 1. the system has two Pumps but one is damaged and is not working, only one pump is used to pump water 2. Eleven (11) watre points served by the distribution reservoir R 50m3 located at Kibamba village do not have water today because water don't reach this reservoir, there is not water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5. one water point doesn't Function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | ff55cb3f94c492f293fad4aba370bb79
2386-20jt-dr4h | 1 |  | J7 Rw10 | 1313980109 | 20-04-2017 17:41:51 CEST | Tuyisenge Vianney | 00:06:03 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Nkanga |  |  | Nkanga center water point/Kivomo-Ntakara gravity |  |  | 129 | 129 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | Nkanga and Ntakara villages | Governement (District, WASAC) and Water For People | Not operational | 1 | Spring | -1.827334932521246 | 29.9509016093900119431 | 1943.1 | 2by2osad |  | Yes | 50 | No | [5 empty] | 50 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8199834869881402 | 29.962226888233022 | 1679.4 | 2blx36qu | 1 | https://waterforpeople.s3.amazonaws.com/images/7d226069-6654-437f-a8b8-fc1833eef511.jpg | 2015 | Does Not Function | No |  |  |  | No | not operational | Does Not Function | Not operational | e02dc0e13f9510db59b211d610ddd862
78x5-b5bt-wmrx | 1 |  | J7 Rw15 | 1217950127 | 12-03-2017 13:32:54 CET | Mukakarangwa Assoumpta | 00:09:56 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Nyabubare |  |  | Muvumu- Taba |  |  | 97 | 40 | 57 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.8242130164596562 | 29.931083430301516 | 1700.7 | 2bswxje6 |  | Yes | 25 | No | [5 empty] | 25 | Yes | 1 |  | 2013 | Normal | 800 | Yes | 3 | 1.828985219687556 | 29.926634523104315 | 1627.1 | 2c0sxawy |  | 2013 | Poor | Yes | 9 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 7500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8539602603750878 | 29.91532827723735 | 1496.7 | 2d6463yp | 1 | https://waterforpeople.s3.amazonaws.com/images/a83004b3-6baa-461b-8bea-4f00069b846c.jpg | 2013 | Normal | Yes | 1 | 3 | Those rehabilitating Rushinya source had strayed it | Yes |  | Poor |  | 8935cb184c3c3d411b36d4758548c7b
d0ua-6cfv-t36v | 1 |  | J7 Rw15 | 1241830091 | 21-03-2017 14:19:30 CET | Mukakarangwa Assoumpta | 00:07:14 | 2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Mutoyi |  |  | Miyove-Kinihira | 10452 |  | 119 | 60 | 59 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.89395927041342 | 2023.9 | 24j8bq63 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6528114915534222 | 29.982628973279862 | 1793.7 | 23xg7v5e | 2 | https://waterforpeople.s3.amazonaws.com/images/4b21da6e-7498-4c39-80de-1758c0f2e6f2.jpg | 2015 | Normal | No |  |  |  | Yes |  | Poor |  | 9dbfe34867475b833809311ae78a972
ghb3-brj2-edf9 | 1 |  | J7 Rw23 | 1251460062 | 27-03-2017 07:17:48 CEST | Rugirangoga Augustin | 00:43:46 | 2017 | Rwanda | Rulindo | Buyoga | Ndarage | Gahondo |  |  | Ndarage |  |  | 105 | 100 | 5 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | karambi Gahondo Bunyana Rugarama Gasave | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.6829614865475908 | 30.031434012077444 | 1962.1 | 25bb9sey |  | Yes | 30 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 30 | Yes | 1 |  | 2014 | Normal | 6300 | Yes | 5 | -1.6902852583901373 | 30.03414816539013 | 1811.8 | 25nf3391 |  | 2014 | Normal | Yes | 8 | Distribution Chamber |  | 2014 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.687035867730842 | 30.031244147733165 | 1794.8 | 25i1l7mg | 2 | https://waterforpeople.s3.amazonaws.com/images/eadfc520-98a1-450a-bc9e-564a39df57f8.jpg | 2014 | Poor | No |  |  |  | Yes |  | Normal |  | c172e1ab9ad86d3638fa6a593921890
p8u9-udyh-j9xt | 1 |  | J7 Rw19 | 1315910276 | 20-04-2017 14:45:32 CEST | Kayinamura Innocent | 00:25:46 | 2017 | Rwanda | Rulindo | Mbogo | Mushali | Gitaba |  |  | Gitabage Network |  |  | 118 | 68 | 50 | Yes | Piped Network -- Gravity Only |  | 2008 | Yes | Bukongi | Catholic Church |  | 1 | Spring | -1.7894191074184786 | 29.98061378695303 | 1922.2 | 2a7d12la | https://waterforpeople.s3.amazonaws.com/images/8abe7fe2-0483-4dd7-8512-66a986fd1914.jpg | Yes | 40 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/34dc2902-339a-457c-809d-25c3f0268e52.jpg | "Springbox" --Intake Structure at a Spring | 2008 | Normal | 40 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/e1c7bd14-0417-4229-87d2-4c7dd593ac30.jpg | 2008 | Normal | 700 | Yes | 2 | -1.7927177501595748 | 29.982999206837842 | 1821.5 | 2acti48l | https://waterforpeople.s3.amazonaws.com/images/1f3583ee-bb63-4d8d-b807-962a13952fa2.jpg | 2008 | Normal | No | [5 empty] | Yes | 1 |  | 2008 | Normal | 500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7890012068731995 | 29.980890990319377 | 1889.1 | 2a6omasg | 3 | https://waterforpeople.s3.amazonaws.com/images/81a12389-3fae-4079-9bb0-a15e5a784020.jpg | 2008 | Poor | No |  |  |  | Yes |  | Normal | This network has 3 water points It serves 2 villages and one School | b0cec080212cbcadc421606c1f321ed5
4c82-t708-9ucg | 1 |  | J7 Rw10 | 1229020219 | 03-01-2015 02:15:31 CET | Tuyisenge Vianney | 00:02:30 | 2017 | Rwanda | Rulindo | Tumba | Barari | Karambi |  |  | Karambi2 water point/Nyirambuga pumping | 30604 |  | 170 | 170 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Everything operates normally the water is available everyday | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7053426587670815 | 29.93912621522902 | 2094.4 | 26cbpvjz | 2 | https://waterforpeople.s3.amazonaws.com/images/7dbe933a-04d7-4285-9ce1-c8b6b649f433.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Everything operates normally the water is available everyday | ac36c64c2f69f279d49542815cff63e
30ns-w29v-u7qx | 1 |  | J7 Rw15 | 1211680150 | 08-03-2017 20:20:11 CET | Mukakarangwa Assoumpta | 00:07:59 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | kinywamagana pumping network | 6436 |  | 281 | 50 | 231 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8378240574466125 | 29.947774036176963 | 1884.5 | 2cff8hud | 1 | https://waterforpeople.s3.amazonaws.com/images/410a337f-6475-4014-86da-83326d164d9c.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | a35aa6b0a2acd376f018ae63ff40feab
45ff-wpyd-b0ya | 1 |  | J7 Rw10 | 1307400049 | 16-04-2017 21:07:26 CEST | Tuyisenge Vianney | 00:10:09 | 2017 | Rwanda | Rulindo | Bushoki | Mukoto | Mukoto |  |  | Mukoto water point/Nyagahondo gravity system | 844 |  | 119 | 119 | 0 | Yes | Piped Network -- Gravity Only |  | 2010 | No |  | Caritas | This is Mukoto water point connected to Nyagahondo gravity system.It is nolonger in operation neither functioning | 1 | Spring | -1.7298781428197503 | 29.909858739201194 | 2099.2 | 27gw668q |  | Yes | 30 | No | [5 empty] | 30 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7128522882499273 | 29.916479645931865 | 1744.1 | 26oqueos | 1 | https://waterforpeople.s3.amazonaws.com/images/8d74afd2-aa51-40f6-ac17-5d841fc53d58.jpg | 2010 | Does Not Function | No |  |  |  | No | This is Mukoto water point connected to Nyagahondo gravity system.It is nolonger in operation neither functioning | Does Not Function | This is Mukoto water point connected to Nyagahondo gravity system.It is nolonger in operation neither functioning | 316af4e1c237f691fd6a29434de4994
4cmd-vnju-ggkq | 1 |  | J7 Rw15 | 1239570585 | 22-03-2017 19:12:31 CET | Mukakarangwa Assoumpta | 00:09:13 | 2017 | Rwanda | Rulindo | Kinihira | Butunzi | Ndorandi |  |  | Nyamagana-Kinihira |  |  | 139 | 50 | 89 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦Ventouse,Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.671444406067911 | 29.950382920396084 | 1903.7 | 24s9eewf | 2 | https://waterforpeople.s3.amazonaws.com/images/ffd0cafd-d004-4f93-a69b-023ba5c48a76.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | c2cebd3ecc6be53468b770bea6c5907a
rw0c-k0ke-bcn2 | 1 |  | J7 Rw24 | 1208321137 | 16-03-2017 08:38:05 CET | Kabalisa Manzi Christella | 00:08:19 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kigarama |  |  | charity water 203.031 | 6572 |  | 1165 | 1165 | 0 | Yes | Piped Network with Pump |  | 2016 | No |  | Governement (District, WASAC) and Water For People |  | 3 | Spring | -1.8024532750946713 | 30.0426473975034 | 1748.3 | 2asxebwq |  | Yes | 3 | Yes | 1 |  |  | 2016 | Normal | 3 | Yes | 1 |  | 2016 | Normal | 35000 | Yes | 10 | -1.767486275024945 | 30.035974538149265 | 1988.5 | 2973dhdz |  | 2016 | Normal | Yes | 8 |  |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 1000 | Yes | 3 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7627720456478893 | 30.032516425751357 | 1939.2 | 28zaybfp | 1 | https://waterforpeople.s3.amazonaws.com/images/8629462e-97dc-414c-ac6e-67b78cf51e3f.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 92146f40fe7249ef294c2e41de6e6550
cvh7-qp86-p3ew | 1 |  | J7 Rw10 | 1232890295 | 02-01-2015 12:26:42 CET | Tuyisenge Vianney | 00:05:53 | 2017 | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point for People near Buyoga secondary school/Nyirambuga pumping | 30604 |  | 177 | 177 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Operational but to refix valve tap.Water point near Buyoga secondary school.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.694352880338091 | 30.01174076225681 | 2068.3 | 25u5eiad | 2 | https://waterforpeople.s3.amazonaws.com/images/4afd8963-60b3-4d13-96e1-fb3d75cf3752.jpg | 2015 | Poor | No |  |  |  | Yes |  | Poor | Operational but to refix valve tap.Water point near Buyoga secondary school.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water | 8434f5d4b882513d4df551cae3451
x5nn-haq1-2yxn | 1 |  | J7 Rw10 | 1232890290 | 02-01-2015 13:12:45 CET | Tuyisenge Vianney | 00:06:07 | 2017 | Rwanda | Rulindo | Buyoga | Karama | Cyasenga |  |  | Water point at grouped area of Cyasenga/Nyirambuga | 30604 |  | 165 | 165 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point grouped area of Cyasenga.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water.Several valve chambers are nolonger having covers. | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7134673585534292 | 29.977772658192993 | 2090.5 | 26pr5v29 | 2 | https://waterforpeople.s3.amazonaws.com/images/c1ea4743-cb50-46fa-b0d7-bd6b62240090.jpg | 2015 | Poor | No |  |  |  | Yes |  | Normal | Water point grouped area of Cyasenga.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water.One water tap valve was damaged and removed | c9a81b51f76abbe6d3e6cf9fdc1248a
4k83-pnaj-s2pm | 1 |  | J7 Rw10 | 1244490436 | 22-03-2017 14:30:06 CET | Tuyisenge Vianney | 00:09:14 | 2017 | Rwanda | Rulindo | Rusiga | Kirenge | Kigarama |  |  | Kigarama water point[Charity:Water203.148]/AEP Kigarama gravity | 2621 |  | 243 | 243 | 0 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | This is one of water points located in grouped area Kigarama village.It is normally operational and functional | 1 | Spring | -1.7875070118422336 | 29.92431620181639 | 2051.7 | 2a47b9m3 |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | Yes | 1 | -1.7789432435756314 | 29.930795867088854 | 1907.8 | 29q1o7u3 | https://waterforpeople.s3.amazonaws.com/images/6d049b98-81cc-40f8-889b-4f9f94c889f9.jpg | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.779400248814247 | 29.93227734885672 | 1849.7 | 29qt25oa | 2 | https://waterforpeople.s3.amazonaws.com/images/6991241c-ab87-46b4-8360-5d4303aa6906.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | This is one of water points located in grouped area Kigarama village.It is normally operational and functional | d24b73371bd8d2a91bb0635c7384
9xp8-smj0-es4k | 1 |  | J7 Rw10 | 1225420535 | 14-03-2017 22:20:08 CET | Tuyisenge Vianney | 00:10:26 | 2017 | Rwanda | Rulindo | Rusiga | Kirenge | Ntaruka |  |  | Ntaruka source/Ntaruka-Gahama gravity | 1567 |  | 176 | 176 | 0 | Yes | Piped Network -- Gravity Only |  | 2006 | No |  | GoR | The water source is well captured and protected. | 2 | Spring | -1.765657270137325 | 29.91982532317513 | 2061.6 | 2942f4se | https://waterforpeople.s3.amazonaws.com/images/447ce678-7eeb-410d-be5f-44aeb413f28f.jpg | Yes | 40 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/ffa11c13-0675-4c3e-90bf-17cca79d4dd9.jpg | "Springbox" --Intake Structure at a Spring | 2006 | Normal | 40 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/8a99aabf-2a48-4142-8f76-2f13d436d23c.jpg | 2006 | Normal | 100 | Yes | 1 | -1.7657041344779334 | 29.920260309723567 | 2074.7 | 2945eate | https://waterforpeople.s3.amazonaws.com/images/9fb6412b-fe8a-433c-b42f-5a9cffbe878b.jpg | 2006 | Normal | No | [5 empty] | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/7907ea29-815b-4e47-ae79-0fbab6a4ef93.jpg | 2006 | Normal | 1000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7655865926339016 | 29.92024400695498 | 2059.2 | 293y93k2 | 1 | https://waterforpeople.s3.amazonaws.com/images/6c45ed3a-bd70-4fc5-8e24-f8378603104a.jpg | 2006 | Normal | No |  |  |  | Yes |  | Normal | The water source is well captured and protected | 50fbf0d16a667725d4f5e60922af6d0
mu6w-eaqe-3aru | 1 |  | J7 Rw10 | 1301820105 | 14-04-2017 22:27:58 CEST | Tuyisenge Vianney | 00:04:12 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Budaha |  |  | Budaha water point/Nkombe gravity system |  |  | 205 | 205 | 0 | Yes | Piped Network -- Gravity Only |  | 2002 | No |  | COFORWA | This is water point located in Budaha at the peak opposite to Gitwa and at top of Gasiza.It operates poorly with few water as well as with tap removed | 1 | Spring | -1.726263209282046 | 29.90351686333194 | 2121.4 | 27ax8ot7 |  | Yes | 18 | No | [5 empty] | 18 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7253775757931566 | 29.91712396933418 | 1877.9 | 279g942r | 1 | https://waterforpeople.s3.amazonaws.com/images/5d0e0f3e-9a4c-413b-b305-e35a69268943.jpg | 2002 | Poor | No |  |  |  | Yes |  | Poor | This is water point located in Budaha at the peak opposite to Gitwa and at top of Gasiza.It operates poorly with few water as well as with tap removed | 7ccb6f830e6a79a2b7d1b9502e1d18
5svc-0m4f-ymr | 1 |  | J7 Rw10 | 1301320108 | 16-04-2017 22:31:15 CEST | Tuyisenge Vianney | 00:07:48 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Gashiru |  |  | Water point at Marembo center/Nyirambuga pumping system | 30604 |  | 120 | 120 | 0 | Yes | Piped Network with Pump |  | 2012 | Yes | Buramira and Gashiru | Governement (District, WASAC) and Water For People | In use,operational and water available | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.6866673599584476 | 29.913563956163582 | 2117 | 25hfk5bz | https://waterforpeople.s3.amazonaws.com/images/e29794cb-d44c-4b7d-8158-ca9cd0c0f786.jpg | 2012 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6870268077292736 | 29.913818282304987 | 2121.2 | 25i0zr42 | 1 | https://waterforpeople.s3.amazonaws.com/images/18624088-0d2d-4e7e-adde-ab2344f3ba6f.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | In use,operational and water available | efa4eff0f56694f2c88b2fb1e91dca8
jnpt-wv5n-6rsk | 1 |  | J7 Rw23 | 1220280081 | 16-03-2017 01:36:41 CET | Rugirangoga Augustin | 00:45:00 | 2017 | Rwanda | Rulindo | Base | Gitare | Nyamugali |  |  | Rutembe | 1012 |  | 121 | 65 | 56 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | This Systems Functions well | 2 | Spring | -1.6511266219663017 | 29.88205635445047 | 1696.8 | 23unll50 |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 1 |  | 2016 | Normal | 2500 | Yes | 1 | -1.6509217634187945 | 29.884295403163026 | 1711.9 | 23ubox22 |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6517837462538751 | 29.88425548115787 | 1723.2 | 23vqw72y | 2 |  | 2017 | Does Not Function | Yes | 7 | 7 | it is because some pipes were damaged | No | water does not reach into the last storage tank | Poor | Water reach tank depending to the position of it position and the position of the source.(1696.8 elevation of source is less than 1711.9 which is the elevation of storage tank | 4a853672967da88bf93576c1ea4604b
uvuk-bc3t-r1e0 | 1 |  | J7 Rw8 | 1208930838 | 10-03-2017 10:19:09 CET | Amani Desire | 00:34:06 | 2017 | Rwanda | Rulindo | Ngoma | Karambo | Karambi |  |  | Kabarore-Ngoma-Nyabuko network | 8284 |  | 117 | 30 | 87 | Yes | Piped Network with Pump |  | 2014 | Yes | nyabuko,kagwa,kiruli,busizi,ngaru,kirungu,kiboha,kigina | Governement (District, WASAC) and Water For People | the network has 17 water points and it serves 8 villages | 4 | Spring | -1.8123357076877171 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦collection chamber | 2014 | Poor | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.808716485895084 | 29.973362007273437 | 1783.9 | 2b3a3o2d |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8255811977247869 | 29.975787299752984 | 1904.9 | 2bv6hxm5 | 17 | https://waterforpeople.s3.amazonaws.com/images/bfe31955-6b7f-418a-a204-da0d15a41158.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | -The network has 17 water points -water are in good operational condition except the water point at the source that is damaged -4 water points don't have water today -The pipes are in good conditions -The pump is not working properly as it was expected during Design , Today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy -The transformer at the pumping station doesnt offer the required energy for the pump -The system has two pumps with four units with two units pumping in one direction towards Nyabuko and other two in an other direction towards ngoma sector office -The suction tank is in bad physical condition | d6674e384ebc7e4815381d91f8f6a3
1k8q-cnu5-c1vt | 1 |  | J7 Rw15 | 1235771102 | 22-03-2017 18:56:58 CET | Mukakarangwa Assoumpta | 00:09:10 | 2017 | Rwanda | Rulindo | Kinihira | Butunzi | Kiniihira |  |  | Nyamagana-Kinihira |  |  | 118 | 60 | 58 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦Ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6688513326963186 | 29.958808765190494 | 1957 | 24nz75ac | 3 | https://waterforpeople.s3.amazonaws.com/images/f0d169cd-a7ac-45b1-86b4-586ce3618740.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | e1529642e13a134cccc67f4dc835cb64
7yqy-q6c1-keg0 | 1 |  | J7 Rw24 | 1256640094 | 28-03-2017 08:31:03 CEST | Kabalisa Manzi Christella | 00:06:05 | 2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Karera |  |  | Rwamugaza network | 14106 |  | 182 | 182 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  | https://waterforpeople.s3.amazonaws.com/images/844fbe73-fef8-49ab-a199-b032d1868616.jpg | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7945288178951202 | 30.09627077913941 | 1744.8 | 2aft9llu | 1 | https://waterforpeople.s3.amazonaws.com/images/746dd2f4-ed83-429b-88f1-2d816c84dd6c.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | a4135599c574ec751bac57afd5351
7ymq-usek-90x8 | 1 |  | J7 Rw24 | 1327770049 | 24-04-2017 23:51:27 CEST | Kabalisa Manzi Christella | 00:12:41 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyarurama |  |  | Rwamugaza network | 14106 |  | 168 | 168 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7374173333138418 | 30.006563288387278 | 1723.9 | 27td3141 |  | 2003 | Normal | Yes | 14 |  |  | 2003 | Normal | Yes | 1 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.752481721740589 | 30.05797587075162 | 1764.6 | 28iaba5f | 1 | https://waterforpeople.s3.amazonaws.com/images/6ecbfd7d-0d05-4873-92aa-d14cb313a3a7.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | 1dfe952dfb26ff9b64ebe8ff5f25c83
byp7-pjw6-6js6 | 1 |  | J7 Rw23 | 1324690060 | 23-04-2017 15:41:31 CEST | Rugirangoga Augustin | 00:19:42 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Gitwa |  |  | Gihanga | 2456 |  | 104 | 80 | 24 | Yes | Piped Network -- Gravity Only |  | 1980 | Yes | gihanga | Governement (District, WASAC) and Water For People | This Systems Functions well | 1 | Spring | -1.66922136727874054 | 30.02146392212493 | 1866.9 | 24ol875i |  | No | 70 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 1985 | Normal | 60 | Yes | 1 |  | 2014 | Normal | 5000 | Yes | 2 | -1.6932117321635163 | 30.026191374639453 | 1765.8 | 25s9j3fp |  | 2014 | Poor | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6547237248616216 | 29.90644452261734 | 1769.9 | 240lxn3s | 2 | https://waterforpeople.s3.amazonaws.com/images/b2b28224-318c-41e1-80ba-9b59b38639b4.jpg | 2014 | Normal | Yes | 2 | 2 | Not well constructed | No | Broken parts | Poor |  | 54492efde944f06948b1e1feaca53623
sp5k-x1ee-xt1f | 1 |  | J7 Rw23 | 1325590092 | 23-04-2017 14:41:22 CEST | Rugirangoga Augustin | 00:10:00 | 2017 | Rwanda | Rulindo | Buyoga | Mwumba | Murambo |  |  | Kiruruma | 8295 |  | 136 | 100 | 36 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | Water system is not yet functional it is being built | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 11 | -1.684773741137722 | 29.8839135826884 | 1775.8 | 25eb17rr |  | 2014 | Normal | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6840349413363755 | 30.009187265451065 | 2002.9 | 25d2z5yz | 2 | https://waterforpeople.s3.amazonaws.com/images/cbaa32cc-c4c2-4924-8567-fd629d167d57.jpg | 2014 | Does Not Function | No |  |  |  | Yes |  | Poor |  | 1efb16a7171f7f597815680ceba6a
7hwk-0ndf-v002 | 1 |  | J7 Rw26 | 1200570601 | 07-03-2017 09:51:30 CET | Byukusenge Elie | 00:25:20 | 2017 | Rwanda | Rulindo | Cyungo | Marembo | Rusayo |  |  | Nyabirarama |  |  | 150 | 100 | 50 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This network has two water taps and It serves the Population of Ruyayo Village and the main purpose is to serve G.S.Nganzo | 1 | Spring | -1.604039112491394 | 29.911449592055785 | 2015.7 | 21orzdpm | https://waterforpeople.s3.amazonaws.com/images/5e9bc70a-e337-49f3-9298-48944ab9bf53.jpg | Yes | 150 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/6d9f43ea-2e3e-47f2-93da-111b4015d8d7.jpg | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 150 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/539713fc-46cb-4355-8d80-99085a6b2a83.jpg | 2015 | Normal | 1200 | Yes | 1 | -1.6034700300768703 | 29.91505418395048 | 1924.9 | 21nun3v2 | https://waterforpeople.s3.amazonaws.com/images/7fcde4e2-2978-4ede-b662-d479038593b5.jpg | 2015 | Normal | Yes | 1 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/2cac6e3f-7c43-4ca6-b3c5-cb134673eb34.jpg | 2015 | Normal | Yes | 1 |  | 2015 | Normal | 1200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6030308859853388 | 29.91505846517413 | 1920.1 | 21n4g18u | 2 | https://waterforpeople.s3.amazonaws.com/images/4e2a7209-8e7b-45b8-aff3-d99bf49686d9.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The network have been used by G.S.Nganzo school and the Population used the water tap on the source | f4cb23282ad0df3749608ef788cac497
snft-kj4m-b3np | 1 |  | J7 Rw24 | 1326080072 | 25-04-2017 17:05:28 CEST | Kabalisa Manzi Christella | 00:17:38 | 2017 | Rwanda | Rulindo | Cyinzuzi | Rudogo | Gaseke |  |  | Nyamateke network | 0 |  | 127 | 127 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7521357636267942 | 30.004650031976542 | 1829.2 | 28hph3ke | https://waterforpeople.s3.amazonaws.com/images/a4b9dcdb-8401-4b85-ba43-303e2a614c6a.jpg | No | 50 | Yes | 1 |  |  | 2003 | Normal | 20 | Yes | 2 |  | 2011 | Normal | 30000 | Yes | 5 | -1.7521357636267942 | 30.004650031976542 | 1829.2 | 28hph3ke |  | 2003 | Poor | Yes | 6 |  | https://waterforpeople.s3.amazonaws.com/images/31bd56fe-87f2-4131-a177-c44c99ff8ce4.jpg | 2003 | Does Not Function | Yes | 1 |  | 2011 | Normal | 30000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7521357636267942 | 30.004650031976542 | 1829.2 | 28hph3ke | 1 | https://waterforpeople.s3.amazonaws.com/images/da08e1c9-c1b1-42ed-a9c3-f2dd36609a19.jpg | 2003 | Normal | No |  |  |  | No | Broken parts | Does Not Function |  | a2da75bee22fe49bdf1d607c9b3dc837
twjn-6r80-tdka | 1 |  | J7 Rw15 | 1205330143 | 08-03-2017 18:41:59 CET | Mukakarangwa Assoumpta | 00:18:26 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kiziranyenzi |  |  | kinywamagana pumping network | 6436 |  | 140 | 40 | 100 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People | Water does not reach this water point(abaturage bavoma igishanga) | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8478874690537923 | 29.98380026724029 | 1746.1 | 2cw26kou | 1 | https://waterforpeople.s3.amazonaws.com/images/b3b8c83e-2565-4a3c-94d9-f0b486a21b6b.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | dddde7f0e2e3caffbe843889d39a4fe1
gqgu-83m6-jkj7 | 1 |  | J7 Rw10 | 1277920049 | 05-04-2017 20:56:20 CEST | Tuyisenge Vianney | 00:05:47 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Terambere |  |  | Rutare-Nyirangarama gravity system/Terambere water point | 726 |  | 118 | 118 | 0 | Yes | Piped Network -- Gravity Only |  | 1960 | No |  | Government | Rutare-Nyirangarama gravity system/Terambere water point does nolonger operate | 1 | Spring | -1.6705676828047722 | 29.878696276428556 | 2067 | 24qt0942 |  | Yes | 20 | No | [5 empty] | 20 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6704185810555394 | 29.878936241296852 | 2015 | 24qk2r1h | 0 | https://waterforpeople.s3.amazonaws.com/images/dd351841-dba6-45fb-ac11-8198f65cb3a1.jpg | 1960 | Does Not Function | No |  |  |  | No | It got demolished and does no longer operate | Does Not Function | Rutare-Nyirangarama gravity system/Terambere water point does nolonger operate | 7dcec889d0d8605fec37a794759be66
52bc-urj9-p4b8 | 1 |  | J7 Rw10 | 1230340153 | 03-01-2015 00:33:43 CET | Tuyisenge Vianney | 00:11:34 | 2017 | Rwanda | Rulindo | Tumba | Taba | Nyirataba |  |  | Water point at EP Ruvumba/Nyirambuga pumping | 30604 |  | 169 | 169 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point meter at EP Ruvumba was seized due to improper payment of water cost.The water system private named as AGEOH does not cooperate since he couldn't wait the school be offered capitation grant to pay the water cost.This in result has caused the students/pupils to lack potable drinking water.The school management claims its water point closed and water meter seized because they have never denied paying the cost. | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.731700703555195 | 29.96118906371582 | 2127.1 | 27jx4icb | https://waterforpeople.s3.amazonaws.com/images/9b0fd2c3-edb1-47c2-b66c-ba9978f4a634.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7317306775142705 | 29.960878961266374 | 2132 | 27jywt5k | 6 | https://waterforpeople.s3.amazonaws.com/images/ce2d44fe-fdc2-4867-8de8-cd08301ea6bc.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point meter at EP Ruvumba was seized due to improper payment of water cost.The water system private named as AGEOH does not cooperate since he couldn't wait the school be offered capitation grant to pay the water cost.This in result has caused the students/pupils to lack potable drinking water.The school management claims its water point closed and water meter seized because they have never denied paying the cost.The water point storage tank valve chamber does nolonger have a cover | f89e503abc643ac3a8c0aa18aa916a26
1p0u-6cfd-f5x8 | 1 |  | J7 Rw26 | 1230060455 | 21-03-2017 14:01:43 CET | Byukusenge Elie | 00:09:22 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Kabgayi |  |  | Kabonanyoni | 7894 |  | 40 | 35 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.6412335696821507 | 29.972925388904738 | 1820.6 | 23earwk1 | https://waterforpeople.s3.amazonaws.com/images/8bca923d-92df-4dc3-9038-4ebd1ba50ecd.jpg | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6411804557031084 | 29.97315169077256 | 1805.5 | 23e7sqj7 | 31 | https://waterforpeople.s3.amazonaws.com/images/9bfdcda2-396a-411b-8830-bda4dd25f0fd.jpg | 2015 | Normal | No |  |  |  | No | Distribution reservoir doesn't work properly | Poor | This water tap doesn't functional because the distribution reservoir has been damaged. | 4068f5e3ad7df76bd681ee254b7fcfe4
k33b-ppvu-e3k7 | 1 |  | J7 Rw10 | 1299260123 | 15-04-2017 23:20:29 CEST | Tuyisenge Vianney | 00:05:04 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Kabunigu |  |  | Water point at Kabunigu/Tare-Rusiga pumping system | 9577 |  | 219 | 219 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | The water is operational and functional | 1 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8238133600691964 | 29.950389947164016 | 2063.5 | 2bs947cf | 1 | https://waterforpeople.s3.amazonaws.com/images/3df9615e-ad42-4de6-b81f-409a62f19097.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The water is operational and functional | da5bc756a6b5faba50a1adb2794ec91e
6qj4-eeh2-8wbp | 1 |  | J7 Rw23 | 1201030227 | 08-03-2017 07:30:48 CET | Rugirangoga Augustin | 00:37:07 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutembe | 1012 |  | 229 | 229 | 0 | Yes | Piped Network -- Gravity Only |  | 2009 | No |  | Padiri | Water source is well maintained | 2 | Groundwater (well, etc.) | -1.6452293607002955 | 29.88940159790624 | 1774.8 | 23kwbua6 |  | Yes | 45 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 45 | Yes | 1 |  | 2016 | Normal | 2500 | Yes | 2 | 1.6350822337877793 | 29.89531663121816 | 1775.7 | 2344max5 |  | 2009 | Poor | No | [5 empty] | Yes | 2 |  | 2009 | Poor | 3000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6491376822935664 | 29.885958356298563 | 1810.6 | 23rd4bsb | 1 |  | 2016 | Normal | No |  |  |  | Yes |  | Poor | System is working but some need rehabilitation | ba7c8cf0de53ea0a577b9b8ef7b617
mdp4-fstf-ga6a | 1 |  | J7 Rw15 | 1239070177 | 21-03-2017 15:33:40 CET | Mukakarangwa Assoumpta | 00:13:03 | 2017 | Rwanda | Rulindo | Kinihira | Rebero | Ndusu |  |  | Miyove-Kinihira | 10452 |  | 146 | 120 | 26 | Yes | Piped Network -- Gravity Only |  | 2001 | Yes | Kabuga | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6595532065134715 | 29.99202679202144 | 1945.5 | 248li0y8 | 2 | https://waterforpeople.s3.amazonaws.com/images/de69e595-10a0-4fa3-b10b-236fbd99059b.jpg | 2015 | Normal | No |  |  |  | Yes |  | Poor | This water point is constructed in 2015 by world vision and is normal | a92db04d8ba53b3c3cd44027fc99eba7
punn-he4s-6w60 | 1 |  | J7 Rw19 | 1319530050 | 20-04-2017 14:59:11 CEST | Kayinamura Innocent | 00:22:19 | 2017 | Rwanda | Rulindo | Ngoma | Karambo | Nyakagezi |  |  | Sehuta |  |  | 99 | 50 | 49 | Yes | Piped Network -- Gravity Only |  | 2014 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.81382066497262223 | 29.979785742648726 | 1726.1 | 2bbqc68l |  | Yes | 30 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 30 | Yes | 1 |  | 2014 | Normal | 1500 | Yes | 1 | -1.8146320670142189 | 29.982476016583142 | 1706.5 | 2bd2ka9c |  | 2014 | Normal | No | [5 empty] | Yes | 1 |  | 2014 | Normal | 200 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8146352553694047 | 29.98265994576245 | 1711.6 | 2bd2ka9e | 2 | https://waterforpeople.s3.amazonaws.com/images/8f2e2a07-c48f-41d4-8464-b2e2ae6a5bed.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | This network has 2 Water points It serves one village and the conduction line continue into the suction tank of Kabarore- Ngoma- Nyabuko network. | 90f8f0bc9b5123b58be3cf19fd13b8d
2ys1-6b6w-fu8s | 1 |  | J7 Rw15 | 1199330389 | 09-03-2017 21:31:04 CET | Mukakarangwa Assoumpta | 00:09:25 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Bitete-Rwahi network | 1316 |  | 188 | 20 | 168 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.83366417737979869 | 29.94346668826428 | 1815.5 | 2c8jk65m |  | Yes | 12 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 |  | 2013 | Normal | 600 | Yes | 6 | 1.8427360326225883 | 29.938932546871705 | 1676.5 | 2cnjkbst |  | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.858337377518586 | 29.93372944104972 | 1467.2 | 2ddccjgp | 1 | https://waterforpeople.s3.amazonaws.com/images/c1db1c13-ace5-4288-96f2-23ef78b59cd2.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 7c7fdca79f471fd936a489d47ac2019
8p8p-wtu4-un9a | 1 |  | J7 Rw10 | 1317610177 | 20-04-2017 08:32:28 CEST | Tuyisenge Vianney | 00:05:12 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Rusura |  |  | Water point near Rusura center/Nyirambuga pumping | 30604 |  | 157 | 157 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  |  |  | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | Yes | 1 | -1.6781326057212425 | 29.94788249612654 | 1781.3 | 253bpel2 | https://waterforpeople.s3.amazonaws.com/images/8467ca95-686f-4a50-9ba9-9463612c82e7.jpg | 2017 | Normal | No | [5 empty] | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/6b483fd5-7a34-44a6-85e9-799947805fd9.jpg | 2017 | Normal | 100 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6776672883325652 | 29.948208911201977 | 1776.6 | 252jq15m | 2 | https://waterforpeople.s3.amazonaws.com/images/ef83404f-6787-47e7-9e0b-dd3aed902140.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | operational | aa6b684f9fa63128e104733a87e4d83
redn-fuv4-0eh6 | 1 |  | J7 Rw7 | 1241250178 | 24-03-2017 11:38:28 CET | Safari Bosco | 00:12:43 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Nyakibungo | [5 empty] | 229 | 229 | 0 | Yes | Piped Network with Pump |  | 1998 | Yes | nyakabungo,marenge,gacyamo | Governement (District, WASAC) and Water For People | Have one Water point but the private operator intends to give them another Water point | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8193316541451867 | 30.062137310893345 | 1814.3 | 2bkue171 | 2 | https://waterforpeople.s3.amazonaws.com/images/15278372-1ad9-4c6d-9d07-62456e0fcb32.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | ebbcb92e0e7aa55edcb511c553a27
fxds-xmdb-3hkx | 1 |  | J7 Rw23 | 1205600175 | 07-03-2017 09:08:58 CET | Rugirangoga Augustin | 00:47:18 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 1789 |  | 192 | 100 | 92 | Yes | Piped Network -- Gravity Only |  | 2017 | Yes | karambi gitovu | padiri | Its planned to add another source to the system because water is not enough | 3 | Spring | -1.6127556054386574 | 29.874751563874717 | 1964 | 22375cxn |  | Yes | 120 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2017 | Normal | 120 | No |  |  | 2016 | Normal | 6450 | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6127858945649622 | 29.874684072604158 | 1901.7 | 2238xnqy | 1 |  | 2017 | Normal | No |  |  |  | Yes |  | Poor | System is working but not enough water | 55390dd617bf5b3efbd2d8a4afecaa
67vh-k0c6-ramf | 1 |  | J7 Rw10 | 1306890176 | 18-04-2017 20:14:38 CEST | Tuyisenge Vianney | 00:03:56 | 2017 | Rwanda | Rulindo | Tumba | Taba | Ruvumba |  |  | Water point chez Fari/Nyirambuga pumping | 30604 |  | 109 | 109 | 0 | Yes | Piped Network with Pump |  | 2012 | Yes | Nyirambuga and Kamuragi | Governement (District, WASAC) and Water For People | Operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7335658842362234 | 29.945411628527598 | 1899.5 | 27mzv4qm | 2 | https://waterforpeople.s3.amazonaws.com/images/a4ee8c54-f0a6-447a-90a4-73f223093d8a.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | The water point is operational | d4e2713097fc50c042475d4491cd8671
hajt-k45a-0t89 | 1 |  | J7 Rw26 | 1230060449 | 21-03-2017 13:50:44 CET | Byukusenge Elie | 00:09:32 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Rukingu |  |  | Kabonanyoni | 7894 |  | 70 | 65 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6321411307659457 | 29.957714582608894 | 2129.8 | 22z9kvjt | 31 | https://waterforpeople.s3.amazonaws.com/images/c71837c8-3d20-40c6-b8bb-e738d9028f15.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap located in this village is near with another so that the community doesn't use both of them. | fa8bd8f68eca83c39c7d3cb9124be8f
qqh9-8evq-pxjg | 1 |  | J7 Rw10 | 1235980274 | 03-01-2015 02:04:20 CET | Tuyisenge Vianney | 00:07:36 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point1 at ADEPR PEPO Tumba/Nyirambuga pumping | 30604 |  | 169 | 169 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Everything operates normally the water is available everyday | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6921267372267261 | 29.93946286199889 | 2134.5 | 25qgmttu | 5 | https://waterforpeople.s3.amazonaws.com/images/e840189d-c56e-44b1-a972-fd2677dba1d4.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Everything operates normally the water is available everyday | 88ad73ace767d7c1d373c4ca3304037
3vc3-3tcx-agab | 1 |  | J7 Rw8 | 1222570991 | 16-03-2017 08:55:39 CET | Amani Desire | 00:13:34 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kibamba |  |  | Musenge Network | 6074 |  | 76 | 76 | 0 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi |  |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7560783564003224 | 29.93398835455034 | 1951.3 | 28o81vd7 | 28 | https://waterforpeople.s3.amazonaws.com/images/92a1f576-4f09-4e4a-a552-518c572953d6.jpg | 2014 | Does Not Function | Yes | 8 | 30 | all water served by R50m3 located at kibamba village do not have water today from last july 2016 | No | water points served by R50m3 located at kibamba village do not have water as water do not reach this Reservoir | Does Not Function | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | c4a062b5a351e3d67145365698f1328
v1tu-n558-096x | 1 |  | J7 Rw26 | 1213130090 | 11-03-2017 10:27:01 CET | Byukusenge Elie | 00:15:31 | 2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gahwazi |  |  | Nyamagana | 20456 |  | 70 | 30 | 40 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank | This network serves four sectors Cyungo,Rukozo, Base,Base and Kinihira, It has some problems in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible because it serves many populations and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6443688930375195 | 29.949532896460365 | 1843.7 | 23jh4kpz | 29 | https://waterforpeople.s3.amazonaws.com/images/de615918-cd2e-4ab0-b448-398c16550f59.jpg | 2011 | Normal | Yes | 10 | 25 | Bad tee connections and the types of pipeline needs rehabilitation | No | No water available in distribution reservoir due to bad connection to the distribution line. | Poor | No water available in Kadendegeri Centre the Population use the rain water of washland water. | 74d1fc8df92efed67fa7f5c1d8122e42
ahw7-eyup-12gr | 1 |  | J7 Rw15 | 1199330372 | 09-03-2017 19:26:48 CET | Mukakarangwa Assoumpta | 00:08:21 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyarusange |  |  | Gisoro- Nyundo network | 2297 |  | 97 | 45 | 52 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.840451151026817 | 29.948165560771624 | 1795.9 | 2cjrthy1 |  | Yes | 13 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 13 | Yes | 1 |  | 2013 | Normal | 30 | Yes | 6 | 1.8406374522240199 | 29.94836287627501 | 1783.7 | 2ck2jau3 |  | 2013 | Poor | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 7000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8574548891703082 | 29.949099991720665 | 1569.9 | 2dbvyeci | 1 | https://waterforpeople.s3.amazonaws.com/images/d493e69e-5fcb-4caf-ad18-62a7975662ee.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 6bc5794ec7b8ee4f96de0878ca0459e
h071-ufsu-yv8j | 1 |  | J7 Rw26 | 1431830244 | 02-06-2017 09:24:25 CEST | Byukusenge Elie | 00:04:53 | 2017 | Rwanda | Rulindo | Cyinzuzi | Migendezo | Rusagara |  |  | Kararama | 6572 |  | 98 | 90 | 8 | Yes | Piped Network with Pump |  | 2009 | Yes | Not Water Tap | Water For People |  | 3 | Spring | -1.750378530192073 | 29.986212109350618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 7 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2009 | Normal | Yes | 14 | Pressure Break Tank¦Distribution Chamber |  | 2009 | Normal | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 1 |  | 2012 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7391691117504233 | 29.982702887914872 | 2077.4 | 27w99vsj | 1 | https://waterforpeople.s3.amazonaws.com/images/9b0313ae-2280-41ee-a536-e3511259cbd4.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal |  | cd90e1b460582575fe707524c0974a2
9ngs-smxt-2r65 | 1 |  | J7 Rw23 | 1325630072 | 23-04-2017 14:42:09 CEST | Rugirangoga Augustin | 00:16:02 | 2017 | Rwanda | Rulindo | Buyoga | Ndarage | Kagozi |  |  | ndarage |  |  | 155 | 130 | 25 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | kagozi gikingo karambi gahondo karambi | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.6829614865475908 | 30.031434012077444 | 1962 | 25bb9sey |  | Yes | 30 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 30 | Yes | 1 |  | 2014 | Normal | 6700 | Yes | 5 | -1.6829614865475908 | 30.031434012077444 | 1962 | 25bb9sey |  | 2014 | Normal | No | [5 empty] | Yes | 1 |  | 2014 | Normal | 6700 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6902852583901354 | 30.03414816537023 | 1790.7 | 25nf3391 | 1 |  | 2014 | Normal | No |  |  |  | Yes |  | Normal |  | 7cc042331424a71cc2f952356a6e06d
472b-5rcq-5h26 | 1 |  | J7 Rw10 | 1301320120 | 16-04-2017 22:55:03 CEST | Tuyisenge Vianney | 00:06:13 | 2017 | Rwanda | Rulindo | Buyoga | Karama | Kajeneni |  |  | Kajeneni water point/Nyirambuga pumping system | 30604 |  | 175 | 175 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | Under construction | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.6937536604326815 | 29.97405783767635 | 1933.6 | 25t5ohp8 | https://waterforpeople.s3.amazonaws.com/images/98beaa16-7638-43e6-90a5-a80e8562945a.jpg | 2017 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6930480666489902 | 29.973566039277717 | 1913 | 25rzepqv | 2 | https://waterforpeople.s3.amazonaws.com/images/55f1ae33-36d6-4539-9717-48d4845d6547.jpg | 2017 | Does Not Function | No |  |  |  | No | construction works under progress | Does Not Function | under construction | cb184472655f8472674c252dd8c463e5
23tp-e6pw-1a05 | 1 |  | J7 Rw15 | 1202320480 | 08-03-2017 22:31:24 CET | Mukakarangwa Assoumpta | 00:07:25 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Bugarura |  |  | kirikumuryango network |  |  | 119 | 35 | 84 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.884920481559111 | 29.971791214792702 | 1472.8 | 2elbg5ad | 1 | https://waterforpeople.s3.amazonaws.com/images/314a1f17-2ef3-4664-9ac1-3b549419b313.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 6d42ec645a67722588d0575b56b26
99qm-cuhp-g940 | 1 |  | J7 Rw10 | 1234670455 | 03-01-2015 00:46:04 CET | Tuyisenge Vianney | 00:05:48 | 2017 | Rwanda | Rulindo | Tumba | Taba | Nyirataba |  |  | Nyirataba2 water point/Nyirambuga pumping | 30604 |  | 169 | 169 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point at Nyirataba operates well and functions normally | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7321011173790135 | 29.96059441149479 | 2137.5 | 27kkxuj9 | 3 | https://waterforpeople.s3.amazonaws.com/images/963401c0-4beb-4697-b7a2-94a176c7c01f.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point at Nyirataba operates well and functions normally | dd72847bfc925843a1047fc04769c4
4k5k-emdk-cbt0 | 1 |  | J7 Rw26 | 1201690507 | 02-01-2015 05:58:17 CET | Byukusenge Elie | 00:08:16 | 2017 | Rwanda | Rulindo | Cyungo | Burehe | Nyagatovu |  |  | Nyamagana | 20456 |  | 50 | 45 | 5 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6339440320124687 | 29.930069056196285 | 1813.7 | 2328qw84 | 29 | https://waterforpeople.s3.amazonaws.com/images/eb40184e-a649-449f-9ebc-ff3dd1221cfe.jpg | 2011 | Normal | Yes | 10 | 30 | The distribution reservoir does not supply water in this transmission line because of bad connection of tee junctions towards Gatovu and The pipeline was damaged | Yes |  | Poor | water tap located at centre mukaragato | 95e0cb9d7fe1bfd7f24bf23ea2d4
htst-vjea-7h4t | 1 |  | J7 Rw26 | 1235770599 | 21-03-2017 14:03:49 CET | Byukusenge Elie | 00:10:38 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Kamiyove |  |  | Kabonanyoni | 7894 |  | 70 | 65 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.6412335696821507 | 29.972925388904738 | 1820.6 | 23earwk1 |  | 2015 | Does Not Function | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6395907004855792 | 29.973107775988026 | 1773.2 | 23bl4tcj | 31 | https://waterforpeople.s3.amazonaws.com/images/d7c61318-7c2d-4dac-9704-27240a67ef32.jpg | 2015 | Normal | No |  |  |  | No | Distribution reservoir doesn't work properly | Poor | Water tap doesn't have water because the distribution reservoir has been damaged and the community use the protected spring. | bfeae67c645bac6695f85fbf1b59cce6
8v7a-eb11-bkas | 1 |  | J7 Rw23 | 1198150128 | 07-03-2017 13:21:14 CET | Rugirangoga Augustin | 00:47:30 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 1789 |  | 192 | 100 | 92 | Yes | Piped Network -- Gravity Only |  | 2012 | Yes | Gitovu | Padiri | This Systems Functions well | 3 | Spring | 1.613001918870488 | 29.87535077266787 | 1921.6 | 223m1729 |  | Yes | 40 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 40 | Yes | 2 |  | 2012 | Normal | 6450 | Yes | 3 | -1.6148201270542197 | 29.88638334239096 | 1829.4 | 226me38v |  | 2012 | Normal | Yes | 3 | Distribution Chamber |  | 2012 | Normal | Yes | 2 |  | 2012 | Poor | 6800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6132044358172468 | 29.88648943766929 | 1830.4 | 223xxv8w | 1 |  | 2012 | Does Not Function | Yes | 365 | 0 | Water doenst reach well the destination | No | Water doesn’t reach Water Tap low pressure | Poor | System is working but not enough water | 2cefc3ec7ff973322da70e73de3b95b
gg4j-4q6g-v6f | 1 |  | J7 Rw10 | 1234240203 | 03-01-2015 02:20:59 CET | Tuyisenge Vianney | 00:04:36 | 2017 | Rwanda | Rulindo | Tumba | Barari | Gaseke |  |  | Water point at Gashora/Nyirambuga pumping | 30604 |  | 149 | 149 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | Everything operates normally the water is available everyday | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.7151366751019868 | 29.931507840293843 | 1790.6 | 26sil8qb | https://waterforpeople.s3.amazonaws.com/images/1796ad40-17c7-4e63-bc21-4fe3db545976.jpg | 2017 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7151396035624962 | 29.93069533802902 | 1815.4 | 26sil8q2 | 2 | https://waterforpeople.s3.amazonaws.com/images/ed0b39d9-11c1-40ae-b196-ccbfd2a7c5ef.jpg | 2017 | Normal | No |  |  |  | Yes |  | Normal | Everything operates normally the water is available everyday. | 4eb3bc86b6d2d4b2a17abd6307aab5
x2cd-km48-0h5q | 1 |  | J7 Rw26 | 1203030069 | 02-01-2015 05:50:24 CET | Byukusenge Elie | 00:13:35 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Gihemba |  |  | Nyamagana | 20456 |  | 100 | 90 | 10 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6276577118780158 | 29.926433610839236 | 1813.2 | 22ru98ow | 29 | https://waterforpeople.s3.amazonaws.com/images/6636ca6f-d7da-41e9-b308-079aaee99fb0.jpg | 2011 | Normal | Yes | 7 | 30 | The distribution reservoir does not supply water in this transmission line | Yes |  | Poor | The transmission line towards Base has water but the community does not use it they use spring sources and rain water | 9798174ead41dc9b57a271ba3c18b2
m2xc-smkb-9w0y | 1 |  | J7 Rw10 | 1317450063 | 20-04-2017 07:53:42 CEST | Tuyisenge Vianney | 00:04:44 | 2017 | Rwanda | Rulindo | Tumba | Misezero | Taba |  |  | Water point at Taba/Nyirambuga pumping | 30604 |  | 100 | 100 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | operational | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | Yes | 1 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/bede586d-5916-41a7-8fd7-3806aeae4ae2.jpg | 2012 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6937760581356693 | 29.9563300864917 | 2011 | 25t6vcrv | 2 | https://waterforpeople.s3.amazonaws.com/images/75776f7c-4bed-4451-b297-e9f925dfbafd.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | operational | 15694bb3828178aed3a29a610e3e2ee
dxw4-xnq6-q4p8 | 1 |  | J7 Rw8 | 1220200247 | 16-03-2017 08:49:45 CET | Amani Desire | 00:13:36 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kalindi |  |  | Musenge Network | 6074 |  | 55 | 55 | 0 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi | WFP |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 59.956828330459043 | 2206.4 | 29s1w3ps |  | 2014 | Normal | Yes | 8 | Distribution Chamber¦washout and Air release |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7609163302250674 | 29.936436940206363 | 1934.1 | 28w87o6c | 28 | https://waterforpeople.s3.amazonaws.com/images/ad49e435-8dd7-4b3f-b25d-c89e389885f7.jpg | 2014 | Does Not Function | Yes | 8 | 30 | water do not reach the distribution reservoir that serves this water point | No | water point served by R50m3 located at kibamba village do not have water as water dont reach this distribution reservoir | Does Not Function | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | 5f3b27d2d82c5af8644374e7aeb9c61
m6t5-ua24-tsh1 | 1 |  | J7 Rw8 | 1224840223 | 16-03-2017 08:54:10 CET | Amani Desire | 00:17:36 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gicumbi |  |  | Musenge Network | 6074 |  | 141 | 35 | 106 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi |  |  | 1 | Spring | -1.76874219980039 | 29.93859037216456 | 1824.3 | 2996e2ux |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.78015089964588008 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber¦washout and Air release |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7681585759318281 | 29.94111459365851 | 1944.2 | 29879i6r | 28 | https://waterforpeople.s3.amazonaws.com/images/05301939-6e07-4e78-b6ac-5c4587dfd205.jpg | 2014 | Does Not Function | Yes | 8 | 30 | all water served by R50m3 located at kibamba village do not have water today from last july 2016 | No | all water served by R50m3 located at kibamba village do not have water today from last july 2016 | Does Not Function | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | 424ebc3d353fa306ddf13d206ef2b0
vev9-f1hm-0snw | 1 |  | J7 Rw10 | 1215820383 | 13-03-2017 21:04:55 CET | Tuyisenge Vianney | 00:05:48 | 2017 | Rwanda | Rulindo | Base | Gitare | Gihora |  |  | Gihora2 Water point/Rutomvu gravity | 3015 |  | 101 | 101 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | GoR | Water point operational but people do not use it frequently due to fear of cost | 1 | Spring | -1.677891751247546 | 29.90118126071259 | 1802.6 | 252xezpf |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6646394753320743 | 29.89267465146232 | 1734.8 | 24gzy7hq | 1 | https://waterforpeople.s3.amazonaws.com/images/8b38f68c-afc9-41f7-9fe8-19b95478ecbd.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | The water point operates normally | 30448be035204e2c1746b2b18c5f9ef
3ybh-263d-vftr | 1 |  | J7 Rw10 | 1302730098 | 15-04-2017 23:17:19 CEST | Tuyisenge Vianney | 00:06:18 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Rwintare |  |  | Water point at GS Rusiga/Tare-Rusiga pumping | 9577 |  | 281 | 281 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | The water point operates well and normally.The bolt to fix the cover of the top the water storage tank was stolen.People are climbing on top the tank to directly fetch water from within which exposes the water to danger of filth | 1 | Spring | -1.7379838326200818 | 29.9058565970111 | 2048.8 | 27ub0pte |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | Yes | 1 | -1.826985008618618 | 29.94713479415194 | 2091 | 2bxhum33 | https://waterforpeople.s3.amazonaws.com/images/d6fcee06-5370-45b4-99d5-b1a20e0a2fb2.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8276821253691444 | 29.94729120526646 | 2095.4 | 2byniyfk | 2 | https://waterforpeople.s3.amazonaws.com/images/84849fbc-04ca-4eac-9063-401be86eb1f3.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The water point operates well and normally.The bolt to fix the cover of the top the water storage tank was stolen.People are climbing on top the tank to directly fetch water from within which exposes the water to danger of filth | d229df314ea9391796a66f1e256dbf42
mnwm-gwbc-4hq1 | 1 |  | J7 Rw15 | 1237970218 | 23-03-2017 06:59:33 CET | Mukakarangwa Assoumpta | 00:05:28 | 2017 | Rwanda | Rulindo | Kinihira | Marembo | Gatare |  |  | Nyamagana- Kinihira |  |  | 160 | 80 | 80 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.92406873398803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 7 | Distribution Chamber¦Ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6600604629653397 | 29.922076870516953 | 1929.7 | 249fv49g | 2 | https://waterforpeople.s3.amazonaws.com/images/15a0f4a2-0f62-4967-b030-a4ecd5824efb.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | a9e8317c57a729aa5aaa057188c9c4
m1fr-tusu-db6y | 1 |  | J7 Rw19 | 1241220174 | 23-03-2017 20:14:35 CET | Kayinamura Innocent | 01:03:05 | 2017 | Rwanda | Rulindo | Masoro | Kivugiza | Gasenga |  |  | Mutagata motorised network | 26296 |  | 284 | 146 | 138 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.792287972143684 | 30.075218495709937 | 1634.7 | 2ac3whxs | 64 | https://waterforpeople.s3.amazonaws.com/images/53aab623-5a97-4694-876e-fa6c8cf09977.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 8beb3392fa45dadc3f415285394afa3
dpvh-psde-j9m9 | 1 |  | J7 Rw10 | 1239880392 | 22-03-2017 14:19:00 CET | Tuyisenge Vianney | 00:06:42 | 2017 | Rwanda | Rulindo | Rusiga | Taba | Karambi |  |  | Karambi water point/Nyakabizi gravity | 1259 |  | 109 | 109 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People | Water not available.Water point not operational.Infrastrure damaged needs repair and maintenance | 2 | Spring | -1.803447729664134 | 29.930708856826865 | 1927.1 | 2aukc7xn |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8227890513289529 | 29.91841381263292 | 1698.3 | 2bqjsjsg | 2 | https://waterforpeople.s3.amazonaws.com/images/1f58cb32-eebc-4ad0-a239-ac90aeb03ac4.jpg | 2013 | Does Not Function | No |  |  |  | No | Water not available.Water point not operational.Infrastrure damaged needs repair and maintenance | Does Not Function | Water not available.Water point not operational.Infrastrure damaged needs repair and maintenance | 85946ece6ea16416ea1798fd904ddd
urxj-cguh-3qkd | 1 |  | J7 Rw24 | 1328910050 | 25-04-2017 16:36:28 CEST | Kabalisa Manzi Christella | 00:07:23 | 2017 | Rwanda | Rulindo | Cyinzuzi | Rudogo | Munoga |  |  |  | 0 |  | 98 | 98 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 1 | Spring | -1.7521357636267942 | 30.004650031976542 | 1829.2 | 28hph3ke |  | Yes | 50 | Yes | 1 |  |  | 2011 | Poor | 50 | Yes | 2 |  | 2011 | Normal | 30000 | Yes | 5 | -1.7521357636267942 | 30.004650031976542 | 1829.2 | 28hph3ke |  | 2011 | Normal | Yes | 6 |  |  | 2011 | Normal | Yes | 1 |  | 2011 | Normal | 30000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7498798263437751 | 30.020620500322753 | 1623.5 | 28dyx4z2 | 1 | https://waterforpeople.s3.amazonaws.com/images/f176cad4-65e6-4cff-b8ce-5d9b9d644a5d.jpg | 2003 | Poor | No |  |  |  | Yes |  | Normal |  | 8ab56c5dc88c235ac468ac3858213c52
8t8t-njnt-6fbe | 1 |  | J7 Rw19 | 1227460916 | 17-03-2017 05:22:03 CET | Kayinamura Innocent | 00:15:59 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Ruhondo |  |  | Musenge network | 6074 |  | 184 | 39 | 145 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma, Karehe, Rutonde, Gitaba, Kiruri, Buhera, Ruhanya, Kibamba, and Karindi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Washout and Air release chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.788396636069806 | 29.963989472848052 | 2077 | 2a5oaurb | 28 | https://waterforpeople.s3.amazonaws.com/images/0259fa6a-11fe-47ef-95c8-4a8c93f11638.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | 1. the system has two Pumps but one is damaged and is not working, only one pump is used to pump water 2. Eleven (11) water points served by the distribution reservoir R 50m3 located at Kibamba village do not have water today because water don't reach this reservoir, there is not water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5. one water point doesn't Function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | df62b494f5a25f16e2418721705ccbb8
fvuv-15ad-jupt | 1 |  | J7 Rw15 | 1210760336 | 09-03-2017 22:26:59 CET | Mukakarangwa Assoumpta | 00:05:37 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Bwimo |  |  | Bitete-Rwahi network | 1316 |  | 188 | 30 | 158 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.8336417737979869 | 29.94346668826428 | 1815.5 | 2c8iday2 |  | Yes | 12 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 |  | 2013 | Normal | 600 | Yes | 6 | 1.8427360326225883 | 29.938932546871705 | 1676.5 | 2cnjkbst |  | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8521811788020792 | 29.93546142665366 | 1533.7 | 2d366yfu | 1 | https://waterforpeople.s3.amazonaws.com/images/3703ec97-b1c5-4b08-8dac-4de21ed576a4.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 2a5f88c3b3f28be022e84a5c9da74ed5
fkcn-gc9j-qv6p | 1 |  | J7 Rw23 | 1203860159 | 07-03-2017 21:17:15 CET | Rugirangoga Augustin | 00:57:10 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Bukangano |  |  | Migogo | 558 |  | 129 | 120 | 9 | Yes | Piped Network -- Gravity Only |  | 2009 | Yes | kiruli bukangano kabahama rubanda | Italians(LAKE ANGELS) | Near the source there is a Water Point Needed and there is a village and many households around | 1 | Groundwater (well, etc.)¦Lake/Reservoir | -1.632311918504939 | 29.90125938622725 | 1810.2 | 22zjp8ec |  | No | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2009 | Normal | 20 | Yes | 2 |  | 2009 | Poor | 3000 | Yes | 3 | -1.6350822337877793 | 29.89531663121816 | 1775.7 | 2344max5 |  | 2009 | Poor | No | [5 empty] | Yes | 2 |  | 2009 | Poor | 3000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.635064098884494 | 29.895355082459844 | 1751.2 | 2343ffpl | 1 |  | 2009 | Poor | Yes | 4 | 2 | Size of Pipes which is not in accordance with the volume of Water from source | Yes |  | Poor | System needs rehabilitation | 8d9dee4dcb97f9bad5ea6454f11bb752
yxn0-kt1y-6kd0 | 1 |  | J7 Rw23 | 1322150090 | 23-04-2017 14:41:05 CEST | Rugirangoga Augustin | 00:20:00 | 2017 | Rwanda | Rulindo | Buyoga | Gahororo | Gatare |  |  | kiruruma | 8295 |  | 169 | 120 | 49 | Yes | Piped Network with Pump |  | 2014 | Yes | gatare gatenderi nyarubuye nyamwiza murambo | Governement (District, WASAC) and Water For People | Water system has no problem | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 2 |  | 2014 | Normal | 4200 | Yes | 11 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2014 | Normal | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 4200 | Yes | 2 |  | 2014 | Normal | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7284987232858422 | 30.07306687831415 | 1510.6 | 27em0e0q | 2 | https://waterforpeople.s3.amazonaws.com/images/dc915c70-4aba-4b9d-bbe3-9b19206092e0.jpg | 2017 | Does Not Function | No |  |  |  | No | Water point under construction | Poor | Water point is fully Built and new but water has not started flowing | b1f62950389faafeca57248ccdfb96b6
2m33-ag31-bawr | 1 |  | J7 Rw24 | 1328910063 | 25-04-2017 16:43:25 CEST | Kabalisa Manzi Christella | 00:09:10 | 2017 | Rwanda | Rulindo | Cyinzuzi | Rudogo | Kirambo |  |  | Nyamateke source | 0 |  | 137 | 137 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 1 | Spring | -1.7521357636267942 | 30.004650031976542 | 1829.2 | 28hph3ke |  | Yes | 50 | Yes | 1 |  |  | 2003 | Normal | 50 | Yes | 2 |  | 2003 | Normal | 30000 | Yes | 5 | -1.7515741340060311 | 30.01759179728754 | 1662.2 | 28gs4tsf | https://waterforpeople.s3.amazonaws.com/images/f4dee776-a8c3-4990-b031-d99fecbddd41.jpg | 2003 | Normal | Yes | 6 |  |  | 2003 | Normal | Yes | 1 |  | 2003 | Normal | 30000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7518908994085245 | 30.018512521527295 | 1634.9 | 28hb6p5l | 1 | https://waterforpeople.s3.amazonaws.com/images/8b8103b7-cdc3-4c99-bdfa-b2cef55ffbe9.jpg | 2003 | Does Not Function | No |  |  |  | Yes |  | Poor |  | 639791f0687c6af3bd9bbdfdfa85fa3
84uc-hck6-7ww5 | 1 |  | J7 Rw26 | 1235950386 | 21-03-2017 14:15:26 CET | Byukusenge Elie | 00:05:35 | 2017 | Rwanda | Rulindo | Rukozo | Mbuye | Mujebe |  |  | Kabonanyoni | 7894 |  | 90 | 80 | 10 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6181055678365246 | 29.96217242932456 | 1872.6 | 22c1oa91 | 31 | https://waterforpeople.s3.amazonaws.com/images/7b994d00-1cec-4b1f-89f9-1901b8acde25.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | It is most used by the community in Centre Bar in Mujebe village. | 222538170b9b1f0cede1f994f65d1f7
u284-0g01-s9dw | 1 |  | J7 Rw24 | 1327820055 | 25-04-2017 17:04:44 CEST | Kabalisa Manzi Christella | 00:09:47 | 2017 | Rwanda | Rulindo | Cyinzuzi | Rudogo | Kirambo |  |  | Nyamateke network | 0 |  | 137 | 137 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | Yes | Kirambo na Gaseke | Government |  | 2 | Spring | -1.7521357636267942 | 30.004650031976542 | 1829.2 | 28hph3ke |  | Yes | 120 | Yes | 1 |  |  | 2003 | Normal | 120 | Yes | 2 |  | 2003 | Normal | 30000 | Yes | 5 | -1.7520630142611384 | 30.011117297675636 | 1740.9 | 28hlb2dr | https://waterforpeople.s3.amazonaws.com/images/84613ef8-3c91-41ed-b66e-fc8e368624a7.jpg | 2003 | Poor | Yes | 14 |  |  | 2003 | Normal | Yes | 1 |  | 2003 | Normal | 30000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7522601329100966 | 30.011262721207366 | 1704.5 | 28hx7qhc | 1 | https://waterforpeople.s3.amazonaws.com/images/3b38c7d7-c93d-4a31-9382-2a3c7c79b593.jpg | 2003 | Normal | No |  |  |  | Yes |  | Poor |  | 11a579cfbcaccf9c2f09d8ac962118f
n4w0-sm9g-rt9s | 1 |  | J7 Rw8 | 1246540339 | 23-03-2017 07:58:32 CET | Amani Desire | 00:08:58 | 2017 | Rwanda | Rulindo | Murambi | Mugambazi | Buliza |  |  | Mutagata Motorised Network | 26296 |  | 221 | 100 | 121 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release chamber |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.800469707001088 | 30.03667235255294 | 1979 | 2apmx2ha | 64 | https://waterforpeople.s3.amazonaws.com/images/9919a475-d041-425a-bb6e-9e1318d333cd.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | 85e2d19d5cd12b769a9c96640cdfafe
rs6v-nr9v-2k7q | 1 |  | J7 Rw10 | 1199580503 | 08-03-2017 12:35:52 CET | Tuyisenge Vianney | 00:24:49 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Tare-Rusiga water pumping system/Nyakabingo1 water spring source | 9577 |  | 228 | 228 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This nyakabingo1 water spring source is one of the sources feeding Tare-Rusiga pumping system | 1 | Spring | -1.7371495295820434 | 29.91154113672574 | 1963.2 | 27sx0b1n | https://waterforpeople.s3.amazonaws.com/images/9b0c532e-64a8-4833-b898-af5daabf520d.jpg | Yes | 20 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/0eec09e0-1e75-4d3d-b25f-988ba022a23e.jpg | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 20 | Yes | 1 |  | 2015 | Normal | 400 | Yes | 2 | -1.7372117119507136 | 29.911813360764405 | 1962.5 | 27t16ca6 | https://waterforpeople.s3.amazonaws.com/images/a0d83d44-3387-46b4-a091-89006747b595.jpg | 2015 | Normal | Yes | 1 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/84fe90ac-0e22-4116-aa20-15f7e53264e6.jpg | 2015 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.73752249830559 | 29.912373117811338 | 2005.1 | 27tjms1f | 1 | https://waterforpeople.s3.amazonaws.com/images/4f41be6b-e4b4-4daa-8bde-b91167535c0a.jpg | 2015 | Normal | No |  |  |  | No | Since the construction,the water point hasn't been used.The people fetch water from the start chamber pipe | Normal | The water source has one water point though it is not serving the people due to the fact they can't pay it while on the start chamber there is free water delivered | 155343339a6392c979b030bc4ae3ea57
e15n-mtvw-bv7q | 1 |  | J7 Rw24 | 1256480225 | 28-03-2017 08:14:03 CEST | Kabalisa Manzi Christella | 00:08:32 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Kiyanza I |  |  | Rwamugaza network | 14106 |  | 1025 | 1025 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7656153941068853 | 30.07778537610675 | 1730.3 | 29401fl5 | 1 | https://waterforpeople.s3.amazonaws.com/images/5f7ef307-0b30-4f53-922f-b253f363aed1.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 309aed648491fb895e11f8ff9dd251ff
dyfp-krmk-fn2g | 1 |  | J7 Rw10 | 1218620378 | 13-03-2017 21:57:31 CET | Tuyisenge Vianney | 00:05:40 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Ngarama |  |  | Ngarama2 water point/Nkore gravity |  |  | 110 | 110 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Private people joined hands together to get water | The water point does not operate well | 1 | Spring | -1.6883400866741962 | 29.91133431277988 | 1897.9 | 25k7kyy1 |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6893917146659465 | 29.905509771514932 | 1802.7 | 25ly3hf3 | 1 | https://waterforpeople.s3.amazonaws.com/images/8c615fc9-1ca2-42be-a417-f8b5fd80662d.jpg | 2013 | Does Not Function | No |  |  |  | No | It got damaged and is no longer deliver water to the people | Does Not Function | Nolonger working | 44b4f495808fe5b3afb4f591f0e2afb8
muh9-emqr-nptm | 1 |  | J7 Rw19 | 1212520351 | 13-03-2017 07:06:01 CET | Kayinamura Innocent | 01:08:55 | 2017 | Rwanda | Rulindo | Ngoma | Munyarwanda | Busizi |  |  | Kabarore-Ngoma-Nyabuko network | 8284 |  | 100 | 31 | 69 | Yes | Piped Network with Pump |  | 2014 | Yes | Nyabuko, Kagwa, Kiruri, Busizi, Ngaru, Kirungu, Kiboha, and Kigina | Governement (District, WASAC) and Water For People | The network has 17 water points and it serves 8 villages | 4 | Spring | -1.8247197370619486 | 29.978923696109938 | 1671.3 | 2btqp80d | https://waterforpeople.s3.amazonaws.com/images/a919ab53-0753-4136-8b81-50b1fd337a54.jpg | No | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦Collection Chamber | 2014 | Normal | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.8118879629206273 | 30.003478805087482 | 2031 | 2b8iu32a | https://waterforpeople.s3.amazonaws.com/images/21625baf-142f-4ba1-a869-5875363d4fe4.jpg | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 4 | https://waterforpeople.s3.amazonaws.com/images/d5ee0521-f144-4ea0-86f3-b419d0316f27.jpg | 2014 | Poor | Yes | https://waterforpeople.s3.amazonaws.com/images/09572f42-3aef-4416-bb23-f493d1a33771.jpg | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8197952236937738 | 30.005079034494425 | 1932 | 2bllryky | 17 | https://waterforpeople.s3.amazonaws.com/images/4731fdaf-d9b0-46cd-81a2-b1cbdd0fd760.jpg | 2014 | Poor | Yes | 1 | 10 | it was due to the road construction | Yes |  | Normal | - the network has 17 water points - water points are in good operations conditions except the water point at the source that is damaged - 4 water points don't have water today - The pipe are in good conditions - The pump is not working properly as it was expected during Design, today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy - the transformer at the pumping station doesn't offer the required energy for the pump - the anti-hammers of pumps are not functioning because of bad installation of pumping house - the system has 4 pumps units with two units pumping in one direction towards Nyabuko, towards Ngoma sector office - the suction tank is in bad physical condition | 3a44d3f32cb0b1ed70a5686815dd63b4
18gn-f078-6ykp | 1 |  | J7 Rw10 | 1281480089 | 05-04-2017 21:51:28 CEST | Tuyisenge Vianney | 00:05:08 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Tare |  |  | Nyabishengeshi gravity system | 893 |  | 109 | 109 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | Yes | Tare and Byimana villages | Governement (District, WASAC) and Water For People | Tare water point connected to Nyabishengeshi and shares water to Byimana and Tare villages | 1 | Spring | -1.6778517470929726 | 29.880934967401814 | 2032.3 | 252v194p |  | Yes | 50 | No | [5 empty] | 50 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6732579054235457 | 29.889185330451163 | 1950.5 | 24v95ux7 | 1 | https://waterforpeople.s3.amazonaws.com/images/a662270d-7dda-4aaa-a344-8003701581ed.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | Tare water point connected to Nyabishengeshi and shares water to Byimana and Tare villages | d04ea63eb458571cda125729751ad6
gcpt-jp15-d652 | 1 |  | J7 Rw10 | 1300340081 | 16-04-2017 22:08:01 CEST | Tuyisenge Vianney | 00:07:40 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Rugote |  |  | Water point chez Jean de Dieu/Nyirambuga pumping system | 30604 |  | 120 | 120 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | The water point chez JeandeDieu operates normally and water is available | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.671789777881368 | 29.905326317415152 | 2127 | 24stn54d | 2 | https://waterforpeople.s3.amazonaws.com/images/dcc1de35-d5b6-42f2-af9a-ab82d066ee9d.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | The water point chez JeandeDieu operates normally and water is available | 3d8db9d7d2c1f5b1f9ff59a5bbf8de9
enfk-22tv-6aak | 1 |  | J7 Rw24 | 1328810063 | 25-04-2017 00:03:40 CEST | Kabalisa Manzi Christella | 00:15:37 | 2017 | Rwanda | Rulindo | Ntarabana | Kiyanza | Nyagasozi |  |  | Rwamugaza network | 14106 |  | 197 | 197 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | Yes | nyagisozi,nombe | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7374173333138418 | 30.006563288387298 | 1723.9 | 27td3141 |  | 2003 | Normal | Yes | 14 |  |  | 2003 | Normal | Yes | 1 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.753047770377866 | 30.062955644445008 | 1784.9 | 28j7nk2d | 1 | https://waterforpeople.s3.amazonaws.com/images/dba2cecb-5461-4339-a363-7b09e34b8985.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | 6994aedc4dbc1fe2ce017f6bcd1a78
vdt3-gpnw-r4cd | 1 |  | J7 Rw24 | 1217930752 | 16-03-2017 06:51:57 CET | Kabalisa Manzi Christella | 00:08:49 | 2017 | Rwanda | Rulindo | Burega | Taba | Lyinzovu |  |  | Rwamugaza | 14106 |  | 505 | 505 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | no problem | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  | https://waterforpeople.s3.amazonaws.com/images/3c48bc45-9d0e-4d55-bed0-c6acedadb731.jpg | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7304920894218812 | 30.02101062816108 | 2052.3 | 27hx32lu | 1 | https://waterforpeople.s3.amazonaws.com/images/a9d672c1-d41c-47dd-b5ae-78f345cd09a2.jpg | 2012 | Normal | No |  |  |  | No | Water seller was not around | Normal | no problem | 7bce4be31c7d3bb389a0f228bb210fb
awen-58k1-xctp | 1 |  | J7 Rw8 | 1236820458 | 22-03-2017 20:24:37 CET | Amani Desire | 01:25:36 | 2017 | Rwanda | Rulindo | Murambi | Mvuzo | Ntyaba |  |  | Mutagata Motorised Network | 26296 |  | 136 | 136 | 0 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 | https://waterforpeople.s3.amazonaws.com/images/f57e7817-4bb6-455e-b59e-6df187dcc16f.jpg | Yes | 5 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/6fbedb88-752a-4941-aae6-5733b9be0b94.jpg | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew | https://waterforpeople.s3.amazonaws.com/images/cd79bce0-1783-40eb-a52a-44dce1929b1e.jpg | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air Release | https://waterforpeople.s3.amazonaws.com/images/4a62075e-ca6c-48d3-975d-5e5abc4eddab.jpg | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 | https://waterforpeople.s3.amazonaws.com/images/33e5473d-76f1-4d8e-b513-3e5f496d91ee.jpg | 2017 | Normal | Yes | https://waterforpeople.s3.amazonaws.com/images/3699b43e-a1a2-4406-a08f-34e5e6ab8b03.jpg | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8121174083219544 | 30.022831714212202 | 1948.5 | 2b8wj24k | 64 | https://waterforpeople.s3.amazonaws.com/images/23e6a02b-6088-4649-9bdc-d65b44a7fc01.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | 67d09a7969063e2f9439c261d3695b1
yu3a-7ed7-ty6h | 1 |  | J7 Rw10 | 1199092922 | 02-01-2015 12:22:38 CET | Tuyisenge Vianney | 00:06:03 | 2017 | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water point at Buyoga Banque Populaire/Nyirambuga pumping | 30604 |  | 177 | 177 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point at Buyoga BPR.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6948497295162013 | 30.012444717505357 | 2078.2 | 25uykqxo | 6 | https://waterforpeople.s3.amazonaws.com/images/c9f508e1-7a08-42e0-97c3-b8b49f6d1905.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point at Buyoga BPR.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water | 559fe04462b7757d289219b34882e4cd
6a1b-jw95-pykh | 1 |  | J7 Rw10 | 1308490063 | 16-04-2017 22:59:13 CEST | Tuyisenge Vianney | 00:05:46 | 2017 | Rwanda | Rulindo | Buyoga | Karama | Kigarama |  |  | Kigarama water point/Nyirambuga pumping | 30604 |  | 121 | 121 | 0 | Yes | Piped Network with Pump |  | 2017 | No |  | Governement (District, WASAC) and Water For People | under construction | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.6895716624812134 | 29.976309736870697 | 1861.1 | 25m8taur | https://waterforpeople.s3.amazonaws.com/images/7b9ed55d-dd88-4c73-b198-269063c89815.jpg | 2017 | Does Not Function | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6873117230290016 | 29.975499349209755 | 1838.3 | 25ii9c4q | 2 | https://waterforpeople.s3.amazonaws.com/images/5313b3f3-4854-4f6a-be2d-e37dbb5e4014.jpg | 2017 | Does Not Function | No |  |  |  | No | construction works progress | Does Not Function | under construction | f4391d8148614e6e6963c1e16603276
w1ab-rts6-ymnj | 1 |  | J7 Rw10 | 1300160093 | 15-04-2017 22:36:53 CEST | Tuyisenge Vianney | 00:06:54 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Buhande |  |  | Buhande water point/Tare-Rusiga pumping system | 9577 |  | 129 | 129 | 0 | Yes | Piped Network with Pump |  | 2015 | Yes | Buhande and Remera | Governement (District, WASAC) and Water For People | The water point is operational.It has been mapped again today due to the mistake made previously while recording it as located in Remera village | 10 | Spring | -1.7379838326200018 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.740266648546695 | 29.91882669676037 | 1847 | 27y2rjuc | 1 | https://waterforpeople.s3.amazonaws.com/images/b77a4d0a-33be-494e-9ef1-88b1234aba84.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The water point is operational.It has been mapped again today due to the mistake made previously while recording it as located in Remera village | bb7691ebab4a3b6cfe1cbf26fd5869a
gk9x-1ctw-tya0 | 1 |  | J7 Rw10 | 1277100070 | 05-04-2017 21:55:12 CEST | Tuyisenge Vianney | 00:10:51 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Tare |  |  | Nyakariba-Tare small gravity system | 9577 |  | 109 | 109 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | Local government in Ubudehe program | Nyakariba-Tare small gravity system for one water public point with R3m3 as well Sina Gerard Workshop | 1 | Spring | -1.669680932468877 | 29.88823550873981 | 1794.1 | 24pcm3ya | https://waterforpeople.s3.amazonaws.com/images/b757a063-8ac2-4786-94a7-0df9504e3fe7.jpg | Yes | 40 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/505f01b0-a0c7-4b5f-8a36-242713561726.jpg | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/69f90157-49d2-4dce-a4a8-c4a9f747f930.jpg | 2015 | Normal | 5 | Yes | 1 | -1.669550375999323 | 29.888339432749937 | 1811.2 | 24p4vh37 | https://waterforpeople.s3.amazonaws.com/images/20a36e10-af1f-46da-867b-fda7600d2955.jpg | 2015 | Normal | Yes | 1 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/5f4f039f-3b9b-4931-8b8f-8563d6e47abc.jpg | 2015 | Normal | Yes | 1 |  | 2015 | Normal | 500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6696629784187222 | 29.888168617879373 | 1669.7 | 24pbf8qp | 1 | https://waterforpeople.s3.amazonaws.com/images/387a43d3-247e-459e-aa42-08440000fb2f.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Nyakariba-Tare small gravity system for one water public point with R3m3 as well Sina Gerard Workshop | 7bbe641b57c8dae0f2d5c12a5baba0
8n6f-k7hk-57q3 | 1 |  | J7 Rw7 | 1443770179 | 04-06-2017 13:20:10 CEST | Rugirangoga Augustin | 00:24:02 | 2017 | Rwanda | Rulindo | Kisaro | Kamushenyi | Gatete |  |  | gahama | 10234 |  | 163 | 140 | 23 | Yes | Piped Network with Pump |  | 2012 | Yes | ruberano gatete mugomero gishinge nyakarekare kibingwe | waterforpeople | ntakibazo iri vomo rifite | 2 | Spring | -1.6675834297797398 | 30.0428712210569 | 1965.7 | 24lvl43w |  | Yes | 15 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 65 | Yes | 2 |  | 2012 | Normal | 12000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 | Pressure Break Tank¦Distribution Chamber¦washout,air release |  | 2012 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6124351303824385 | 30.03440978173257 | 2187.4 | 222o3it4 | 1 | https://waterforpeople.s3.amazonaws.com/images/0ebf341b-d4ed-465b-a00d-de97aaadc2a8.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal |  | f67f8a5419df33bf639cb15fce467ccf
w800-05bu-2y82 | 1 |  | J7 Rw10 | 1211500098 | 09-03-2017 10:52:41 CET | Tuyisenge Vianney | 00:09:57 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Remera water point from Rutare gravity on Tare pumping | 9577 |  | 228 | 228 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This water point has water however service delivery is almost none due to lack of tap manager. | 8 | Spring | -1.73798326200818 | 29.90585605970111 | 2048.48 | 27ub0pte |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2017 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 2000 | Yes | 1 | -1.7339006663625771 | 29.918548753396248 | 1854.7 | 27nk3v3l | https://waterforpeople.s3.amazonaws.com/images/28938c64-f008-439c-8a84-0227ffcd481e.jpg | 2015 | Normal | No | [5 empty] | Yes | 1 |  | 2015 | Normal | 2000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7338843570815312 | 29.918515145706117 | 1619.2 | 27niwzw1 | 1 | https://waterforpeople.s3.amazonaws.com/images/3d9d3407-45e8-4cac-9bcf-66e2df59a436.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Remera water point hasnt water tap manager | b331c71b7b03f8fd8ae7773014228a
wjpg-swy2-2h0h | 1 |  | J7 Rw26 | 1196340247 | 01-01-2015 20:20:32 CET | Byukusenge Elie | 00:34:59 | 2017 | Rwanda | Rulindo | Cyungo | Rwili | Nyabisasa |  |  | Sakara |  |  | 570 | 520 | 50 | Yes | Piped Network with Pump |  | 2015 | Yes | Kivumu,Nturo, Nyabisasa and Sakara | Governement (District, WASAC) and Water For People | it has source Nyamagana shared with Nyamagana gravitu and it was constructed in 2015 and the extensions in Kivumu and Nyabisasa villages was constructed in 2016 and it is not yet used by the community and the pumping station use main distribution reservoir of Nyamagana gravity as the suction reservoir | 2 | Spring | -1.5919947371749814 | 29.923957502559304 | 2015.8 | 214v5hgn | https://waterforpeople.s3.amazonaws.com/images/d446054e-9b91-4a73-822d-9bc5af42f869.jpg | Yes | 5 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/08351512-5742-4047-92c1-ffc3fb39167c.jpg | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/92770916-e30b-4d33-a2fa-90b8ce39690d.jpg | 2015 | Normal | 1200 | Yes | 2 | -1.6031327757439937 | 29.922709284118525 | 2131.4 | 21naedcr | https://waterforpeople.s3.amazonaws.com/images/e286ee52-d293-4251-b2ce-ad68bec6524e.jpg | 2015 | Normal | Yes | 5 | Distribution Chamber | https://waterforpeople.s3.amazonaws.com/images/f3a5ed07-37a7-43f4-be72-3658ac568e13.jpg | 2015 | Normal | Yes | 1 |  | 2016 | Normal | 2300 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/af57d7d8-28ba-442b-9493-f46a1f8227a7.jpg | 2015 | Normal | Yes | https://waterforpeople.s3.amazonaws.com/images/c5773eac-cdfd-4fdb-bfbe-cc10faa41cd9.jpg | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6031166340921956 | 29.92243824226304 | 2136.9 | 21n97i54 | 4 | https://waterforpeople.s3.amazonaws.com/images/41385f8c-d854-4d1a-b132-b98e05b8cdab.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This network is new pumping system and it has some extensions which are under construction and it covers four villages | 199681d565c3668fe129711f187f
6nsh-nwxt-66a3 | 1 |  | J7 Rw15 | 1199350906 | 09-03-2017 22:07:57 CET | Mukakarangwa Assoumpta | 00:08:30 | 2017 | Rwanda | Rulindo | Shyorongi | Rubona | Nyarunyinya |  |  | Bitete-Rwahi network | 1316 |  | 132 | 50 | 82 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.8336417737979869 | 29.94346668826428 | 1815.5 | 2c8iday2 |  | Yes | 12 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 12 | Yes | 1 |  | 2013 | Normal | 600 | Yes | 6 | 1.8336417737979869 | 29.94346668826428 | 1815.5 | 2c8iday2 |  | 2013 | Poor | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 1 |  | 2013 | Normal | 6500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8426762723196137 | 29.939068646034894 | 1693.6 | 2cnfzq66 | 1 | https://waterforpeople.s3.amazonaws.com/images/92eb5d7b-581d-4f98-9506-595a3065c9d2.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | c18ec343f8383f4fc5a14a3498c752ae
46jx-5kwa-62ya | 1 |  | J7 Rw19 | 1198260832 | 13-03-2017 06:45:59 CET | Kayinamura Innocent | 00:55:42 | 2017 | Rwanda | Rulindo | Ngoma | Munyarwanda | Busizi |  |  | Kabarore-Ngoma-Nyabuko network | 8284 |  | 100 | 30 | 70 | Yes | Piped Network with Pump |  | 2014 | Yes | Nyabuko, Kagwa, Kiruri, Busizi, Ngaru, Kirungu, Kiboha and Kigina | Governement (District, WASAC) and Water For People | The network has 17 water points and it serves 8 villages | 4 | Spring | -1.81233570766877171 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | No | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦Collection Chamber | 2014 | Normal | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.8118879629206273 | 30.003478805087482 | 2031 | 2b8iu32a |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 4 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.82108275886591 | 30.005560397701647 | 1932.4 | 2bnqkvmf | 17 | https://waterforpeople.s3.amazonaws.com/images/57510848-e4d8-4f10-af41-467eb7638fb3.jpg | 2014 | Normal | Yes | 1 | 10 | it was due to the road construction | Yes |  | Normal | - the network has 17 water points - water points are in good operation conditions except the water point at the source that is damaged - 4 water points don't have water toady - the pipes are in good conditions The pump is not working properly as it was expected during Design, today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy - the transformer at the pumping station doesn't offer the required energy for the pump The anti-hammer of pump are not functioning because of bad installation towards Nyabuko, towards Ngoma sector office - The suction tank is in bad physical condition. | 1e1af966a471bcdceec9c4fc204060c4
a5rf-x5tg-jgbd | 1 |  | J7 Rw19 | 1222231218 | 17-03-2017 05:22:39 CET | Kayinamura Innocent | 00:19:19 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gakoma |  |  | Musenge network | 6074 |  | 146 | 52 | 94 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma, Karehe, Rutonde, Gitaba, Kiruri, Buhera, Ruhanya, Kibamba and Karindi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.93859037216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Washout and Air release chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7833911502043553 | 29.96061721325848 | 2137.6 | 29xem49i | 28 | https://waterforpeople.s3.amazonaws.com/images/91fb85eb-3135-4a01-89d5-88d303c019ba.jpg | 2014 | Normal | No |  |  |  | Yes |  | Poor | 1. the system has two Pumps but one is damaged and is not working, only one pump is used to pump water 2. Eleven (11) water points served by the distribution reservoir R 50m3 located at Kibamba village do not have water today because water don't reach this reservoir, there is not water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5. one water point doesn't Function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water and reservoir being under construction | a91ab5b53769d0b19c4b4ab4ef31adb2
x4dt-9d4n-n8sm | 1 |  | J7 Rw23 | 1213010214 | 12-03-2017 18:40:05 CET | Rugirangoga Augustin | 00:30:50 | 2017 | Rwanda | Rulindo | Base | Gitare | Kirwa |  |  | Rwicanyoni | 698 |  | 136 | 101 | 35 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | kirwa gatete gisiza | Governement (District, WASAC) and Water For People | this net work has enough water and it works properly | 2 | Groundwater (well, etc.) | -1.6644377224987001 | 29.909270742116649 | 1808.8 | 24go1jis |  | Yes | 10 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 10 | Yes | 1 |  | 2016 | Normal | 8600 | Yes | 3 | -1.6605194594779042 | 29.90927074216649 | 1808.8 | 24a6nmdw | https://waterforpeople.s3.amazonaws.com/images/2e423b64-1ac5-4e53-82c9-852eecb2f08d.jpg | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.658812879196903 | 29.911052497350177 | 1764.2 | 247dfxk6 | 2 | https://waterforpeople.s3.amazonaws.com/images/16016486-b2d7-43b9-b368-e474f8d256ae.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | this network has no problems | 363cc55eb6af70a5fcf37248cc61bb7a
b04v-s6e5-4bdu | 1 |  | J7 Rw19 | 1193850108 | 06-03-2017 10:30:33 CET | Kayinamura Innocent | 00:30:33 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  |  | 510 |  | 30 | 30 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | WFP | Normal | 1 | Spring | -1.986258277324145 | 30.10280014493059 | 1526.1 | 2j8wdj50 | https://waterforpeople.s3.amazonaws.com/images/00794e13-7f1b-4b2c-82d8-24a089ce5954.jpg | Yes | 14 | Yes | 5 | https://waterforpeople.s3.amazonaws.com/images/9d2be736-c45c-4a67-842d-7bcce0256e2a.jpg | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 20 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/bf1396cb-d5b7-4174-adea-cbc041e4f31f.jpg | 2015 | Normal | 1500 | Yes | 1 | -1.9863117482767227 | 30.102751772441422 | 1478 | 2j8zy4rn | https://waterforpeople.s3.amazonaws.com/images/05250ee1-617f-4a19-a63c-fe231e1f35b0.jpg | 2015 | Normal | Yes | 3 | valve chamber | https://waterforpeople.s3.amazonaws.com/images/230f479d-6437-4730-9502-2b15cacb29aa.jpg | 2015 | Normal | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/d92f94aa-e0b9-488c-8d6e-f305cd7059ed.jpg | 2015 | Normal | 500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.9864090414959428 | 30.102766388944897 | 1474 | 2j95b17n | 5 | https://waterforpeople.s3.amazonaws.com/images/797d607e-fd59-4625-9331-8c30dc48624c.jpg | 2015 | Normal | Yes | 1 | 1 | pipe break | Yes |  | Normal |  | 99c32fa666bb866c3330b2c979cd2878
db6r-wtvt-76re | 1 |  | J7 Rw10 | 1318560314 | 20-04-2017 07:09:10 CEST | Tuyisenge Vianney | 00:04:18 | 2017 | Rwanda | Rulindo | Tumba | Misezero | Kavumu |  |  | Water point chez Habarugira/Nyirambuga pumping | 30604 |  | 139 | 139 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | In use | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6989226438420053 | 29.957004515047764 | 2057.8 | 261phlbm | 2 | https://waterforpeople.s3.amazonaws.com/images/9955a3f6-ab7b-4362-8419-f8e660cde25a.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | In use | 7c7c1c37998738b85dbdd33e7b7afaa
p119-twwg-4g83 | 1 |  | J7 Rw10 | 1278690081 | 05-04-2017 21:23:59 CEST | Tuyisenge Vianney | 00:10:17 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Ngarama |  |  | Nyabishengeshi gravity system/Water point at Nyirangarama | 893 |  | 89 | 89 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People | Not enough water in Nyirangarama village on Nyabishengeshi gravity | 1 | Spring | -1.6778517470929726 | 29.880934967401814 | 2032.3 | 252v194p |  | Yes | 50 | No | [5 empty] | 50 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6702189728433396 | 29.885875358256023 | 1855.5 | 24q862zu | 1 | https://waterforpeople.s3.amazonaws.com/images/a06885e0-6e47-480d-8bb2-638439a33b7d.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | Not enough water in Nyirangarama village on Nyabishengeshi gravity | b554131754adf576744ca2edf2e7d7e
m521-s0dg-9t61 | 1 |  | J7 Rw10 | 1229060243 | 03-01-2015 00:16:44 CET | Tuyisenge Vianney | 00:05:29 | 2017 | Rwanda | Rulindo | Tumba | Taba | Mwili |  |  | Mwili2 water point/Nyirambuga pumping | 30604 |  | 141 | 141 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Another water point at Mwili its structure has started getting demolished due to bad management.Cement mortar has cracked and internal bricks are exposed to air | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7307861859359026 | 29.97265937554193 | 2044 | 27iecmry | 2 | https://waterforpeople.s3.amazonaws.com/images/42a1fe0c-b14f-4c1f-b216-a35197114e70.jpg | 2015 | Poor | No |  |  |  | Yes |  | Poor | Another water point at Mwili its structure has started getting demolished due to bad management.Cement mortar has cracked and internal bricks are exposed to air | a475bd331850b23a40b5ea92d1c5797b
7uhq-b71w-ccp5 | 1 |  | J7 Rw23 | 1200740141 | 07-03-2017 10:24:58 CET | Rugirangoga Augustin | 01:07:48 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 1789 |  | 192 | 100 | 92 | Yes | Piped Network -- Gravity Only |  | 2012 | Yes | karambi gitovu | padiri | There are others systems being bult to support this | 3 | Spring | -1.613001918870488 | 29.875135077266787 | 1921.6 | 223m1727 |  | Yes | 60 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 60 | Yes | 2 |  | 2012 | Normal | 6450 | No | [8 empty] | No | [5 empty] | Yes | 1 |  | 2012 | Normal | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.610683458935011 | 29.881261983420583 | 1838.6 | 21zrwmrg | 1 |  | 2012 | Normal | No |  |  |  | Yes |  | Normal | water forpeople needs to bwild its own network from the source rwankende.because Padiri refused the rienforcement of his network.that is why some reservoirs do not get water from the source | 5ead388737d81d653d22c5bb12afa163
7hy2-mu82-nfq2 | 1 |  | J7 Rw15 | 1237250151 | 21-03-2017 16:13:36 CET | Mukakarangwa Assoumpta | 00:14:20 | 2017 | Rwanda | Rulindo | Kinihira | Rebero | Kirwa |  |  | Miyove-Kinihira | 10452 |  | 187 | 60 | 127 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6680925579345127 | 29.983571535329283 | 2021.7 | 24mpy7i3 | 1 | https://waterforpeople.s3.amazonaws.com/images/066270a0-56ee-4a01-8a88-4392133d066c.jpg | 1989 | Poor | No |  |  |  | Yes |  | Poor |  | 3d4a14aa4a915acc68b375ee3b472b0
xxyy-1gkr-4n1g | 1 |  | J7 Rw23 | 1216750416 | 15-03-2017 06:05:53 CET | Rugirangoga Augustin | 00:15:07 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Kabahama |  |  | Migogo | 558 |  | 178 | 150 | 28 | Yes | Piped Network -- Gravity Only |  | 2009 | Yes | kabahama kiruli bukangano Rubanda | Padiri(Lake Angels). | partial rehabilitation is needed for this network | 1 | Groundwater (well, etc.) | -1.6327309674421784 | 29.901262305566668 | 1800.8 | 2308pft0 |  | No | 60 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2009 | Normal | 50 | Yes | 2 |  | 2009 | Poor | 6200 | Yes | 1 | -1.6327309674421784 | 29.901262305566668 | 1900.3 | 2308pft0 |  | 2009 | Poor | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6351123757129316 | 29.895306742506815 | 1649.5 | 2346elqh | 1 | https://waterforpeople.s3.amazonaws.com/images/c1619514-5807-46ad-848f-ca1ecd8fb13a.jpg | 2009 | Poor | No |  |  |  | Yes |  | Poor | the network works but partialy | 4e4d755bc51ed2ac5f52cd5b2fb5e64f
pauw-f24b-3h69 | 1 |  | J7 Rw26 | 1198410924 | 02-01-2015 05:49:39 CET | Byukusenge Elie | 00:09:34 | 2017 | Rwanda | Rulindo | Cyungo | Rwili | Kabanda |  |  | Nyamagana | 20456 |  | 50 | 26 | 24 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6153281437274651 | 29.92817463920362 | 1841.6 | 227g5rtd | 29 | https://waterforpeople.s3.amazonaws.com/images/6043c47f-51f7-47c1-a75d-72c7819bd849.jpg | 2011 | Poor | Yes | 7 | 30 | The distribution reservoir does not supply water in this transmission line | No | bad connection of tee junctions towards Gatovu | Poor | Kabanda village does not have clean water from network they use spring water | 828369378804721d88ebc52c823956c
eerv-y2jm-nmna | 1 |  | J7 Rw8 | 1237480410 | 23-03-2017 10:37:38 CET | Amani Desire | 00:09:12 | 2017 | Rwanda | Rulindo | Murambi | Bubangu | Rebero |  |  | Mutagata Motorised Network | 26296 |  | 148 | 78 | 70 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366138367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦washout and Air release chamber |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8494422592341817 | 30.03080188208526 | 1798.7 | 2cyn27f8 | 64 | https://waterforpeople.s3.amazonaws.com/images/21a766f4-0cc6-444a-9aa4-f7e275be19f0.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | e53999fcd6d794bec266afa3d8026
gcq7-536w-1k5k | 1 |  | J7 Rw8 | 1241920617 | 23-03-2017 10:26:01 CET | Amani Desire | 00:15:15 | 2017 | Rwanda | Rulindo | Murambi | Bubangu | Gashubi |  |  | Mutagata Motorised Network | 26296 |  | 140 | 32 | 108 | Yes | Piped Network with Pump |  | 1987 | Yes | rurama,Ntyaba,ruhunga,gashubi,rebero, taba,nyagisozi,akarambi,kabeza,Munyinya,nyarurembo (Murambi),nyarurembo (masoro),kigarama,karambi,kanunga, amahoro,nyakizu,gisiza,gasenga,rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release chamber |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8410960566627086 | 30.028331599211665 | 1824.1 | 2cktx9a3 | 64 | https://waterforpeople.s3.amazonaws.com/images/9b043ddb-b8b0-4734-9250-4b185a26f82b.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1.The system is New , in general it is in good operational conditions 2.Four (4) water points don't have Water because water pipes has broken due to high pressure 3.The System has a pumping Station ( with 3 pumps)at the source and it has booster Station (with two pumps)located at Murambi 4.All pumps are in good Operational Conditions 5.The system has 64 water points and 39 Reservoirs 6.This system serves the big parts of Murambi and Masoro Sectors and 1cell in Cyinzuzi Sector 7.It serves 10 schools and 2 Health Centres 8.Three water points don't have water access for 7days due to Management issue 9.Most of water taps on water points are damaged due to the low quality of material of Taps | 448833c3ade0165aaf3cc1512c69159e
x1ym-ryhb-0d17 | 1 |  | J7 Rw10 | 1230180257 | 03-01-2015 02:11:23 CET | Tuyisenge Vianney | 00:03:36 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | WATER POINT AT VTC TUMBA/Nyirambuga pumping | 30604 |  | 169 | 169 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Everything operates normally the water is available everyday | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.696701795247508 | 29.942901777025615 | 2148.7 | 25y1bcx1 | https://waterforpeople.s3.amazonaws.com/images/8f88e372-e7a2-4528-95e1-99a164a78860.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6966842337656265 | 29.942872502367575 | 2159.4 | 25y04hpg | 2 | https://waterforpeople.s3.amazonaws.com/images/924db298-b0f7-459c-927c-7b7d1c9e9461.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Everything operates normally the water is available everyday | d3f366f5726f39885f3e2dd68996ab
6jdw-hyc8-4reb | 1 |  | J7 Rw19 | 1244910061 | 24-03-2017 04:55:32 CET | Kayinamura Innocent | 00:05:56 | 2017 | Rwanda | Rulindo | Masoro | Kivugiza | Rebero |  |  | Mutagata motorised network | 26296 |  | 376 | 115 | 261 | Yes | Piped Network with Pump |  | 1987 | Yes | Rurama, Ntyaba, Ruhunga, Gashubi, Rebero, taba, Nyagisozi, akarambi, kabeza, Mjnyinya, Nyarurembo (Murambi), Nyarurembo (Masoro), Kigarama, Karambi, Kanunga, Amahoro, Nyakizu, Gisiza, Gasenga, Rubaya | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8018522287450358 | 30.042875565044753 | 1708.3 | 2arxobm4 |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2007 | Normal | 5 | Yes | 1 |  | 2016 | Normal | 1900 | Yes | 39 | -1.7968944299728253 | 30.023242366198367 | 2125.2 | 2ajqdbew |  | 2016 | Normal | Yes | 17 | Pressure Break Tank¦Distribution Chamber¦Washout and Air release |  | 2016 | Normal | Yes | 6 |  | 2016 | Normal | 40000 | Yes | 5 |  | 2017 | Normal | Yes |  | 2016 | Normal | Yes |  | Disinfection/Chlorination | 2017 | Normal | No |  |  |  | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7921906284105547 | 30.06630044658361 | 1772.9 | 2abyjlfb | 64 | https://waterforpeople.s3.amazonaws.com/images/c3fb1754-a627-4e37-92f5-d2b936363bc8.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | 1. this system is new, in general it is in good operational Conditions 2. Four (4) water points don't have water because water pipes has broken due to high pressure 3. The system has a pumping station (with 3 pumps) at the source and it has booster station ( with two pumps) located at Murambi 4. All pumps are in good operational Conditions 5. The sytem has 64 water points and 39 reservoirs 6. This system serves the big parts of Murambi and Masoro sectors and 1 cell in Cyinzuzi Sector 7. it serves 10 Schools and 2 health centers 8. Three water points don't have water access for 7 day s due management issues 9. most of water taps on water points are damaged due to the low quality of material of taps | 1bf41bc475739f82373b692713edf524
syg2-s11k-xk6m | 1 |  | J7 Rw26 | 1238180394 | 03-01-2015 04:51:31 CET | Byukusenge Elie | 00:09:40 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Shyondwe |  |  | Kabonanyoni | 7894 |  | 125 | 120 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare, Kabera,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe, Kabyayi, Kabingo, Kamiyove, Murwa, Nyenyeri, Rukingu and Kivomo | Governement (District, WASAC) and Water For People | This is the New pumping system which serves the community located at the uphill, it has 5 sources, one source which is located in Miyove sector, Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro,This network has one reservoir which is not functioning, This network serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 10 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.643468673665249 | 29.959145138778183 | 1989.6 | 23hzjkcn | 31 | https://waterforpeople.s3.amazonaws.com/images/7b2f90e4-a627-46d3-8a7a-d2582262a658.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is also used by the community of Kivomo village who doesn't served with Nyamagana Network | 530c7b7e8a0e8122bda3fd2ad6fbe
b2qw-5sx1-srsf | 1 |  | J7 Rw23 | 1241620234 | 23-03-2017 17:25:37 CET | Rugirangoga Augustin | 00:33:45 | 2017 | Rwanda | Rulindo | Buyoga | Ndarage | Karambi |  |  | Ndarage |  |  | 112 | 100 | 12 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | karambi Gasave Gahondo Bunyana Rugarama Gasave | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.6829614865475908 | 30.031434012077444 | 1962 | 25bb9sey |  | Yes | 30 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 30 | Yes | 1 |  | 2014 | Normal | 6700 | Yes | 5 | -1.6902852583901373 | 30.03414816539013 | 1811.8 | 25nf3391 |  | 2014 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7028831474571475 | 30.032607807047253 | 1616.5 | 268999gm | 1 | https://waterforpeople.s3.amazonaws.com/images/64f1d953-3eb0-4bd6-8749-ca7d63869169.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | this network works well | e079256ce5b79ced846c49335e86e70
kx4y-bk8v-052p | 1 |  | J7 Rw15 | 1210770271 | 08-03-2017 22:23:35 CET | Mukakarangwa Assoumpta | 00:06:59 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Mwagiro |  |  | Kirikumuryango network |  |  | 139 | 37 | 102 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8813976140576751 | 29.97163845029334 | 1494.7 | 2efha4qs | 1 | https://waterforpeople.s3.amazonaws.com/images/1afcc260-af5e-4478-b84a-c5760202c49f.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 43997e482cb4c25788cf924c2e194e1
9pdq-x58w-vj5w | 1 |  | J7 Rw26 | 1215510088 | 11-03-2017 08:57:18 CET | Byukusenge Elie | 00:13:59 | 2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 20456 |  | 780 | 780 | 0 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank | This network serves four sectors Cyungo,Rukozo, Base,Base and Kinihira, It has some problems in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible because it serves many populations and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 1913.1 | 1913.1 | 5r24ouhyw |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6222425226778736 | 29.94815862179986 | 1852.6 | 22iw5ql5 | 29 | https://waterforpeople.s3.amazonaws.com/images/bac740ad-39cf-44ce-99ea-cf65be4079b3.jpg | 2011 | Normal | Yes | 15 | 20 | Bad tee junctions connection and Bad location of distribution reservoir in Rukozo even Main Reservoir in Sakara is not well located,and the types of pipeline needs to be replaced. | Yes |  | Poor | water tap is used by the students in E.S.Rukozo and the school staff. | ec5ef822151918bc3d67f870baaf
hmnt-mp3b-9qhm | 1 |  | J7 Rw24 | 1214101798 | 15-03-2017 14:46:35 CET | Kabalisa Manzi Christella | 00:19:42 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kavumu |  |  | 0 | 6572 |  | 850 | 850 | 0 | Yes | Piped Network with Pump |  | 2014 | No |  | Governement (District, WASAC) and Water For People | System is not functional | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 2 | -1.7555179528295524 | 30.03970289656239 | 1690.5 | 28napmb1 | https://waterforpeople.s3.amazonaws.com/images/ddee9833-f934-4bf6-9c7a-8b1aecc0c0c1.jpg | 2014 | Does Not Function | Yes | 8 | Pressure Break Tank | https://waterforpeople.s3.amazonaws.com/images/fe2551fa-cf87-40e3-8825-169349b7c694.jpg | 2014 | Does Not Function | Yes | 2 |  | 2014 | Does Not Function | 3000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7544470330541122 | 30.040594996866243 | 1628.8 | 28lj08l1 | 1 | https://waterforpeople.s3.amazonaws.com/images/f6a40573-74d2-40ba-a827-870f4a2d29bc.jpg | 2014 | Does Not Function | Yes | 365 | 0 | Since the system was built no water is flowing | No | Three years without Water | Does Not Function | Water is not Flowing now its three years | f9204bac12ca99c52059aec146ea6f7
dhyx-xjyf-u57p | 1 |  | J7 Rw10 | 1210470509 | 10-03-2017 12:18:57 CET | Tuyisenge Vianney | 00:09:40 | 2017 | Rwanda | Rulindo | Bushoki | Mukoto | Marembo |  |  | Water point at GS Bushoki/Tare-Rusiga pumping system | 9577 |  | 90 | 90 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This a double tap water point at GS Bushoki.It operates normally | 10 | Spring | -1.7379838326200818 | 29.906994158112184 | 2048.8 | 27ub0ptp |  | Yes | 40 | Yes | 8 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 40 | Yes | 1 |  | 2015 | Normal | 4000 | Yes | 1 | -1.7145961962732041 | 29.899939717198958 | 2134 | 26rmfttj | https://waterforpeople.s3.amazonaws.com/images/5d62f565-8f2c-4a75-bedb-b74bff321b82.jpg | 2015 | Normal | No | [5 empty] | Yes | 1 |  | 2015 | Normal | 8000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7143868772783584 | 29.898981230833282 | 2162.1 | 26r9xq3x | 2 | https://waterforpeople.s3.amazonaws.com/images/8aa6f8fe-8d6c-4f4a-9cea-7b8aa6bcb5c6.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | GS Bushoki water point operates normally.The storage tank serves the GS Bushoki water point and Rusave water point | 6a89258d21376e5a233ac3fc06a9f6c
bsd0-dpqn-we5u | 1 |  | J7 Rw23 | 1218910361 | 15-03-2017 11:03:35 CET | Rugirangoga Augustin | 00:35:12 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Karambi |  |  | Rwankende | 1789 |  | 192 | 180 | 12 | Yes | Piped Network -- Gravity Only |  | 2012 | Yes | karambi gitovu | Padiri | the source gihanga is divergin divis | 2 | Spring¦Groundwater (well, etc.) | -1.6128815953757245 | 29.874655017548616 | 1956.1 | 223evzsq | https://waterforpeople.s3.amazonaws.com/images/adeab207-ebc5-411a-a3d4-9dc01e1bb5bd.jpg | Yes | 60 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/6dfd62af-6e43-4b17-adb2-9edb185c24fe.jpg | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 45 | Yes | 2 |  | 2016 | Normal | 6450 | Yes | 3 | -1.6111677762752643 | 29.8839135826884 | 1852 | 220khftj |  | 2016 | Normal | Yes | 1 | Distribution Chamber |  | 2016 | Normal | Yes | 2 |  | 2016 | Normal | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6127220550456884 | 29.87469624913539 | 1913.5 | 2235d24a | 1 | https://waterforpeople.s3.amazonaws.com/images/03a3f788-1aa2-438d-b0fa-07e25fe42c35.jpg | 2016 | Poor | No |  |  |  | Yes |  | Normal |  | e4464af8a14e6a5ca817a1496e499aea
gbas-pdue-xm1y | 1 |  | J7 Rw10 | 1230180282 | 03-01-2015 02:07:06 CET | Tuyisenge Vianney | 00:05:07 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Bukiga |  |  | Water point at ADEPR Tumba/Nyirambuga pumping | 30604 |  | 169 | 169 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Everything operates normally the water is available everyday | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6926589110083592 | 29.939986788372195 | 2141.9 | 25rc6sw7 | 2 | https://waterforpeople.s3.amazonaws.com/images/43b9f2e6-01ef-4e13-a9e6-c8da5af069bd.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Everything operates normally the water is available everyday | e1bd4f55ba2e5dffd3ab2b87bcb810
194y-gwat-xhcy | 1 |  | J7 Rw24 | 1325690155 | 24-04-2017 23:55:56 CEST | Kabalisa Manzi Christella | 00:10:34 | 2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Karera |  |  | Rwamugaza network | 14106 |  | 182 | 182 | 0 | Yes | Piped Network -- Gravity Only |  | 2014 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7374173333138418 | 30.006563288387298 | 1723.9 | 27td3141 |  | 2003 | Normal | Yes | 14 |  |  | 2003 | Normal | Yes | 1 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8004481191671582 | 30.09339256861318 | 1582.9 | 2aplq7ph | 1 | https://waterforpeople.s3.amazonaws.com/images/201e5606-ebaa-4763-9940-c6115ce0e700.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal |  | e029209a27ef87514cd202579e6661f
2xct-fhrj-9xxt | 1 |  | J7 Rw8 | 1441560314 | 04-06-2017 15:32:54 CEST | Amani Desire | 00:21:38 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Ruhanya |  |  | musenge | 6074 |  | 40 | 40 | 0 | Yes | Piped Network with Pump |  | 2014 | No |  | water for people |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.8 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.8 | Yes | 1 |  | 2014 | Poor | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber¦washout and Air release chamber |  | 2014 | Normal | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Poor | Yes |  | 2014 | Poor | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7454505144859878 | 29.939120017266063 | 1958.4 | 286nriyn | 1 | https://waterforpeople.s3.amazonaws.com/images/d250d66c-ea02-4295-9264-4cd53682f237.jpg | 2014 | Does Not Function | Yes | 6 | 30 | the water poont has been damaged and water dont reach this water point | No | water dont reach this water point | Does Not Function |  | a72a83ec05baf9e4b1cfd1ac13d7cf6
tg8e-arpe-4jes | 1 |  | J7 Rw23 | 1226490233 | 15-03-2017 08:01:01 CET | Rugirangoga Augustin | 00:15:00 | 2017 | Rwanda | Rulindo | Base | Cyohoha | Rubanda |  |  | Gihanga | 2456 |  | 214 | 200 | 14 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | rubanda mushongi buramba kabuga | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6358367374763643 | 29.9135277934778 | 1996.9 | 235d9tfj |  | Yes | 15 | No | [5 empty] | 15 | Yes | 1 |  | 2016 | Poor | 7200 | Yes | 6 | -1.6498521069502532 | 29.917613599705728 | 1996.9 | 23sjzjl4 |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6439783793130531 | 29.90208520449291 | 1778.5 | 23itwnrg | 2 | https://waterforpeople.s3.amazonaws.com/images/e153b606-5d90-4c4b-98a8-73422664c900.jpg | 2016 | Does Not Function | No |  |  |  | No | not enough pressure | Does Not Function | this net work is not working properly | 3cf7441bc5b9a1646e85e017e2c5573a
d8fp-s57r-w9kj | 1 |  | J7 Rw10 | 1300190066 | 15-04-2017 22:17:25 CEST | Tuyisenge Vianney | 00:05:37 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Remera |  |  | Water point at EP Gasiza/Nyagahondo gravity system | 844 |  | 228 | 228 | 0 | Yes | Piped Network -- Gravity Only |  | 2010 | No |  | Caritas | The water point has the tap stand though it has started getting damaged.The water is available in the tap and gots used by the students of EP Gasiza | 1 | Spring | -1.7298781428197503 | 29.909858739201194 | 2099.2 | 27gw668q |  | Yes | 30 | No | [5 empty] | 30 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.731060940451315 | 29.921652062706265 | 1772.5 | 27iv0rbk | 1 | https://waterforpeople.s3.amazonaws.com/images/93e48598-43bc-4398-b61b-f1d482b239e3.jpg | 2010 | Normal | No |  |  |  | Yes |  | Normal | The water point has the tap stand though it has started getting damaged.The water is available in the tap and gots used by the students of EP Gasiza | 326aa76e3be532b6dea5dbc2239f8
3tj0-9vej-x00v | 1 |  | J7 Rw15 | 1243470332 | 21-03-2017 17:23:38 CET | Mukakarangwa Assoumpta | 00:15:54 | 2017 | Rwanda | Rulindo | Kinihira | Rebero | Karambi |  |  | Miyove-Kinihira | 10452 |  | 144 | 60 | 84 | Yes | Piped Network -- Gravity Only |  | 2001 | No |  | GKWW |  | 6 | Spring | 1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 |  | Yes | 5 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 |  | 1989 | Poor | 8000 | Yes | 4 | 1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 |  | 1989 | Normal | Yes | 18 | Distribution Chamber¦ventouse ,Washout |  | 1989 | Poor | Yes | 2 |  | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.675800180230818 | 29.979375567003633 | 1974.7 | 24zgzevl | 1 | https://waterforpeople.s3.amazonaws.com/images/74ef3660-799c-4204-b15f-7e5e5d230c1a.jpg | 1989 | Does Not Function | No |  |  |  | Yes |  | Poor | Water point does not function and they have access to the water point of Gatembe. | cba445e6ddbc256cca97a156828e849a
ntbc-r10j-hfns | 1 |  | J7 Rw19 | 1252090193 | 28-03-2017 11:46:22 CEST | Kayinamura Innocent | 00:08:35 | 2017 | Rwanda | Rulindo | Ngoma | Mugote | Rukoma |  |  | Kararama pumping network | 6572 |  | 92 | 45 | 47 | Yes | Piped Network with Pump |  | 2007 | Yes | Riryi,nyakibyeyi,marembo,ngabitsinze, musenyi,munoga,remera,nyagisozi,rwamiko,kiziba,kisigiro,gacyamo,muhondo | Government |  | 4 | Spring¦Collection chamber | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | No | 6 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring¦Collection chamber | 2007 | Normal | 6 | Yes | 1 |  | 2007 | Normal | 1500 | Yes | 25 | -1.7543004341479447 | 29.99197561543003 | 2178 | 28lao5qn |  | 2007 | Normal | Yes | 20 | Distribution Chamber¦Washout and Air release chamber |  | 2007 | Normal | Yes | 4 |  | 2007 | Poor | 30000 | Yes | 2 |  | 2007 | Poor | Yes |  | 2007 | Poor | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.791959128272212 | 30.002539670619623 | 2110.7 | 2abk96ex | 47 | https://waterforpeople.s3.amazonaws.com/images/a9cd37b6-a884-44bf-9ed0-8705c8cbf2c6.jpg | 2007 | Does Not Function | No |  |  |  | No | water don't reach this water point | Does Not Function | 1.the system has two pumps but only one is functioning 2.The source and the pumping station are under total rehabilitation 3. Water points located in Ngoma sector do not have water 4.this network serves Ngoma, cyinzuzi and Ntarabana sectors | d8ea114ae8828c1ebea15c71c1fd84d
m125-6wf2-7vxh | 1 |  | J7 Rw8 | 1205081304 | 10-03-2017 10:18:00 CET | Amani Desire | 00:24:53 | 2017 | Rwanda | Rulindo | Ngoma | Kabuga | Kagarama |  |  | Kabarore- Ngoma- Nyabuko network | 8284 |  | 57 | 57 | 0 | Yes | Piped Network with Pump |  | 2014 | Yes | nyabuko,kagwa,kiruli,busizi, ngaru, kirungu,kiboha,kigina | Governement (District, WASAC) and Water For People | the network has 17 water points and it serves 8 villages | 4 | Spring | -1.8123357076877171 | 29.96790053996267 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦collection chamber | 2014 | Poor | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.808716485895084 | 29.973362007273437 | 2001 | 2b3a3o2d |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8321394972075067 | 29.97783526609216 | 1950.3 | 2c60guv6 | 17 | https://waterforpeople.s3.amazonaws.com/images/6abc37e2-ef30-48ce-b0f0-6ba105679ec2.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | -the network has 17 water points -water points are in good operational conditions except the water point at the source that is damaged -4 water points don't have water today -the pipes are in good operational conditions -The pump is not working properly as it was expected during Design ,Today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy -the transformer at the pumping station doesnt offer the required energy to the pump -the anti hammers of pump are not functioning because of bad installation of pumping house -the system has two pumps with four units with two units pumping in one direction towards Nyabuko and other two in an other direction towards ngoma sector office -The suction tank is in bad physical conditions | a1526e310f811d7689b205477edd7bd
ys9y-w07b-rn9j | 1 |  | J7 Rw23 | 1320230055 | 23-04-2017 14:43:06 CEST | Rugirangoga Augustin | 00:17:29 | 2017 | Rwanda | Rulindo | Buyoga | Gahororo | Gipfundo |  |  | rugarama |  |  | 162 | 120 | 42 | Yes | Piped Network -- Gravity Only |  | 2012 | No |  | G. thierry | This system was funded by Jado-thierry | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761. | 24mtitma |  | Yes | 30 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 30 | Yes | 1 |  | 2012 | Normal | 4500 | Yes | 4 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2012 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7175250825793835 | 30.080033344510202 | 1536.4 | 26wgvvgg | 1 | https://waterforpeople.s3.amazonaws.com/images/d98b4fbd-47be-4315-ac93-006d9c6aa757.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | This System originates from Gicumbi District | c6df6ff09a295d2ee29acff1436303e
6jfa-vdj7-gnb1 | 1 |  | J7 Rw26 | 1203970087 | 02-01-2015 05:51:13 CET | Byukusenge Elie | 00:13:43 | 2017 | Rwanda | Rulindo | Cyungo | Burehe | Sove |  |  | Nyamagana | 20456 |  | 75 | 35 | 40 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | All villages of Burehe and Rwili cells in Cyungo,Kinihira village ,all villages of Mberuka and Bwimo cells in Rukozo and Kabingo village in Base sector | Government and African Development Bank | This network serves four sectors Cyungo, Rukozo, Base and Kinihira and iy has some problem in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible as it serves many population and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2011 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Normal | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6296155672266062 | 29.93148275966692 | 1879.4 | 22v2y7aq | 29 | https://waterforpeople.s3.amazonaws.com/images/606f7e30-83f0-49f4-86d8-a5887da0fb8d.jpg | 2011 | Normal | No |  |  |  | No | The distribution reservoir does not supply water in this transmission line network towards Paroisse Burehe | Poor | This water tap at paroisse ,is not used they prefer the rain water | 6b17a9621fa8d7f4bdb9d33d2df97b38
m242-yyfc-1kae | 1 |  | J7 Rw23 | 1324470185 | 23-04-2017 14:43:38 CEST | Rugirangoga Augustin | 00:21:27 | 2017 | Rwanda | Rulindo | Buyoga | Gahororo | Gatenderi |  |  | kiruruma | 8295 |  | 141 | 100 | 41 | Yes | Piped Network with Pump |  | 2014 | Yes | gatenderi gatare shagasha rutabo | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2017 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 11 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2014 | Normal | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 9000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7232472639467338 | 30.064656438973454 | 1627.4 | 275xftd2 | 1 | https://waterforpeople.s3.amazonaws.com/images/297b2573-3263-4c96-acac-e5e5a7bc28e1.jpg | 2014 | Poor | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | ec19e387d5f462de12785e8a575c717
881c-4nfs-pmb6 | 1 |  | J7 Rw23 | 1201760451 | 08-03-2017 08:08:33 CET | Rugirangoga Augustin | 00:30:29 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutembe | 1012 |  | 229 | 229 | 0 | Yes | Piped Network -- Gravity Only |  | 2016 | No |  | Governement (District, WASAC) and Water For People | Water doent reach the last resevoir | 2 | Spring | -1.6452293607002955 | 29.88940159790624 |  | 23kwbua6 |  | Yes | 45 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2017 | Normal | 45 | Yes | 1 |  | 2017 | Normal | 2500 | Yes | 1 | 1.6350822337877793 | 29.89531663121816 | 1775.7 | 2344max5 |  | 2016 | Normal | Yes | 3 | Distribution Chamber |  | 2016 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6491376822935664 | 29.885958356298563 | 1810.6 | 23rd4bsb | 1 |  | 2016 | Normal | No |  |  |  | Yes |  | Normal | Water system is functional but in some parts pipes were destroyed | a7673a8235311540d1fc81646d2859e9
dbsc-rsj9-8qs6 | 1 |  | J7 Rw10 | 1221411010 | 15-03-2017 16:54:52 CET | Tuyisenge Vianney | 00:05:22 | 2017 | Rwanda | Rulindo | Rusiga | Gako | Kabuye |  |  | Kabuye water point[RW.WFP.Q3.14.166.066]/Tare-Rusiga pumping | 9577 |  | 169 | 169 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | This water point operates well and normally | 10 | Spring | -1.7379838326200818 | 29.90585605970111 | 2048.8 | 27ub0pte |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7954414753040822 | 29.93176228326588 | 2081.5 | 2ahc1fzp | 2 | https://waterforpeople.s3.amazonaws.com/images/aeb827d3-340c-4e4d-aef4-37c078014893.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water point operates well and normally | 618e32ff9a68a3a676d6fc43ecbe98
uf0s-b0nw-1tud | 1 |  | J7 Rw15 | 1212920218 | 12-03-2017 11:12:55 CET | Mukakarangwa Assoumpta | 00:13:01 | 2017 | Rwanda | Rulindo | Shyorongi | Muvumu | Nyabubare |  |  | Bitete-Muvumu | 1316 |  | 97 | 35 | 62 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 3 | Spring | 1.8337482672601935 | 29.943433443706404 | 1749 | 2c8obmzu |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Poor | 11 | Yes | 1 | 1.8368127107947887 | 29.93457412501046 | 1635 | 2cdr3pn5 |  | 2013 | Normal | Yes | 6 | Pressure Break Tank¦Distribution Chamber¦ventouse, Washout |  | 2013 | Poor | Yes | 1 |  | 2013 | Normal | 4000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8569147554409602 | 29.919446004462962 | 1426.5 | 2dazszga | 1 | https://waterforpeople.s3.amazonaws.com/images/c70a7c94-dcf2-4973-a6e6-ad6741d0f783.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | a1b9fdb99b471130658e65ab3f477
tjc8-2p6w-2thq | 1 |  | J7 Rw26 | 1429330346 | 02-06-2017 09:36:41 CEST | Byukusenge Elie | 00:05:27 | 2017 | Rwanda | Rulindo | Cyinzuzi | Rudogo | Gasiza |  |  | Rwagitare | 0 |  | 45 | 40 | 5 | Yes | Piped Network -- Gravity Only |  | 2009 | No |  | Water For People |  | 1 | Spring | -1.7644810500752824 | 30.007563048175167 | 1783.6 | 2924rfor |  | Yes | 1.2 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2009 | Normal | 1.2 | Yes | 1 |  | 2009 | Normal | 1200 | Yes | 1 | -1.7744810500852932 | 30.017663038155167 | 1697.6 | 29io4wpc |  | 2009 | Normal | Yes | 2 | Pressure Break Tank¦Distribution Chamber |  | 2009 | Normal | Yes | 1 |  | 2009 | Normal | 900 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7698486920639631 | 30.021465096749424 | 1668 | 29azvs1i | 2 | https://waterforpeople.s3.amazonaws.com/images/ca006e93-7d6b-4fb7-bf21-f868bd151f01.jpg | 2009 | Normal | No |  |  |  | Yes |  | Normal |  | 61846f8c11f3092f5c3306e52e81d26
s6wc-wvwk-k5y3 | 1 |  | J7 Rw26 | 1212110062 | 11-03-2017 09:32:34 CET | Byukusenge Elie | 00:12:32 | 2017 | Rwanda | Rulindo | Rukozo | Mberuka | Gakubo |  |  | Nyamagana | 20456 |  | 1200 | 1200 | 0 | Yes | Piped Network -- Gravity Only |  | 2011 | Yes | all villages of Burehe and Rwili cells in Cyungo, Kinihira Village, Villages of Mberuka and Bwimo in Rukozo and Kabingo Village in Base Sector | Government and African Development Bank | This network serves four sectors Cyungo,Rukozo, Base,Base and Kinihira, It has some problems in distribution caused by the wrong design of tee junctions and inter connection with Sakara Pumping even where there is distribution, there is problem of types of pipeline thus This network needs partial rehabilitation as soon as possible because it serves many populations and so much public institutions | 2 | Spring | -1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 2 |  | 2015 | Normal | 2100 | Yes | 11 | -1.622603211034645 | 29.922165132428294 | 1913.1 | 22jhlc5x |  | 2011 | Normal | Yes | 15 | Pressure Break Tank¦Distribution Chamber |  | 2011 | Normal | Yes | 3 |  | 2011 | Poor | 37000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.624340328803786 | 29.94694551576973 | 1814.1 | 22md6rm5 | 29 | https://waterforpeople.s3.amazonaws.com/images/0ac33a37-f475-4732-95c6-4c00a9f939e9.jpg | 2011 | Poor | Yes | 10 | 22 | Bad tee connections and types of pipeline needs to be replaced | Yes |  | Poor | water tap in G.S.Rukozo does not work because there is not taps . | bde540cdd6b4efde054fa2a6a4328c8
mk3q-ypn7-juc3 | 1 |  | J7 Rw15 | 1243440873 | 22-03-2017 19:38:46 CET | Mukakarangwa Assoumpta | 00:10:11 | 2017 | Rwanda | Rulindo | Kinihira | Marembo | Cyogo |  |  | Nyamagana-Kinihira |  |  | 184 | 60 | 124 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦Ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6707118621722936 | 29.943623183849112 | 1897.3 | 24r1xros | 2 | https://waterforpeople.s3.amazonaws.com/images/0e2d8a52-a2b8-4dc0-8d7e-9214982cbaec.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | 9c43a433c7359131ff85e08d946f1eae
4jdm-fwh3-nhma | 1 |  | J7 Rw8 | 1204640238 | 07-03-2017 09:00:36 CET | Amani Desire | 01:35:07 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Gasama |  |  | Gasama | 911 |  | 19 | 19 | 0 | Yes | Piped Network -- Gravity Only |  | 1997 | No |  | Governement (District, WASAC) and Water For People | the network has been totaly rehabilated in 2016 | 2 | Spring | -1.740882760889992 | 29.933869978471744 | 1846.2 | 27z3ofgq | https://waterforpeople.s3.amazonaws.com/images/ff30da1d-3059-48ff-85ae-f821b3643a63.jpg | Yes | 30 | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/89652f15-94ec-47fd-a377-c281437eb748.jpg | start chamber and collection chamber | 2016 | Normal | 30 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/2cf544d6-92c7-4b2f-a5af-dfbdff4dfab1.jpg | 2016 | Normal | 700 | Yes | 1 | -1.7398552316859899 | 29.93657178593082 | 1752.3 | 27xecs6d | https://waterforpeople.s3.amazonaws.com/images/0a28203e-a2dc-4f71-b65e-f75ff5660bfe.jpg | 2016 | Normal | Yes | 2 | Washout chamber, and Air release chamber | https://waterforpeople.s3.amazonaws.com/images/0aff8333-a94f-4ce5-89a3-d18a2c10e87a.jpg | 2016 | Normal | Yes | 2 |  | 2016 | Normal | 800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7408730077933352 | 29.93385996068192 | 1821.3 | 27z32zuy | 5 | https://waterforpeople.s3.amazonaws.com/images/9b174d5b-ec23-4b65-9bcb-1eb877b49d94.jpg | 1997 | Normal | No |  |  |  | Yes |  | Normal | other water structures and pipelinehave been rehabilitated in 2016 except one one water point at the Source | c7f4e9294e0f49ce417b0c9c85f7c6
njpk-1h8u-wkbr | 1 |  | J7 Rw23 | 1246480128 | 23-03-2017 06:27:06 CET | Rugirangoga Augustin | 00:25:32 | 2017 | Rwanda | Rulindo | Buyoga | Gitumba | Munini |  |  | Kiruruma | 8295 |  | 158 | 152 | 6 | Yes | Piped Network with Pump |  | 2014 | Yes | rutabo shagasha cyasuli rugarama rusongati remera | Governement (District, WASAC) and Water For People | this network is ok .but there is a water tap bafore the last one on the branch towards sayo | 1 | Groundwater (well, etc.) | -1.668151432446623 | 30.04664574413683 | 1761.3 | 24mtitma |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 3 | Yes | 3 |  | 2014 | Normal | 9000 | Yes | 15 | -1.6684773741137722 | 29.8839135826884 | 1775.8 | 24ncknpz |  | 2014 | Normal | No | [5 empty] | Yes | 3 |  | 2014 | Normal | 9000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.693967061299327 | 30.05530641228774 | 1974.7 | 25ti6m15 | 2 | https://waterforpeople.s3.amazonaws.com/images/c84b747a-f67f-413d-9406-b3a615315bf2.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal |  | 8a788ad81fac9248d65cb5a5f916b
dk11-21ag-00ub | 1 |  | J7 Rw15 | 1435560071 | 02-06-2017 07:05:19 CEST | Mukakarangwa Assoumpta | 00:08:18 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyakambu |  |  | rwamugaza | 14106 |  | 186 | 30 | 156 | Yes | Piped Network -- Gravity Only |  | 2003 | Yes | all villages of ntarabana | Government | it does not function | 2 | Spring | 1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | 1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 | Sedimentation Tank¦Pressure Break Tank¦Distribution Chamber |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7910631220901614 | 30.125168760559195 | 1452.8 | 2aa39mir | 3 | https://waterforpeople.s3.amazonaws.com/images/3247ef26-2649-4f74-93c0-1fecc6e98f04.jpg | 2003 | Does Not Function | No |  |  |  | Yes |  | Poor |  | e9e0bdc4f5396ee7c54d45a896d72fa
p1cq-gtyx-fxbe | 1 |  | J7 Rw10 | 1229060273 | 03-01-2015 01:55:03 CET | Tuyisenge Vianney | 00:06:34 | 2017 | Rwanda | Rulindo | Tumba | Nyirabirori | Murambi |  |  | Murambi water point/Nyirambuga pumping | 30604 |  | 174 | 174 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point at Murambi operates well though one water tap was damaged nolonger fixed | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | Yes | 1 | -1.6899650130917385 | 29.928220830841383 | 2124.4 | 25mw172q | https://waterforpeople.s3.amazonaws.com/images/74d47cc0-cb53-4ade-afa8-85244193a183.jpg | 2015 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6899762266296021 | 29.928859934012863 | 2125.4 | 25mwmmoo | 2 | https://waterforpeople.s3.amazonaws.com/images/00869542-2592-4a99-9246-b8a4e10d74e6.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point at Murambi operates well though one water tap was damaged nolonger fixed | d997864b45c6a537c1514e2c6bf24ee
htw1-0850-f2c2 | 1 |  | J7 Rw8 | 1214341003 | 16-03-2017 08:51:38 CET | Amani Desire | 00:08:55 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  |  | 510 |  | 186 | 52 | 134 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi |  |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.735745737048247 | 29.933659639224132 | 1977.7 | 27qlnmiw | 28 | https://waterforpeople.s3.amazonaws.com/images/a460f356-c105-461f-a4d5-7b3eccf6caad.jpg | 2014 | Does Not Function | Yes | 8 | 30 | water doesnt reach the distribution Reservoir R50m3 located at kibamba village | No | water points served by R50m3 located at kibamba village do not have water | Does Not Function | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | f0dbeaf7a0d38eea55b8b7eb98401281
fw2q-253e-dmp9 | 1 |  | J7 Rw7 | 1235621081 | 24-03-2017 12:13:00 CET | Safari Bosco | 00:11:01 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge | [5 empty] | 214 | 214 | 0 | Yes | Piped Network with Pump |  | 1998 | Yes | gacyamo,nyakabungo | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8208314273506163 | 30.067171832500428 | 1702.7 | 2bnbp1z3 | 2 | https://waterforpeople.s3.amazonaws.com/images/178ed868-5873-4023-86a4-db95fc6e75b0.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | 9dcf4defbf871cde8e1d8390c2e0fb
qn09-e941-b3gk | 1 |  | J7 Rw15 | 1217800185 | 12-03-2017 12:30:04 CET | Mukakarangwa Assoumpta | 00:29:52 | 2017 | Rwanda | Rulindo | Rusiga | Taba | Bitare |  |  | Muvumu- Taba |  |  | 113 | 35 | 78 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.8242130164596562 | 29.931083430301516 | 1700.7 | 2bswxje6 | https://waterforpeople.s3.amazonaws.com/images/0146b50a-a9cd-4259-bf48-d91fd38ca792.jpg | Yes | 25 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/af140a73-cc3b-4e20-8a6f-032785116c10.jpg | "Springbox" --Intake Structure at a Spring | 2017 | Does Not Function | 25 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/e29c835c-f2fa-44c7-ae59-75eec85bb391.jpg | 2013 | Normal | 800 | Yes | 3 | -1.828985219687556 | 29.926634523104315 | 1627.1 | 2c0sxawy | https://waterforpeople.s3.amazonaws.com/images/9d6eb567-d02d-49bb-8d98-dcf787012dd5.jpg | 2013 | Poor | Yes | 9 | Pressure Break Tank¦Distribution Chamber¦Ventouse, Washout | https://waterforpeople.s3.amazonaws.com/images/d7e88e7d-6848-4719-843c-d630b3a8e3f8.jpg | 2013 | Normal | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/4b22dbe9-6284-46ff-804b-65ea793e05e5.jpg | 2013 | Normal | 7500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8265817974701204 | 29.928800085028595 | 1675.4 | 2bwu19qw | 1 | https://waterforpeople.s3.amazonaws.com/images/92c85970-59f6-450c-aae9-d9a2fd0322c7.jpg | 2013 | Does Not Function | No |  |  |  | Yes |  | Poor | -Muvumu- Taba network was rehabilitated in 2013, its intake chamber is under construction and it has 3 reservoirs in which one of them which is distribution reservoir has leakage; it has also 12 water points in which 1 does not function and there is other which is poor and also it has 9 other concrete structures which are normal. | ea7920d7bf755528c3a7ef5ff2309dbf
vu7q-y41u-8w3u | 1 |  | J7 Rw24 | 1248490227 | 28-03-2017 08:24:11 CEST | Kabalisa Manzi Christella | 00:05:51 | 2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Kayenzi |  |  | Rwamugaza network | 14106 |  | 200 | 200 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7763978990968226 | 30.088177182246284 | 1716.6 | 29ltupsh | 1 | https://waterforpeople.s3.amazonaws.com/images/c06f5b23-e945-4d3a-b4ac-22108cbd5738.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | 57833368247bad7d0f2fc19a2fcf36d
cf1h-rr33-cq3r | 1 |  | J7 Rw10 | 1317710214 | 20-04-2017 07:05:00 CEST | Tuyisenge Vianney | 00:05:51 | 2017 | Rwanda | Rulindo | Tumba | Misezero | Kavumu |  |  | Water point at Tumba Public RS/Nyirambuga pumping | 30604 |  | 139 | 139 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | in use | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 194.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.702454023086054 | 29.95767518663373 | 2108.5 | 267jnlvc | 5 | https://waterforpeople.s3.amazonaws.com/images/a1164178-7a51-4869-936d-82b8d8b3354a.jpg | 2012 | Poor | No |  |  |  | Yes |  | Poor | In use and served by Kajevuba center storage.But one among 6 tap stands damaged.The school last saw water in 2 months ago | e2c65623b0ceb7964110772c21f8765
e7w1-22mf-e071 | 1 |  | J7 Rw26 | 1220012179 | 21-03-2017 14:19:45 CET | Byukusenge Elie | 00:06:25 | 2017 | Rwanda | Rulindo | Rukozo | Buraro | Kamiyove |  |  | Kabonanyoni | 7894 |  | 70 | 65 | 5 | Yes | Piped Network with Pump |  | 2015 | Yes | Kibare,Mujebe, Musave, Nyarusebeya, Ruhanga, Buraro,Shyondwe,Kabyayi, Kabingo, Kamiyove, Murwa,Nyenyeri, Rukingu, Kivomo | Governement (District, WASAC) and Water For People | This is new pumping system which serves the community located at the uphill, it has 5 sources ,one which is located in Miyove sector ,Gicumbi district and this network covers 2 cells of Rukozo sector as Mbuye and Buraro , This network has one reservoir which is functioning ,It serves also two schools. | 5 | Spring | -1.603043907359012 | 29.95342630452421 | 2095.4 | 21n51h5a |  | Yes | 15 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 15 | Yes | 1 |  | 2015 | Normal | 720 | Yes | 19 | -1.634019702292831 | 29.958503791414177 | 2113.4 | 232cwxoh |  | 2015 | Normal | Yes | 10 | Pressure Break Tank¦Distribution Chamber¦null |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 19000 | Yes | 2 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.630697907212181 | 29.967562827927754 | 1834.7 | 22wv90wr | 31 | https://waterforpeople.s3.amazonaws.com/images/c1894d94-194a-4101-83ea-96db7e725350.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | The community doesn't use it as they prefer the protected spring located at Kaje Centre Near pumping station. | 98476d5c834cf17be4985a6f8772f26
6mea-gtb3-e2ch | 1 |  | J7 Rw24 | 1323040165 | 24-04-2017 21:52:15 CEST | Kabalisa Manzi Christella | 00:16:32 | 2017 | Rwanda | Rulindo | Kisaro | Kigarama | Runyinya |  |  | Gahama Kisaro network | 10234 |  | 148 | 148 | 0 | Yes | Piped Network -- Gravity Only |  | 2012 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6671501074688961 | 30.041830412153367 | 1945.4 | 24l5zh36 |  | Yes | 3 | Yes | 1 |  |  | 2012 | Normal | 3 | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 |  |  | 2012 | Normal | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6528872351397113 | 30.059358389408576 | 2069.6 | 23xkdwz5 | 1 | https://waterforpeople.s3.amazonaws.com/images/22999b9b-d88f-4aba-a43c-218b913525b9.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal |  | 6c5cbe998cf1c11933bb4c07b68188
ga43-n3nj-1c93 | 1 |  | J7 Rw10 | 1232070437 | 03-01-2015 01:46:32 CET | Tuyisenge Vianney | 00:04:57 | 2017 | Rwanda | Rulindo | Tumba | Barari | Rukore |  |  | Water point at Tumba Health Center/Nyirambuga pumping | 30604 |  | 157 | 157 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | Water point at Tumba health center operates well | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7023285100937453 | 29.94467422817009 | 2129 | 267bwywm | 4 | https://waterforpeople.s3.amazonaws.com/images/caaecc93-ae7c-4d52-891e-ad12f0b4dcbe.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | Water point at Tumba health center operates well | 1e95acf1b2bdf27dff125757f2820
2mmk-ggnq-qq4f | 1 |  | J7 Rw15 | 1207980204 | 08-03-2017 19:56:24 CET | Mukakarangwa Assoumpta | 00:06:58 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kigarama |  |  | kinywamagana pumping network | 6436 |  | 233 | 120 | 113 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8535700489605678 | 29.97116645542211 | 1939.8 | 2d5gy7sv | 1 | https://waterforpeople.s3.amazonaws.com/images/bf447495-9ed8-40e4-9108-2e887d54eef4.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | this water point function but is not well located | a9c1ab5d3efb557878b9198423d44355
5unu-bug3-jcbd | 1 |  | J7 Rw8 | 1214341033 | 16-03-2017 08:55:14 CET | Amani Desire | 00:36:14 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Kinini ya Mbogo |  |  | Musenge Network | 6074 |  | 100 | 100 | 0 | Yes | Piped Network with Pump |  | 2014 | Yes | gakoma,karehe,rutonde,gitaba,kiruli,buhira,ruhanya,kibamba,karindi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.95682830459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber¦washout and Air release |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7657323745557414 | 29.934628050236263 | 1853.3 | 29476lqq | 28 | https://waterforpeople.s3.amazonaws.com/images/bb0135b4-891c-4588-b4cc-243ce18f5344.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | 2d6567aab2ffcba37187babd4294f62
qm7m-r730-hhqa | 1 |  | J7 Rw19 | 1441560320 | 04-06-2017 15:52:52 CEST | Kayinamura Innocent | 00:16:15 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 6074 |  | 135 | 25 | 110 | Yes | Piped Network with Pump |  | 2014 | No |  | Water for People, WASAC and Rulindo District. |  | 1 | Spring | -1.768794219980039 | 29.93859037216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.556828330459043 | 2206.4 | 29s1pl5c |  | 2014 | Normal | Yes | 8 | Washout, Air release chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7773519216303453 | 29.947610478479717 | 2034.3 | 29nf0as4 | 28 | https://waterforpeople.s3.amazonaws.com/images/a85e1962-9819-48ae-a683-aab7d3c6d36f.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal |  | 38ad6c16c3082c9db86ececfe1f2029
k20g-k2yh-qxpb | 1 |  | J7 Rw19 | 1188291555 | 07-03-2017 12:00:26 CET | Kayinamura Innocent | 00:11:18 | 2017 | Rwanda | Rulindo | Mbogo | Mushali | Buraro |  |  | Matyazo network |  |  | 155 | 47 | 108 | Yes | Piped Network -- Gravity Only |  | 2016 | Yes | Buyanja, Buraro and Nyakabuye | Governement (District, WASAC) and Water For People |  | 3 | Spring | -1.7856001537024087 | 29.978428885393118 | 1894.3 | 2a126x3c |  | Yes | 17 | Yes | 4 |  | "Springbox" --Intake Structure at a Spring¦Collection chamber | 2016 | Normal | 17 | Yes | 1 |  | 2016 | Normal | 4300 | Yes | 1 | -1.7705709593776213 | 29.9686679108343068 | 1834.4 | 29c7cesm |  | 2016 | Normal | Yes | 2 | Air release chamber, Washout chamber |  | 2016 | Normal | Yes | 1 |  | 2016 | Normal | 1800 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.770442346130886 | 29.96722122973003 | 1845.5 | 29bzlrx4 | 4 | https://waterforpeople.s3.amazonaws.com/images/29d7b08a-5d34-467e-82de-9573640a4c52.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal |  | b3d0757e6b65e8e17281ddaea3b65840
a85h-dv47-4smg | 1 |  | J7 Rw10 | 1307450111 | 16-04-2017 22:11:59 CEST | Tuyisenge Vianney | 00:05:51 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Cyili |  |  | Water point at GS Mugenda/ Nyirambuga pumping system | 30604 |  | 165 | 165 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | The water point at school of GS Mugenda operates well | 2 | Spring | -1.7265024345182751 | 29.986089955799534 | 1943.2 | 27bbj3ys |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6757015617572832 | 29.906674022025147 | 2107.4 | 24zb129m | 2 | https://waterforpeople.s3.amazonaws.com/images/1b294a58-0286-4503-b270-2ea1116e7f86.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | The water point at school of GS Mugenda operates well | 2bbc891bfd2016b4ef6593ed184ce7
gyw1-qpr3-cxvj | 1 |  | J7 Rw8 | 1217460128 | 10-03-2017 10:19:28 CET | Amani Desire | 00:53:36 | 2017 | Rwanda | Rulindo | Ngoma | Kabuga | Nyabuko |  |  | Kabarore-Ngoma-Nyabuko network | 8284 |  | 122 | 32 | 90 | Yes | Piped Network with Pump |  | 2014 | Yes | nyabuko,kagwa,kiruli,bisizi,ngaru,kirungu,kiboha,kigina | Governement (District, WASAC) and Water For People |  | 4 | Spring | -1.8123357076877171 | 29.96790053996264 | 1783.9 | 2b99ml0f |  | Yes | 4 | Yes | 5 |  | "Springbox" --Intake Structure at a Spring¦collection chamber | 2014 | Poor | 4 | Yes | 2 |  | 2014 | Normal | 8000 | Yes | 13 | -1.808716485895084 | 29.973362007273437 |  | 2b3a3o2d |  | 2014 | Normal | No | [5 empty] | Yes | 2 |  | 2014 | Normal | 7000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8238029756527472 | 29.976158874775003 | 1871.7 | 2bs8irxt | 17 | https://waterforpeople.s3.amazonaws.com/images/c3cff69d-bd09-4823-b575-3c57c4a07f03.jpg | 2014 | Normal | No |  |  |  | No | water has been closed by the the network management due to the unwillingness of the people to pay water | Does Not Function | -The network has 17 water points -water points are in good operational conditions except the water point at the source -4 water points don't have water today -the pipes are in good conditions -The pump is not working properly as it was expected during Design, Today the pump is pumping less than the quantity of water needed or expected during Design due to the lack of sufficient energy -The transformer at the pumping station does'nt offer the required energy for the pump -The anti hammers of pump are not functioning because of bad installation of pumping house -The system has two pumps with four units with two units pumping in one direction towards Nyabuko and other two in an other direction towards ngoma sector office -The suction tank is in bad physical conditions | d24e2573ca586afa55062bbca791b77
5xwv-u7um-j6b8 | 1 |  | J7 Rw19 | 1433501142 | 04-06-2017 15:53:01 CEST | Kayinamura Innocent | 00:14:38 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Karehe |  |  | Musenge network | 6074 |  | 135 | 28 | 107 | Yes | Piped Network with Pump |  | 2014 | No |  | Water for People, WASAC and Rulindo District |  | 1 | Spring | -1.768794219980039 | 29.93859037216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.556828330459043 | 2206.4 | 29s1pl5c |  | 2014 | Normal | Yes | 8 | Washout, Air release chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.769906573774297 | 29.95317602701175 | 2177.2 | 29b3gd57 | 28 | https://waterforpeople.s3.amazonaws.com/images/638aac54-7ab7-47f8-9b55-6daa24890c86.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal |  | 42b5e4dbb428b2ddca27cc01eba1c
xwxy-r68x-3fp | 1 |  | J7 Rw7 | 1240120328 | 24-03-2017 11:18:54 CET | Safari Bosco | 00:38:02 | 2017 | Rwanda | Rulindo | Masoro | Kigarama | Marenge |  |  | marenge | 5544 |  | 203 | 203 | 0 | Yes | Piped Network -- Gravity Only |  | 1998 | Yes | kigarama,gacyamo,marembo | Governement (District, WASAC) and Water For People | Water points is functioning well | 2 | Spring | -1.8285370486353667 | 30.063460790805994 | 32.8 | 2c024tqy |  | Yes | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 20 | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 15 | -1.8228934876860623 | 30.055223158145252 | 1892.4 | 2bqqcci0 |  | 2016 | Normal | No | [5 empty] | Yes | 2 |  | 2016 | Normal | 5000 | Yes | 1 |  | 2016 | Normal | Yes |  | 2016 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8269951820959995 | 30.060983932999704 | 1750.9 | 2bxig2kh | 1 | https://waterforpeople.s3.amazonaws.com/images/b3e7620c-99df-4124-898e-a344dbd0b509.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | 29ddc5929233e5e1fab2f23496c8df
wp42-g8pn-kaxv | 1 |  | J7 Rw10 | 1307930075 | 18-04-2017 06:59:40 CEST | Tuyisenge Vianney | 00:08:43 | 2017 | Rwanda | Rulindo | Tumba | Gahabwa | Munyinya |  |  | Munyinya water point chez Rugigana/Nyirambuga pumping system | 30604 |  | 142 | 142 | 0 | Yes | Piped Network with Pump |  | 2017 | Yes | Munyinya and Kabuga | Governement (District, WASAC) and Water For People | The water point has been recently completed however no water available till now | 2 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 5 | No | [5 empty] | 5 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/321b75ac-6333-4bbb-915a-7a0bb2b96722.jpg | 2017 | Normal | 500 | Yes | 1 | -1.7222449960136712 | 29.94278207868217 | 1997.2 | 2749wfxf | https://waterforpeople.s3.amazonaws.com/images/0ba9355e-31a4-40f1-9859-b03cc52fb056.jpg | 2017 | Normal | No | [5 empty] | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/ecc742b2-38d2-4db4-98e6-8e10a4eabea8.jpg | 2017 | Normal | 500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7218745717428703 | 29.941033723572243 | 1997.3 | 273nvej6 | 2 | https://waterforpeople.s3.amazonaws.com/images/345d3e50-dfb1-49d1-89fe-e509d1702198.jpg | 2017 | Does Not Function | No |  |  |  | No | The water point has been recently completed however no water available till now | Does Not Function | The water point has been recently completed however no water available till now | 75553ca8caf46934b4f13a3252ecf
9h6y-98vg-dbvu | 1 |  | J7 Rw24 | 1220310093 | 15-03-2017 16:39:16 CET | Kabalisa Manzi Christella | 00:11:44 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Kigarama |  |  | Rwamugaza | 14106 |  | 380 | 0 | 380 | Yes | Piped Network with Pump |  | 2009 | No |  | Governement (District, WASAC) and Water For People | Water doesn’t reach Water point | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 3000 | Yes | 3 | -1.7555179528295524 | 30.03970289656239 | 1690.5 | 28napmb1 |  | 2014 | Does Not Function | Yes | 8 |  |  | 2014 | Does Not Function | Yes | 2 |  | 2014 | Does Not Function | 3000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7542936515083631 | 30.052846661512557 | 1732 | 28la2qls | 1 | https://waterforpeople.s3.amazonaws.com/images/2deee902-bb71-45b6-8f43-d13181d891cb.jpg | 2014 | Does Not Function | Yes | 365 | 0 | System is not Functional | No | Water doesn’t reach Water Tap | Does Not Function | System is not Functional | 1544648667793e2ae81ca1626e6ba090
8dwv-wvrv-dyj9 | 1 |  | J7 Rw15 | 1230740469 | 22-03-2017 19:28:32 CET | Mukakarangwa Assoumpta | 00:08:27 | 2017 | Rwanda | Rulindo | Kinihira | Butunzi | Ndorandi |  |  | Nyamagana-Kinihira |  |  | 139 | 50 | 89 | Yes | Piped Network with Pump |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862039 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦Ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.666963729625348 | 29.94817339500289 | 1854.4 | 24kuo7vd | 2 | https://waterforpeople.s3.amazonaws.com/images/f219c118-06c4-48da-b9f2-a7ec72016efa.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | c7e55fd39ccc6edcdb89505d4aaf2e63
n2n6-3kev-wks2 | 1 |  | J7 Rw24 | 1223120109 | 15-03-2017 15:55:42 CET | Kabalisa Manzi Christella | 00:12:28 | 2017 | Rwanda | Rulindo | Cyinzuzi | Budakiranya | Kamatongo |  |  | 0 | 6572 |  | 1125 | 0 | 1125 | Yes | Piped Network with Pump |  | 2014 | No |  | Governement (District, WASAC) and Water For People | Water doesn’t reach Water point | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 3000 | Yes | 3 | -1.7555179528295524 | 30.03970289656239 | 1690.5 | 28napmb1 |  | 2014 | Does Not Function | Yes | 8 |  |  | 2014 | Does Not Function | Yes | 2 |  | 2014 | Does Not Function | 3000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.766556293102319 | 30.053921627067886 | 1592.3 | 295k069n | 1 | https://waterforpeople.s3.amazonaws.com/images/72101fe8-c33b-4afe-9c90-51ad9e4dacca.jpg | 2014 | Does Not Function | Yes | 365 | 0 | Water is not Flowing | No | Water doesn’t reach Water Tap | Does Not Function | Water is not Flowing | 9c30898e681e835a5c17d939cebfdbd2
ynbe-n4df-k9gj | 1 |  | J7 Rw19 | 1202952126 | 17-03-2017 05:22:22 CET | Kayinamura Innocent | 00:15:29 | 2017 | Rwanda | Rulindo | Mbogo | Rurenge | Gakoma |  |  | Musenge network | 6074 |  | 146 | 48 | 98 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma, Karehe, Rutonde, Gitaba, Kiruri, Buhera, Ruhanya, Kibamba and Karindi | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.768794219980039 | 29.9390370216456 | 1824.3 | 2999d8vy |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Washout and Air release chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 1 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7814180625687344 | 29.954886485232105 | 2189.3 | 29u4qafw | 28 | https://waterforpeople.s3.amazonaws.com/images/947a73f3-758c-48c3-a910-742f248fdf0c.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal | 1. The system has two Pumps but one is damaged and is not working, only one pump is used to pump water 2. Eleven (11) water points served by the distribution reservoir R 50m3 located at Kibamba village do not have water today because water don't reach this reservoir, there is not water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed 2016 5. one water point doesn't Function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | 83203c566c7b98d3339138eb734dfc4d
yd93-ggpd-daqw | 1 |  | J7 Rw15 | 1236320473 | 23-03-2017 06:54:01 CET | Mukakarangwa Assoumpta | 00:06:26 | 2017 | Rwanda | Rulindo | Kinihira | Marembo | Kigali |  |  | Nyamagana- Kinihira |  |  | 189 | 60 | 129 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | All Villages of Butunzi and Marembo cells and Karambi village | Governement (District, WASAC) and Water For People |  | 2 | Spring | 1.5920318970720486 | 29.924068733978803 | 1948.8 | 214xj7vs |  | Yes | 5 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 5 | Yes | 1 |  | 2015 | Normal | 1000 | Yes | 7 | 1.67118131808347 | 29.96232014862839 | 1985.8 | 24rtx59j |  | 2015 | Normal | Yes | 8 | Distribution Chamber¦Ventouse, Washout |  | 2015 | Normal | Yes | 3 |  | 2015 | Normal | 6000 | Yes | 2 |  | 2015 | Normal | Yes |  | 2015 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.662701074576537 | 29.9252994907846 | 1934.1 | 24dt1jzo | 2 | https://waterforpeople.s3.amazonaws.com/images/91979430-e419-4850-aa4b-c1c466dc51e6.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal |  | 663dc9e19ea509cc56bc3c6770af97
a6b6-0rab-4ehw | 1 |  | J7 Rw10 | 1220470672 | 13-03-2017 21:52:37 CET | Tuyisenge Vianney | 00:07:50 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Ngarama |  |  | Ngarama water point/Nkore gravity system |  |  | 110 | 110 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Private group of people that have joined hands to get clean water | Water point operates well though it is not protected | 1 | Spring | -1.6883400866741962 | 29.91133431277988 | 1897.9 | 25k7kyy1 |  | Yes | 40 | No | [5 empty] | 40 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6868579809966338 | 29.90630028853853 | 1812.3 | 25hqvdrr | 1 | https://waterforpeople.s3.amazonaws.com/images/8360cee7-2bc6-48f6-8d4b-aa3a6b3e9ff0.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | The water point operates well | 4122c38ad1910e0a57266a1323dc3d6
1qgg-h0w1-exrf | 1 |  | J7 Rw24 | 1220310090 | 15-03-2017 16:28:30 CET | Kabalisa Manzi Christella | 00:10:11 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Runyinya |  |  | Rwamugaza | 14106 |  | 390 | 0 | 390 | Yes | Piped Network with Pump |  | 2014 | No |  | Governement (District, WASAC) and Water For People | Water doesn’t reach Water point | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 3000 | Yes | 3 | -1.7555179528295524 | 30.03970289656239 | 1690.5 | 28napmb1 |  | 2014 | Does Not Function | Yes | 8 |  |  | 2014 | Does Not Function | Yes | 2 |  | 2014 | Does Not Function | 3000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7510922423033868 | 30.046594357193595 | 1674.7 | 28fzk0z5 | 1 | https://waterforpeople.s3.amazonaws.com/images/ab8c80e2-3d1a-4a9b-a4f0-c0695361ade9.jpg | 2014 | Does Not Function | Yes | 365 | 0 | Water is not Flowing | No | Water doesn’t reach Water Tap | Does Not Function | System is not Functional | e63356559ccf2c7ea609f4b41f1566b
91cf-nrhk-5djm | 1 |  | J7 Rw10 | 1235970101 | 03-01-2015 00:10:48 CET | Tuyisenge Vianney | 00:07:10 | 2017 | Rwanda | Rulindo | Tumba | Taba | Mwili |  |  | Mwili water point/Nyirambuga pumping | 30604 |  | 141 | 141 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point at Mwili gets water on regular basis.However,one water tap valve was damaged | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7301479616062956 | 29.97023382981916 | 2053.9 | 27hc8w1i | 2 | https://waterforpeople.s3.amazonaws.com/images/be4aca66-8da8-48d4-bd3a-2546c58bd17c.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point at Mwili gets water on regular basis.However,one water tap valve was damaged | a48f99a9b7bc66185d5de547aa5e34c5
rxym-hmd0-eb3h | 1 |  | J7 Rw15 | 1199340994 | 09-03-2017 04:57:18 CET | Mukakarangwa Assoumpta | 00:05:39 | 2017 | Rwanda | Rulindo | Shyorongi | Kijabagwe | Kabagabaga |  |  | kirikumuryango network |  |  | 181 | 106 | 75 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.976612576966872 | 1632.8 | 2e2ec99y |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8913947136249902 | 29.957278381566027 | 1378.6 | 2ew0nlkk | 1 | https://waterforpeople.s3.amazonaws.com/images/1be947ff-fced-4a90-b408-307b7a0fe9c6.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 10f73d56ecdbdee4a69a6e24ea583d
5x7e-hn08-hwd7 | 1 |  | J7 Rw23 | 1212281482 | 15-03-2017 05:48:50 CET | Rugirangoga Augustin | 00:28:40 | 2017 | Rwanda | Rulindo | Base | Rwamahwa | Base |  |  | Rutare II | 1458 |  | 229 | 200 | 29 | Yes | Piped Network -- Gravity Only |  | 2014 | No |  | Governement (District, WASAC) and Water For People | this network is working in normal conditions | 2 | Groundwater (well, etc.) | -1.647515621777326 | 29.88420972245651 | 1745 | 23ooo3ru | https://waterforpeople.s3.amazonaws.com/images/42a09046-b9e7-4aa9-8bec-10f4bb154e22.jpg | No | 75 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/2f16e6b6-24bd-4999-aed1-604521ef8bd7.jpg | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 75 | Yes | 1 |  | 2016 | Poor | 4280 | Yes | 1 | -1.6503465715220755 | 29.883009582768896 | 1737.7 | 23td5rym |  | 2012 | Normal | Yes | 1 | Pressure Break Tank |  | 2016 | Normal | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6476543639226169 | 29.884238134322523 | 1727.3 | 23ox068q | 2 | https://waterforpeople.s3.amazonaws.com/images/d9cfe96b-774f-4016-a4fa-d611949cd1b8.jpg | 2016 | Normal | No |  |  |  | No | because some pipes have been deteriorated by constructing the road Base-Gicumbi | Poor | the network has been destroyed by the road construction project | c3bf17bdcadc81a4b53db8b27dfdda9
hjk1-n9rw-6xef | 1 |  | J7 Rw24 | 1222570919 | 15-03-2017 14:37:39 CET | Kabalisa Manzi Christella | 00:18:06 | 2017 | Rwanda | Rulindo | Cyinzuzi | Migendezo | Remera |  |  | 0 | 14106 |  | 975 | 975 | 0 | Yes | Piped Network with Pump |  | 2009 | No |  | umushinga witwa Ema | No Problem with the Water Point | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 16 | -1.7543004341479447 | 29.99197561543003 | 2178 | 28lao5qn | https://waterforpeople.s3.amazonaws.com/images/7e48f570-6fcf-466e-803c-16ea97e8361a.jpg | 2009 | Normal | Yes | 23 |  | https://waterforpeople.s3.amazonaws.com/images/700115d3-bd86-40ca-9d78-2f41c017a5fe.jpg | 2009 | Normal | Yes | 2 |  | 2009 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7539535088819878 | 29.99223603685037 | 2174.7 | 28kptzki | 1 | https://waterforpeople.s3.amazonaws.com/images/74cc78d5-7b04-47cc-8536-80ded11e3c04.jpg | 2009 | Normal | No |  |  |  | No | Water seller was not around | Normal | This Water Point/system functions well | 66e6432ef3d3dea84d8d6c5b22f98371
7hkr-sxj3-s80q | 1 |  | J7 Rw7 | 1449380286 | 04-06-2017 13:34:36 CEST | Rugirangoga Augustin | 00:17:29 | 2017 | Rwanda | Rulindo | Kisaro | Mubuga | Nyakarekare |  |  | gahama | 10234 |  | 150 | 100 | 50 | Yes | Piped Network with Pump |  | 2012 | Yes | ruberano gatete mugomero gishinge nyakarekare kibingwe | waterforpeople |  | 2 | Spring | -1.6675834297799398 | 30.0428712210569 | 1965.7 | 24lvl43w |  | Yes | 65 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2012 | Normal | 65 | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 | Pressure Break Tank¦Distribution Chamber¦washout,air release |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6502656962943962 | 30.032110208945273 | 2158.7 | 23t8ec9t | 1 | https://waterforpeople.s3.amazonaws.com/images/59332cb3-f0f9-40b8-bb66-a7a809f9f0f2.jpg | 2012 | Poor | No |  |  |  | Yes |  | Normal | ntakibazo gihari kuri iri vomo | bde239e2b552193bdcaecb39abe962d
mj5q-8yxy-u57d | 1 |  | J7 Rw15 | 1430300081 | 02-06-2017 06:41:45 CEST | Mukakarangwa Assoumpta | 00:17:40 | 2017 | Rwanda | Rulindo | Ntarabana | Kajevuba | Nyarubuye |  |  | Rwamugaza | 14106 |  | 229 | 229 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | Yes | All Villages of ntarabana sector | Government |  | 2 | Spring | 1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | 1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 | Pressure Break Tank |  | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8103637266646508 | 30.11322906407901 | 1614.4 | 2b60c7yk | 3 | https://waterforpeople.s3.amazonaws.com/images/96f9896c-9f64-4a61-b183-b3585c24abfb.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | e678b611d0c75271fde9b067ff459c30
vyx9-3nqb-tskk | 1 |  | J7 Rw10 | 1278780089 | 05-04-2017 21:43:50 CEST | Tuyisenge Vianney | 00:04:14 | 2017 | Rwanda | Rulindo | Bushoki | N.Ngarama | Byimana |  |  | Nyabishengeshi gravity system | 893 |  | 92 | 92 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | Yes | Byimana and Tare villages | Governement (District, WASAC) and Water For People | Operational.It is shared by Byimana and Tare villages | 1 | Spring | -1.6778517470929726 | 29.880934967401814 | 2032.3 | 252v194p |  | Yes | 50 | No | [5 empty] | 50 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6732489137061515 | 29.889175497822027 | 1949.5 | 24v8kfbf | 1 | https://waterforpeople.s3.amazonaws.com/images/c51b1ad4-709d-4b6e-84d5-70d8c1b36211.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | Operational.It is shared by Byimana and Tare villages | b32d49bccfd64ea2c46f1d351804ced
shdd-xqjm-mpkk | 1 |  | J7 Rw10 | 1215191857 | 14-03-2017 22:51:31 CET | Tuyisenge Vianney | 00:06:28 | 2017 | Rwanda | Rulindo | Rusiga | Taba | Kingazi |  |  | Water point1 at Kingazi/Nyakabizi2 gravity | 1259 |  | 157 | 157 | 0 | Yes | Piped Network -- Gravity Only |  | 2015 | No |  | GoR | The water point operates though people claim to be the low flow with poor service delivery | 2 | Spring | -1.803447729664134 | 29.930708856826865 | 1927. | 2aukc7xn |  | Yes | 20 | No | [5 empty] | 20 | No | [5 empty] | Yes | 1 | -1.8059758230512923 | 29.92508178082003 | 1863.1 | 2ayqyvxu | https://waterforpeople.s3.amazonaws.com/images/b0c0067a-3c48-4c66-bfcd-3262c670ad79.jpg | 2013 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8058629491639202 | 29.92507842989676 | 1876 | 2aykf4aa | 1 | https://waterforpeople.s3.amazonaws.com/images/ffa19c38-bc1a-4b29-a273-ed96d51327dd.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | Water point1 at Kingazi/Nyakabizi2 gravity operates well though people suggest the water flow should augmented to meet their demand | f0d43d22484e2699cebd2253e7d2a42c
ysuu-5hsh-471a | 1 |  | J7 Rw24 | 1323040181 | 24-04-2017 23:27:56 CEST | Kabalisa Manzi Christella | 00:07:24 | 2017 | Rwanda | Rulindo | Burega | Butangampundu | Mayaga |  |  | Rwamugaza network | 14106 |  | 105 | 105 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Governement (District, WASAC) and Water For People |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7374173333138418 | 30.006563288387298 | 1723.9 | 27td3141 |  | 2003 | Normal | Yes | 14 |  |  | 2003 | Normal | Yes | 1 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.745036970857442 | 30.063739335104547 | 1644.8 | 285yrcil | 1 | https://waterforpeople.s3.amazonaws.com/images/6e8612d3-c693-4b7e-9c4c-b4f33d79f4d0.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal |  | 469b27e4b3e6ae71186686f1b9fb4a91
5j6w-qe2c-ph5t | 1 |  | J7 Rw23 | 1213310127 | 12-03-2017 18:40:26 CET | Rugirangoga Augustin | 00:15:36 | 2017 | Rwanda | Rulindo | Base | Gitare | Gatete |  |  | Rwicanyoni | 698 |  | 141 | 135 | 6 | Yes | Piped Network -- Gravity Only |  | 2017 | Yes | kirwa gatete gisiza | Governement (District, WASAC) and Water For People | this network is new and works well | 2 | Spring | -1.6644377224987001 | 29.903649586570488 | 1928 | 24go1jh8 |  | Yes | 10 | Yes | 2 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 10 | Yes | 1 |  | 2016 | Normal | 8600 | Yes | 3 | -1.6605194594779042 | 29.90927074216649 | 1808.8 | 24a6nmdw |  | 2016 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6546727022471075 | 29.90623618594417 | 1739.7 | 240iyh2u | 2 | https://waterforpeople.s3.amazonaws.com/images/d88ac86a-3ec9-4871-8b94-2306eb2f2eb2.jpg | 2016 | Normal | No |  |  |  | Yes |  | Normal | This Water Point/system functions well | 9832d3c9beeedbc6efa92736a6e1d1a
7h4b-52uq-c3xv | 1 |  | J7 Rw24 | 1223090352 | 16-03-2017 07:05:18 CET | Kabalisa Manzi Christella | 00:06:06 | 2017 | Rwanda | Rulindo | Burega | Karengeli | Kiziba |  |  | Rwamugaza | 14106 |  | 400 | 400 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | no problem | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7311081278105218 | 30.03911118655297 | 1948.4 | 27ixeinb | 1 | https://waterforpeople.s3.amazonaws.com/images/63b526b5-ff57-4056-8124-8b731dd8361d.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | no problem | d6fb3c489bb395233e424d4c179719b9
1qge-d801-fdd3 | 1 |  | J7 Rw24 | 1253000101 | 28-03-2017 08:27:30 CEST | Kabalisa Manzi Christella | 00:05:28 | 2017 | Rwanda | Rulindo | Ntarabana | Mahaza | Kayenzi |  |  | Rwamugaza network | 14106 |  | 200 | 200 | 0 | Yes | Piped Network -- Gravity Only |  | 2003 | No |  | Government |  | 2 | Spring | -1.7435819221234254 | 29.988391795139503 | 1882.4 | 283kfh7v |  | Yes | 3 | Yes | 1 |  |  | 2003 | Normal | 3 | Yes | 2 |  | 2003 | Normal | 35000 | Yes | 7 | -1.7647695580900606 | 30.037117893424683 | 1758 | 292lfkur |  | 2003 | Normal | Yes | 12 |  | https://waterforpeople.s3.amazonaws.com/images/ecd53d7e-45ed-4271-9d42-712aa253ea42.jpg | 2003 | Normal | Yes | 2 |  | 2003 | Normal | 35000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7799309825472867 | 30.091686270983043 | 1679.5 | 29rom5ys | 1 | https://waterforpeople.s3.amazonaws.com/images/f6370a33-4f1e-4a23-ab7d-0f871f1d2515.jpg | 2003 | Normal | No |  |  |  | Yes |  | Normal |  | 3b31a9aede1e95eafb7f621c984a511
1mwg-k5u8-0nr6 | 1 |  | J7 Rw23 | 1250400055 | 25-03-2017 20:47:34 CET | Rugirangoga Augustin | 00:23:27 | 2017 | Rwanda | Rulindo | Buyoga | Butare | Gasave |  |  | KIDUHA | 0 |  | 114 | 100 | 14 | Yes | Piped Network -- Gravity Only |  | 2007 | Yes | kankanga giko gasave | italians (LAKE ANGELS) Expanded by Water For People | The system needs rehabilitation | 1 | Groundwater (well, etc.) | -1.692136727874054 | 30.02146392212493 | 1866.9 | 25qh8a2e |  | No | 20 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Poor | 20 | Yes | 1 |  | 2007 | Poor | 2200 | Yes | 3 | -1.6932117321635163 | 30.026191374639453 | 1765.8 | 25s9j3fp |  | 2007 | Poor | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6971823274671667 | 30.030833008876503 | 1654.5 | 25ytw6ms | 1 | https://waterforpeople.s3.amazonaws.com/images/ac6a2c8a-380b-498f-af37-1851429f74f9.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal |  | 12a19318eb5e3911e2d1ea154584efd
gncd-r26e-m6af | 1 |  | J7 Rw23 | 1241620263 | 23-03-2017 17:26:27 CET | Rugirangoga Augustin | 01:03:00 | 2017 | Rwanda | Rulindo | Buyoga | Ndarage | Gahondo |  |  | Ndarage |  |  | 105 | 100 | 5 | Yes | Piped Network -- Gravity Only |  | 2014 | Yes | karambi gahondo Bunyana Rugarama Gasave | Governement (District, WASAC) and Water For People | the one source of the two sources which are captured. one is inhibited by the roots of trees because the source is near a forest | 2 | Spring | -1.6829614865475908 | 30.031434012077444 | 1962.1 | 25bb9sey | https://waterforpeople.s3.amazonaws.com/images/a5fe2435-456e-479b-bd4f-09f20d594015.jpg | Yes | 30 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 30 | Yes | 1 |  | 2014 | Normal | 6700 | Yes | 5 | -1.6902852583901373 | 30.03414816539013 | 1811.8 | 25nf3391 |  | 2014 | Normal | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.682922544637571 | 30.0314384273157 | 2006.4 | 25b8w1zu | 1 | https://waterforpeople.s3.amazonaws.com/images/942f075e-dda0-4fc8-ae1b-54999abbc8bf.jpg | 2014 | Normal | No |  |  |  | Yes |  | Normal |  | 78c35d9c875f9169cddfe7e9f1be50d2
a5n4-dmrx-khyj | 1 |  | J7 Rw8 | 1227520136 | 16-03-2017 08:52:24 CET | Amani Desire | 00:10:17 | 2017 | Rwanda | Rulindo | Mbogo | Bukoro | Bukoro |  |  | Musenge Network | 6074 |  | 186 | 22 | 164 | Yes | Piped Network with Pump |  | 2014 | Yes | Gakoma,karehe,rutonde,gitaba,kiruri, buhira,Ruhanya,kibamba,karindi |  |  | 1 | Spring | -1.768794219980039 | 29.938590370216456 | 1824.3 | 2999d8vt |  | Yes | 4.44 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2014 | Normal | 4.44 | Yes | 1 |  | 2014 | Normal | 3000 | Yes | 16 | -1.7801508996458808 | 29.956828330459043 | 2206.4 | 29s1po8g |  | 2014 | Normal | Yes | 8 | Distribution Chamber |  | 2014 | Poor | Yes | 3 |  | 2014 | Poor | 20000 | Yes | 2 |  | 2014 | Poor | Yes |  | 2014 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.733184310074633 | 29.930207195827318 | 1965.4 | 27md8nmu | 28 | https://waterforpeople.s3.amazonaws.com/images/24f0cf4b-f5e3-4f59-9772-fcea09530317.jpg | 2014 | Does Not Function | Yes | 8 | 30 | all water served by R50m3 located at kibamba village | No | all water served by R50m3 located at kibamba village do not have water today from last july 2016 | Does Not Function | 1.The system has two pumps but one is damaged and is not working ,Only one pump is used to pump water 2.Eleven(11) water points served by the distribution Reservoir R50m3 located at kibamba village do not have water today because water dont reach this reservoir,there is no water at those water points from last August 2016 3. 2 water points located at Raro centre have been damaged and destroyed 4. there is an extension to Gitaba village is constructed in 2016 5.one water point doesn't function because of the pipe break due to high pressure 6. the interconnection to Ngoma network is under construction with one water point and reservoir being under construction | 609181509fe7f6c618c3cbd11b9c452
7wvv-qf8q-h9dy | 1 |  | J7 Rw26 | 1183541176 | 07-03-2017 12:43:55 CET | Byukusenge Elie | 00:12:38 | 2017 | Rwanda | Rulindo | Cyungo | Marembo | Murambo |  |  | Mugomero Murambo | 3456 |  | 161 | 150 | 11 | Yes | Piped Network -- Gravity Only |  | 2015 | Yes | Gahinga, Nganzo, Rusayu, Buyaga and Murambo | Governement (District, WASAC) and Water For People | The sourve5of this network is located in Burera District and this network serves three villages in Burera and starting chamber with reservoirs | 1 | Spring | -1.5777496463341437 | 29.93714072556937 | 2147.8 | 20haqsiz |  | Yes | 120 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2015 | Normal | 120 | Yes | 2 |  | 2015 | Normal | 10000 | Yes | 10 | -1.5961706844323926 | 29.91257085345822 | 2085.4 | 21bs0o8l |  | 2015 | Normal | Yes | 3 | Distribution Chamber |  | 2015 | Normal | Yes | 2 |  | 2015 | Normal | 10000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6203858137614442 | 29.909397141877722 | 2029.2 | 22ftf3rp | 1 | https://waterforpeople.s3.amazonaws.com/images/f76d41d2-bc27-4171-bf73-833f22662404.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | This water tap is used by Marembo Health Center | f3f9e051b49982138b4e837113dc68a9
9x55-p8q6-nttr | 1 |  | J7 Rw19 | 1195371258 | 07-03-2017 16:07:56 CET | Kayinamura Innocent | 00:16:36 | 2017 | Rwanda | Rulindo | Mbogo | Mushali | Buraro |  |  | Kishwi network | 1309 |  | 155 | 53 | 102 | Yes | Piped Network -- Gravity Only |  | 2003 | Yes | Buraro and Ruhondo | Goverment | One Part of the system was Rehabilitated By the Government (District, WASAC) and Water For People | 1 | Spring | -1.7714946380440713 | 29.963728274178695 | 1845.6 | 29dq4aet |  | Yes | 25 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2016 | Normal | 25 | Yes | 2 |  | 2016 | Normal | 700 | Yes | 2 | -1.771494630440713 | 29.963728274178695 | 1845.6 | 29dq4aet |  | 2003 | Normal | No | [5 empty] | Yes | 2 |  | 2003 | Normal | 680 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7684090276018936 | 29.96678276367607 | 1813.1 | 298m5cib | 4 | https://waterforpeople.s3.amazonaws.com/images/f2f9f3e7-a027-43c1-8a10-05db2a6172ba.jpg | 2003 | Poor | No |  |  |  | Yes |  | Normal | Source gets dirty in the rainy season, part of the system was destroyed, one water point is not functional | 93d66cc759f3d403adca4b3e976e37e
2eka-ggsc-vu5d | 1 |  | J7 Rw10 | 1241440079 | 02-01-2015 12:38:00 CET | Tuyisenge Vianney | 00:07:32 | 2017 | Rwanda | Rulindo | Buyoga | Mwumba | Mataba |  |  | Water at Buyoga Market/Nyirambuga pumping | 30604 |  | 177 | 177 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  |  | Water point at Buyoga Market.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water. Note that[3uqw-xjv9-sk90 ] is water point for Buyoga sector not Buyoga market | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.690649510677137 | 30.01349378924872 | 2083.8 | 25o0iova | 2 | https://waterforpeople.s3.amazonaws.com/images/3d8057e6-aa1f-4105-a083-55a31e5be525.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Operational normally.Water point at Buyoga Market.It operates well though it faces the same problem exerted on Nyirambuga pumping system on Buyoga side of rarely availing water. Note that[3uqw-xjv9-sk90 ] is water point for Buyoga sector not Buyoga market | b2dc11fd66baa5bc8ad9beecf2277c0
ekx1-86ya-fsnc | 1 |  | J7 Rw24 | 1330410421 | 24-04-2017 21:52:48 CEST | Kabalisa Manzi Christella | 00:08:29 | 2017 | Rwanda | Rulindo | Kisaro | Murama | Akamanama |  |  | Gahama Kisaro network | 10234 |  | 141 | 141 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | -1.6671501074688961 | 30.041830412153367 | 1947.4 | 24l5zh36 |  | Yes | 3 | Yes | 1 |  |  | 2012 | Normal | 3 | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 7 | -1.6199488423010775 | 30.027460459887696 | 2254 | 22f3822a |  | 2012 | Normal | Yes | 14 |  |  | 2012 | Normal | Yes | 1 |  | 2012 | Normal | 30000 | Yes | 2 |  | 2012 | Normal | Yes |  | 2012 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6444884535853794 | 30.04905062160057 | 2032.6 | 23jo9sqy | 1 | https://waterforpeople.s3.amazonaws.com/images/17ec45bf-ff46-4ddb-be01-309044b4908d.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal |  | 199de3d010aad4bafaa388655d4ac1
m6fb-k9qd-42pd | 1 |  | J7 Rw15 | 1228150359 | 21-03-2017 13:39:51 CET | Mukakarangwa Assoumpta | 01:18:35 | 2017 | Rwanda | Rulindo | Kinihira | Karegamazi | Buhita |  |  | Miyove-Kinihira | 10452 |  | 131 | 60 | 71 | Yes | Piped Network -- Gravity Only |  | 2001 | Yes | Mutoyi | GKWW | GKWW was a project in eight sub Prefucture | 6 | Spring | -1.611549912597613 | 29.966791783057694 | 2071.7 | 22173xg3 | https://waterforpeople.s3.amazonaws.com/images/36e31277-cc59-4644-840d-524cd0032675.jpg | Yes | 5 | Yes | 3 | https://waterforpeople.s3.amazonaws.com/images/720d5955-044a-4ffc-86c4-8ed7bf8d3e95.jpg | "Springbox" --Intake Structure at a Spring | 1989 | Poor | 5 | Yes | 1 | https://waterforpeople.s3.amazonaws.com/images/3220cf12-00fd-4e3c-8897-3408feb73f18.jpg | 1985 | Poor | 8000 | Yes | 4 | -1.6659813252567734 | 29.98395927041342 | 2023.9 | 24j8bqv3 | https://waterforpeople.s3.amazonaws.com/images/3918622e-8b6d-4021-bbc9-2f5fa040b50b.jpg | 1985 | Normal | Yes | 18 | Distribution Chamber¦ventouse, Washout | https://waterforpeople.s3.amazonaws.com/images/8e662a14-23cf-4375-85f4-5c2041e22e0a.jpg | 2015 | Poor | Yes | 2 | https://waterforpeople.s3.amazonaws.com/images/c740e829-bf16-4ea8-8a6d-1b780370ec99.jpg | 1989 | Poor | 15000 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6469366279457327 | 29.98228841745874 | 1924 | 23nq4zfy | 2 | https://waterforpeople.s3.amazonaws.com/images/9cd0b259-9b5c-4321-964b-1da8f35305ad.jpg | 2015 | Normal | No |  |  |  | Yes |  | Poor | -Miyove-Kinihira network was first constructed in 1989 by GKWW and it has 23km,it serves water in Gicumbi district (Miyove sector) and Rulindo district (Kinihira sector),was rehabilitated from sources to collection chamber in 2001 and in 2015 world vision did the extension of this network in some cells of Kinihira which had not access to the improved water system like Karegamazi and Rebero. -At this moment the network is being rehabitated by water for people. -It has 6 sources and 3 collection chambers which are not in good condition. -It has 4 reservoirs in which 3 of them was constructed 1989 and are working properly and 1 contructed by world vision in 2015 in Karegamazi cell. - it has 18 other concrete structures some was constructed in 2015 and others are constructed in 1989 and do not function properly and are going to be rehabilitated. -It has 31 water points in which 8 is for Miyove and 23 is for Kinihira,some are normal and are contructed by world vision in 2015 and others are constructed in 1989(some are poor and others do not function). | 7e778c56a1682635abb92cbd4c1687f
vy2k-rxsj-tfma | 1 |  | J7 Rw10 | 1289334552 | 16-04-2017 00:29:17 CEST | Tuyisenge Vianney | 00:09:23 | 2017 | Rwanda | Rulindo | Bushoki | Gasiza | Buhande |  |  | Water point at Pensez-y/Gasebeya gravity system |  |  | 129 | 1 | 128 | Yes | Piped Network -- Gravity Only |  | 2004 | No |  | Pensez-y bar restaurant | This water point is privately owned by Pensez-y and it has been captured from Gasebeya catchment area | 1 | Spring | -1.7463205694821387 | 29.92397335829367 | 1778.2 | 2883k8h3 |  | Yes | 60 | No | [5 empty] | 60 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7450534344041366 | 29.92133571624435 | 1769 | 285zy6ml | 1 | https://waterforpeople.s3.amazonaws.com/images/5fae6c14-d14d-4e37-91e7-185bb5de537f.jpg | 2004 | Normal | No |  |  |  | Yes |  | Normal | This water point is privately owned by Pensez-y and it has been captured from Gasebeya catchment area | f1b7b51bc94988713a32ec36315b8d9f
tcwm-ekcm-p0n8 | 1 |  | J7 Rw10 | 1214121009 | 15-03-2017 17:04:16 CET | Tuyisenge Vianney | 00:06:54 | 2017 | Rwanda | Rulindo | Bushoki | Giko | Buramira |  |  | Water point nearby Giko cell/Nyirambuga pumping | 30604 |  | 134 | 134 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | GoR | This water point operates well and normally | 11 | Spring | -1.778040825436737 | 29.922360289445436 | 2013.8 | 29ok37br |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.6815049000077666 | 29.91011898264954 | 2093.7 | 258wch5p | 1 | https://waterforpeople.s3.amazonaws.com/images/a4a40413-0a83-4d09-bd8c-6dc16a806e6c.jpg | 2012 | Normal | No |  |  |  | Yes |  | Normal | This water point operates well and normally | 801c1d785e85d5cdab47de74b4c8178
yhcj-g82y-ncmw | 1 |  | J7 Rw10 | 1228160171 | 02-01-2015 13:23:55 CET | Tuyisenge Vianney | 00:11:31 | 2017 | Rwanda | Rulindo | Mbogo | Ngiramazi | Gisha |  |  | Water point nearby Gisha/Nyirambuga pumping | 30604 |  | 133 | 133 | 0 | Yes | Piped Network with Pump |  | 2015 | No |  | Governement (District, WASAC) and Water For People | Water point at Gisha.It operates well located in Mbogo connected on Nyirambuga pumping system | 11 | Spring | -1.7265024345182751 | 29.956089955799534 | 1943.2 | 27bbj3qg |  | Yes | 4 | No | [5 empty] | 4 | No | [5 empty] | No | [8 empty] | No | [5 empty] | No | [5 empty] | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7529610146326662 | 29.96552475005398 | 2040.6 | 28j2w2h3 | 2 | https://waterforpeople.s3.amazonaws.com/images/4db18d6e-5de3-44b0-9caa-9487eb4d47cb.jpg | 2015 | Normal | No |  |  |  | Yes |  | Normal | Water point at Gisha.It operates well located in Mbogo connected on Nyirambuga pumping system | 2c5ea3da4c3ae4ae8fe63ee825ae3e8
bcpu-vt9b-ss3v | 1 |  | J7 Rw24 | 1215891101 | 16-03-2017 06:08:35 CET | Kabalisa Manzi Christella | 00:06:26 | 2017 | Rwanda | Rulindo | Burega | Karengeli | Mataba |  |  | Rwamugaza | 14106 |  | 495 | 495 | 0 | Yes | Piped Network with Pump |  | 2012 | No |  | Governement (District, WASAC) and Water For People | No Problem with the Water Point | 3 | Spring | -1.7503785350192076 | 29.986212109950618 | 1826.3 | 28esosye |  | Yes | 4.5 | Yes | 3 |  |  | 2009 | Normal | 4.5 | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 16 | -1.7464436544754613 | 30.002844827231502 | 2130.3 | 288apgcc |  | 2012 | Normal | Yes | 8 |  |  | 2012 | Normal | Yes | 2 |  | 2012 | Normal | 5000 | Yes | 1 |  | 2009 | Normal | Yes |  | 2009 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.7350311333407635 | 30.030159985647725 | 2012.4 | 27pfdvbh | 1 | https://waterforpeople.s3.amazonaws.com/images/04d297f9-b97d-450e-b86b-fdef18c6da2b.jpg | 2012 | Normal | No |  |  |  | No | Water seller was not around | Normal | no problem | 8176f4387e6d80062c4b2b037faef8
h1eu-qa74-9xj1 | 1 |  | J7 Rw15 | 1208010217 | 09-03-2017 04:45:50 CET | Mukakarangwa Assoumpta | 00:06:19 | 2017 | Rwanda | Rulindo | Shyorongi | Rutonde | Rutonde |  |  | kirikumuryango network |  |  | 160 | 160 | 0 | Yes | Piped Network -- Gravity Only |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 1 | Spring | 1.87348771132016 | 29.876612576966872 | 1632.8 | 2e2ec8i6 |  | Yes | 11 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 11 | Yes | 1 |  | 2013 | Normal | 500 | Yes | 17 | 1.8753288815719713 | 29.9731727166091 | 1557.6 | 2e5fw0k3 |  | 2013 | Normal | Yes | 6 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 2 |  | 2013 | Normal | 3500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.898765776301512 | 29.967194636896036 | 1398 | 2f87g2hj | 1 | https://waterforpeople.s3.amazonaws.com/images/fb8cb0eb-fb89-48bb-a7a1-a5450cabf32c.jpg | 2013 | Normal | No |  |  |  | Yes |  | Normal | -water point is for Rutonde health center. | cd11efdd363c4cc13f9f5148f2ae3
hc41-qqyb-2rnt | 1 |  | J7 Rw19 | 1250840191 | 25-03-2017 11:40:09 CET | Kayinamura Innocent | 00:10:54 | 2017 | Rwanda | Rulindo | Masoro | Shengampuri | Amataba |  |  | Mutagata Gravity network | 26296 |  | 220 | 54 | 166 | Yes | Piped Network -- Gravity Only |  | 2004 | Yes | Ruri, Musenga, Rukurazo, Umubuga, Amataba, Rusine, Marenge |  |  | 1 | Spring | -1.8023389079852206 | 30.042447389592418 | 1691.2 | 2asq94nc |  | Yes | 8 | Yes | 1 |  | "Springbox" --Intake Structure at a Spring | 2004 | Poor | 8 | Yes | 1 |  | 2004 | Poor | 3500 | Yes | 6 | -1.80784467636504 | 30.06649761552014 | 1669.8 | 2b1uaz5k |  | 2004 | Poor | Yes | 4 | Distribution Chamber¦Washout and Air release |  | 2004 | Poor | Yes | 2 |  | 2004 | Poor | 4500 | No | [8 empty] | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8117121418188546 | 30.081964253997405 | 1600.6 | 2b88pqdv | 12 | https://waterforpeople.s3.amazonaws.com/images/7bd68169-4bab-4bed-9f93-4f3c112dd424.jpg | 2004 | Poor | No |  |  |  | Yes |  | Poor | 1. the Extension to Nyabinyana village has 2 reservoirs and two water points which is under construction 2. this system have been constructed in 2004 3. it serve a party of Masoro Sector and other party is located in Gasabo District 4. 2 water points and one reservoir have been constructed in 2016. 5. in general, this network has 27 water points in which 12 are in Rulindo District and the remaining are in Gasabo District. | c7478e88aac58ed4b556ca6a782677b
wd8g-gava-638m | 1 |  | J7 Rw15 | 1200280212 | 08-03-2017 20:55:31 CET | Mukakarangwa Assoumpta | 00:06:02 | 2017 | Rwanda | Rulindo | Shyorongi | Bugaragara | Kabaraza |  |  | kinywamagana pumping network | 6436 |  | 165 | 35 | 130 | Yes | Piped Network with Pump |  | 2013 | No |  | Governement (District, WASAC) and Water For People |  | 7 | Spring | 1.8477960746052928 | 29.97097938016282 | 1741 | 2cvwto59 |  | Yes | 10 | Yes | 3 |  | "Springbox" --Intake Structure at a Spring | 2013 | Normal | 10 | Yes | 1 |  | 2013 | Normal | 1500 | Yes | 20 | 1.859369162038424 | 29.966841344261912 | 2001.1 | 2df1o710 |  | 2013 | Normal | Yes | 25 | Distribution Chamber¦ventouse, Washout |  | 2013 | Normal | Yes | 4 |  | 2013 | Normal | 11000 | Yes | 2 |  | 2013 | Poor | Yes |  | 2013 | Normal | No | [8 empty] | Yes | Yes | 0 | Yes | 0 | Yes | Not Present | Yes | 0 | Yes | -1.8660782410306138 | 29.980382599571787 | 1957.2 | 2dq5621n | 1 | https://waterforpeople.s3.amazonaws.com/images/9f62ec9d-7cb1-4fc5-9ea1-7143fe2708b9.jpg | 2013 | Normal | No |  |  |  | Yes |  | Poor |  | 9eb2ff615c8fadc9321bb5fe946e3fca

## Reference Sheet
Reference data: Design Lifetime | Years
Well | 20
Intake | 30
Conduction Line | 20
Storage tank | 30
Other Concrete Structure (sedimentation tank, pleasure break tank, etc.) | 20
Distribution Network | 30
Pump and Pump Related Electrical Equipment | 7
Pump House/Station | 20
Treatment Equipment | 10
Treatment Housing Structure | 10
Kiosk or Public Tap | 20
Government Standards Water Quantity | Liters Per Person Per Day
India | 55
Honduras | 75
Guatemala | 75
Nicaragua | 50
Bolivia | 50
Peru | 80
Malawi Chikhwawa | 27
Malawi Blantyre | 40
Rwanda | 20
Uganda | 20
Government Standards Number Of Users Per Day | Users Per Day
India | 250
Honduras
Gautemala
Nicaragua
Bolivia | 50
Peru | 60
Malawi Blantyre | 250
Malawi Chikwawa | 250
Rwanda | 300
Uganda | 300

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only